## Introduction
IMPORTANT!
For all users of the PV System Calculator
Mastervolt has created the PV System Calulator as a free of charge tool to help design a grid connected
PV system, utilizing Mastervolt XS, CS and IS inverters. Although the data and functionality is thoroughly checked,
Mastervolt International BV, a Mastervolt branch office in your country or a Mastervolt dealer/ distributor,
is not liable for the correctness of this tool. We advise all users to double check the outcome with a
qualified installer, your supplier or with the local Mastervolt representative.
ATTENTION: New versions of this tool with updated module database are regularly available from www.mastervoltsolar.com
current version: March'11.
If you have questions or remarks about this tool, please do not hesitate to contact us at |  |  | SysCalc@mastervolt.com
Taal \ Language \ Sprache \ Lenguaje \ Langue \ Lingua :
Version changelog:
Version: |  | Change:
March 2011 |  | Added reactive power
Included IS inverter
>100 New modules
beta in [%/°C] instead of [‰/°C]

## Design (graphical)
module : |  |  |  |  | range | input 1 | input 2 | input 3 | total no. of modules
|  |  | modules per string : |  | 7 - 15
|  |  | no. of strings : |  | 3 - 7 |  |  |  | 110
location :
orientation :
gradient :
temp. of module :
Max. :
Min. :
underdimensioning [UDF] :
cos(φ)=
inverter :
Kleurcodes
|  |  |  | Compatability check | [5 empty] | Paneel/omvormer combinatie: | 1
[10 empty] | max modules: | 2
[11 empty] | Ingang 1: | Ingang 2: | Ingang 3: | Ingang 4:
[10 empty] | Onderdimensionering: | 1 | 1 | 3 | 3
|  |  | Inverter efficiency will be most optimal for DC voltages close to 650 V | [6 empty] | Stroom: | 1 | 1 | 3 | 3
[10 empty] | Energieomzetting: | 1 | 1 | 4 | 4
[10 empty] | Opstartspanning: | 1 | 1 | 3 | 3
[10 empty] | Umpp bij -10°C: | 1 | 1 | 1 | 3
|  | 1 | The connected PV power is optimal | [6 empty] | Uoc bij -10°C : | 1 | 1 | 1 | 3
The inverter will convert all the available solar power
Optimal energy conversion of available solar power
The startup voltage is optimal
The MPP-voltage at min module temperature is optimal
The open circuit voltage at min module temperature is within the operating window
|  | 2 | The connected PV power is optimal
The inverter will convert all the available solar power
Optimal energy conversion of available solar power
The startup voltage is optimal
The MPP-voltage at min module temperature is optimal
The open circuit voltage at min module temperature is within the operating window
|  | 3 | No complete conversion
Umpp < 100V
This configuration has a relatively high energy loss at max irradiation
The startup voltage is too low
The MPP-voltage at min module temperature is optimal
The open circuit voltage at min module temperature is within the operating window
|  | 4 | No complete conversion
Umpp < 100V
This configuration has a relatively high energy loss at max irradiation
The startup voltage is too low
The MPP-voltage is too low
The open circuit voltage at min module temperature is too low
Note on C24: Set to 1 exc ept for Germany, for more information see HELP page.

## Design opties (hidden)
Max modules |  | Temperatuur |  |  | Onderdimensionering |  |  | Parallel Mode |  | modules per string | [6 empty] | Power Factor
[10 empty] | no. of strings |  | input 1 | input 2 | input 3 | input 4
1 | 1 | -50 |  |  |  |  | 1 | [8 empty] | 1 | 0.85
2 | 2 | -45 |  |  |  |  | 2 |  |  | 1 | modules per string | 11 | 11 | 5 | 1 | 2 | 0.86
3 | 3 | -40 | [7 empty] | 2 | no. of strings : | 5 | 5 | 1 | 1 | 3 | 0.87
4 | 4 | -35 | [7 empty] | 3 | [5 empty] | 4 | 0.88
5 | 5 | -30 |  | 1 | 0.7 |  |  | Geselecteerd: | 2 | 4 | [5 empty] | 5 | 0.89
6 | 6 | -25 |  | 2 | 0.75 |  |  |  |  | 5 | [5 empty] | 6 | 0.9
7 | 7 | -20 |  | 3 | 0.8 |  |  | Wordt niet gebruikt |  | 6 | [5 empty] | 7 | 0.91
8 | 8 | -15 |  | 4 | 0.85 |  |  |  |  | 7 | [5 empty] | 8 | 0.92
9 | 9 | -10 |  | 5 | 0.9 |  |  |  |  | 8 | [5 empty] | 9 | 0.93
10 | 10 | -5 |  | 6 | 0.95 |  |  |  |  | 9 | [5 empty] | 10 | 0.94
11 | 11 | 0 |  | 7 | 1 |  |  |  |  | 10 | [5 empty] | 11 | 0.95
12 | 12 | 5 | [7 empty] | 11 | [5 empty] | 12 | 0.96
13 | 13 | 10 | [7 empty] | 12 | [5 empty] | 13 | 0.97
14 | 14 | 15 |  |  | Geselecteerd: | 5 |  |  |  | 13 | [5 empty] | 14 | 0.98
15 | 15 | 20 | [7 empty] | 14 | [5 empty] | 15 | 0.99
16 | 16 | 25 |  |  | Onderdimensionering: | 0.9 |  |  |  | 15 | [5 empty] | 16 | 1
17 | 17 | 30 | [7 empty] | 16
18 | 18 | 35 | [7 empty] | 17
19 | 19 | 40 | [7 empty] | 18 | [6 empty] | Geselecteerd: | 16
20 | 20 | 45 | [7 empty] | 19
21 | 21 | 50 | [7 empty] | 20 | [6 empty] | PF | 1
22 | 22 | 55 | [7 empty] | 21
23 | 23 | 60 | [7 empty] | 22
24 | 24 | 65 | [7 empty] | 23
25 | 25 | 70 | [7 empty] | 24
26 | 26 | 75 | [7 empty] | 25
27 | 27 | 80 | [7 empty] | 26
28 | 28 | 85 | [7 empty] | 27
29 | 29 | 90 | [7 empty] | 28
30 | 30 | 95 | [7 empty] | 29
31 | 31 | 100 | [7 empty] | 30
32 | [9 empty] | 31
33 | [9 empty] | 32
34 |  | Tontwerp: | 20 | [6 empty] | 33
35 | [9 empty] | 34
36 |  | temp: | 45 | [6 empty] | 35
37 | [9 empty] | 36
38 |  | Tmin: | 9 | [6 empty] | 37
39 | [9 empty] | 38
40 |  | temp: | -10 | [6 empty] | 39
41 | [9 empty] | 40
42 | [9 empty] | 41
43 | [9 empty] | 42
44 | [9 empty] | 43
45 | Geselecteerd: | 79 | [7 empty] | 44
46 | [9 empty] | 45
47 | [9 empty] | 46
48 | [9 empty] | 47
49 | [9 empty] | 48
50 | [9 empty] | 49
51 | [9 empty] | 50
52 | [9 empty] | 51
53 | [9 empty] | 52
54 | [9 empty] | 53
55 | [9 empty] | 54
56 | [9 empty] | 55
57 | [9 empty] | 56
58 | [9 empty] | 57
59 | [9 empty] | 58
60 | [9 empty] | 59
61 | [9 empty] | 60
62 | [9 empty] | 61
63 | [9 empty] | 62
64 | [9 empty] | 63
65 | [9 empty] | 64
66 | [9 empty] | 65
67 | [9 empty] | 66
68 | [9 empty] | 67
69 | [9 empty] | 68
70 | [9 empty] | 69
71 | [9 empty] | 70
72 | [9 empty] | 71
73 | [9 empty] | 72
74 | [9 empty] | 73
75 | [9 empty] | 74
76 | [9 empty] | 75
77 | [9 empty] | 76
78 | [9 empty] | 77
79 | [9 empty] | 78
80 | [9 empty] | 79
81 | [9 empty] | 80
82 | [9 empty] | 81
83 | [9 empty] | 82
84 | [9 empty] | 83
85 | [9 empty] | 84
86 | [9 empty] | 85
87 | [9 empty] | 86
88 | [9 empty] | 87
89 | [9 empty] | 88
90 | [9 empty] | 89
91 | [9 empty] | 90
92 | [9 empty] | 91
93 | [9 empty] | 92
94 | [9 empty] | 93
95 | [9 empty] | 94
96 | [9 empty] | 95
97 | [9 empty] | 96
98 | [9 empty] | 97
99 | [9 empty] | 98
100 | [9 empty] | 99
101 | [9 empty] | 100
102 | [9 empty] | 101
103 | [9 empty] | 102
104 | [9 empty] | 103
105 | [9 empty] | 104
106 | [9 empty] | 105
107 | [9 empty] | 106
108 | [9 empty] | 107
109 | [9 empty] | 108
110 | [9 empty] | 109
111 | [9 empty] | 110
112 | [9 empty] | 111
113 | [9 empty] | 112
114 | [9 empty] | 113
115 | [9 empty] | 114
116 | [9 empty] | 115
117 | [9 empty] | 116
118 | [9 empty] | 117
119 | [9 empty] | 118
120 | [9 empty] | 119
121 | [9 empty] | 120
122 | [9 empty] | 121
123 | [9 empty] | 122
124 | [9 empty] | 123
125 | [9 empty] | 124
126 | [9 empty] | 125
127 | [9 empty] | 126
128 | [9 empty] | 127
129 | [9 empty] | 128
130 | [9 empty] | 129
131 | [9 empty] | 130
132 | [9 empty] | 131
133 | [9 empty] | 132
134 | [9 empty] | 133
135 | [9 empty] | 134
136 | [9 empty] | 135
137 | [9 empty] | 136
138 | [9 empty] | 137
139 | [9 empty] | 138
140 | [9 empty] | 139
141 | [9 empty] | 140
142 | [9 empty] | 141
143 | [9 empty] | 142
144 | [9 empty] | 143
145 | [9 empty] | 144
146 | [9 empty] | 145
147 | [9 empty] | 146
148 | [9 empty] | 147
149 | [9 empty] | 148
150 | [9 empty] | 149
151 | [9 empty] | 150
152 | [9 empty] | 151
153 | [9 empty] | 152
154 | [9 empty] | 153
155 | [9 empty] | 154
156 | [9 empty] | 155
157 | [9 empty] | 156
158 | [9 empty] | 157
159 | [9 empty] | 158
160 | [9 empty] | 159
161 | [9 empty] | 160
162 | [9 empty] | 161
163 | [9 empty] | 162
164 | [9 empty] | 163
165 | [9 empty] | 164
166 | [9 empty] | 165
167 | [9 empty] | 166
168 | [9 empty] | 167
169 | [9 empty] | 168
170 | [9 empty] | 169
171 | [9 empty] | 170
172 | [9 empty] | 171
173 | [9 empty] | 172
174 | [9 empty] | 173
175 | [9 empty] | 174
176 | [9 empty] | 175
177 | [9 empty] | 176
178 | [9 empty] | 177
179 | [9 empty] | 178
180 | [9 empty] | 179
181 | [9 empty] | 180
182 | [9 empty] | 181
183 | [9 empty] | 182
184 | [9 empty] | 183
185 | [9 empty] | 184
186 | [9 empty] | 185
187 | [9 empty] | 186
188 | [9 empty] | 187
189 | [9 empty] | 188
190 | [9 empty] | 189
191 | [9 empty] | 190
192 | [9 empty] | 191
193 | [9 empty] | 192
194 | [9 empty] | 193
195 | [9 empty] | 194
196 | [9 empty] | 195
197 | [9 empty] | 196
198 | [9 empty] | 197
199 | [9 empty] | 198
200 | [9 empty] | 199
201 | [9 empty] | 200
202 | [9 empty] | 201
203 | [9 empty] | 202
204 | [9 empty] | 203
205 | [9 empty] | 204
206 | [9 empty] | 205
207 | [9 empty] | 206
208 | [9 empty] | 207
209 | [9 empty] | 208
210 | [9 empty] | 209
211 | [9 empty] | 210
212 | [9 empty] | 211
213 | [9 empty] | 212
214 | [9 empty] | 213
215 | [9 empty] | 214
216 | [9 empty] | 215
217 | [9 empty] | 216
218 | [9 empty] | 217
219 | [9 empty] | 218
220 | [9 empty] | 219
221 | [9 empty] | 220
222 | [9 empty] | 221
223 | [9 empty] | 222
224 | [9 empty] | 223
225 | [9 empty] | 224
226 | [9 empty] | 225
227 | [9 empty] | 226
228 | [9 empty] | 227
229 | [9 empty] | 228
230 | [9 empty] | 229
231 | [9 empty] | 230
232 | [9 empty] | 231
233 | [9 empty] | 232
234 | [9 empty] | 233
235 | [9 empty] | 234
236 | [9 empty] | 235
237 | [9 empty] | 236
238 | [9 empty] | 237
239 | [9 empty] | 238
240 | [9 empty] | 239
241 | [9 empty] | 240
242 | [9 empty] | 241
243 | [9 empty] | 242
244 | [9 empty] | 243
245 | [9 empty] | 244
246 | [9 empty] | 245
247 | [9 empty] | 246
248 | [9 empty] | 247
249 | [9 empty] | 248
250 | [9 empty] | 249
251 | [9 empty] | 250
252 | [9 empty] | 251
253 | [9 empty] | 252
254 | [9 empty] | 253
255 | [9 empty] | 254
256 | [9 empty] | 255
257 | [9 empty] | 256
258 | [9 empty] | 257
259 | [9 empty] | 258
260 | [9 empty] | 259
261 | [9 empty] | 260
262 | [9 empty] | 261
263 | [9 empty] | 262
264 | [9 empty] | 263
265 | [9 empty] | 264
266 | [9 empty] | 265
267 | [9 empty] | 266
268 | [9 empty] | 267
269 | [9 empty] | 268
270 | [9 empty] | 269
271 | [9 empty] | 270
272 | [9 empty] | 271
273 | [9 empty] | 272
274 | [9 empty] | 273
275 | [9 empty] | 274
276 | [9 empty] | 275
277 | [9 empty] | 276
278 | [9 empty] | 277
279 | [9 empty] | 278
280 | [9 empty] | 279
281 | [9 empty] | 280
282 | [9 empty] | 281
283 | [9 empty] | 282
284 | [9 empty] | 283
285 | [9 empty] | 284
286 | [9 empty] | 285
287 | [9 empty] | 286
288 | [9 empty] | 287
289 | [9 empty] | 288
290 | [9 empty] | 289
291 | [9 empty] | 290
292 | [9 empty] | 291
293 | [9 empty] | 292
294 | [9 empty] | 293
295 | [9 empty] | 294
296 | [9 empty] | 295
297 | [9 empty] | 296
298 | [9 empty] | 297
299 | [9 empty] | 298
300 | [9 empty] | 299
301 | [9 empty] | 300
302 | [9 empty] | 301
303 | [9 empty] | 302
304 | [9 empty] | 303
305 | [9 empty] | 304
306 | [9 empty] | 305
307 | [9 empty] | 306
308 | [9 empty] | 307
309 | [9 empty] | 308
310 | [9 empty] | 309
311 | [9 empty] | 310
312 | [9 empty] | 311
313 | [9 empty] | 312
314 | [9 empty] | 313
315 | [9 empty] | 314
316 | [9 empty] | 315
317 | [9 empty] | 316
318 | [9 empty] | 317
319 | [9 empty] | 318
320 | [9 empty] | 319
321 | [9 empty] | 320
322 | [9 empty] | 321
323 | [9 empty] | 322
324 | [9 empty] | 323
325 | [9 empty] | 324
326 | [9 empty] | 325
327 | [9 empty] | 326
328 | [9 empty] | 327
329 | [9 empty] | 328
330 | [9 empty] | 329
331 | [9 empty] | 330
332 | [9 empty] | 331
333 | [9 empty] | 332
334 | [9 empty] | 333
335 | [9 empty] | 334
336 | [9 empty] | 335
337 | [9 empty] | 336
338 | [9 empty] | 337
339 | [9 empty] | 338
340 | [9 empty] | 339
341 | [9 empty] | 340
342 | [9 empty] | 341
343 | [9 empty] | 342
344 | [9 empty] | 343
345 | [9 empty] | 344
346 | [9 empty] | 345
347 | [9 empty] | 346
348 | [9 empty] | 347
349 | [9 empty] | 348
350 | [9 empty] | 349
351 | [9 empty] | 350
352 | [9 empty] | 351
353 | [9 empty] | 352
354 | [9 empty] | 353
355 | [9 empty] | 354
356 | [9 empty] | 355
357 | [9 empty] | 356
358 | [9 empty] | 357
359 | [9 empty] | 358
360 | [9 empty] | 359
361 | [9 empty] | 360
362 | [9 empty] | 361
363 | [9 empty] | 362
364 | [9 empty] | 363
365 | [9 empty] | 364
366 | [9 empty] | 365
367 | [9 empty] | 366
368 | [9 empty] | 367
369 | [9 empty] | 368
370 | [9 empty] | 369
371 | [9 empty] | 370
372 | [9 empty] | 371
373 | [9 empty] | 372
374 | [9 empty] | 373
375 | [9 empty] | 374
376 | [9 empty] | 375
377 | [9 empty] | 376
378 | [9 empty] | 377
379 | [9 empty] | 378
380 | [9 empty] | 379
381 | [9 empty] | 380
382 | [9 empty] | 381
383 | [9 empty] | 382
384 | [9 empty] | 383
385 | [9 empty] | 384
386 | [9 empty] | 385
387 | [9 empty] | 386
388 | [9 empty] | 387
389 | [9 empty] | 388
390 | [9 empty] | 389
391 | [9 empty] | 390
392 | [9 empty] | 391
393 | [9 empty] | 392
394 | [9 empty] | 393
395 | [9 empty] | 394
396 | [9 empty] | 395
397 | [9 empty] | 396
398 | [9 empty] | 397
399 | [9 empty] | 398
400 | [9 empty] | 399
401 | [9 empty] | 400
402 | [9 empty] | 401
403 | [9 empty] | 402
404 | [9 empty] | 403
405 | [9 empty] | 404
406 | [9 empty] | 405
407 | [9 empty] | 406
408 | [9 empty] | 407
409 | [9 empty] | 408
410 | [9 empty] | 409
411 | [9 empty] | 410
412 | [9 empty] | 411
413 | [9 empty] | 412
414 | [9 empty] | 413
415 | [9 empty] | 414
416 | [9 empty] | 415
417 | [9 empty] | 416
418 | [9 empty] | 417
419 | [9 empty] | 418
420 | [9 empty] | 419
421 | [9 empty] | 420
422 | [9 empty] | 421
423 | [9 empty] | 422
424 | [9 empty] | 423
425 | [9 empty] | 424
426 | [9 empty] | 425
427 | [9 empty] | 426
428 | [9 empty] | 427
429 | [9 empty] | 428
430 | [9 empty] | 429
431 | [9 empty] | 430
432 | [9 empty] | 431
433 | [9 empty] | 432
434 | [9 empty] | 433
435 | [9 empty] | 434
436 | [9 empty] | 435
437 | [9 empty] | 436
438 | [9 empty] | 437
439 | [9 empty] | 438
440 | [9 empty] | 439
441 | [9 empty] | 440
442 | [9 empty] | 441
443 | [9 empty] | 442
444 | [9 empty] | 443
445 | [9 empty] | 444
446 | [9 empty] | 445
447 | [9 empty] | 446
448 | [9 empty] | 447
449 | [9 empty] | 448
450 | [9 empty] | 449
451 | [9 empty] | 450
452 | [9 empty] | 451
453 | [9 empty] | 452
454 | [9 empty] | 453
455 | [9 empty] | 454
456 | [9 empty] | 455
457 | [9 empty] | 456
458 | [9 empty] | 457
459 | [9 empty] | 458
460 | [9 empty] | 459
461 | [9 empty] | 460
462 | [9 empty] | 461
463 | [9 empty] | 462
464 | [9 empty] | 463
465 | [9 empty] | 464
466 | [9 empty] | 465
467 | [9 empty] | 466
468 | [9 empty] | 467
469 | [9 empty] | 468
470 | [9 empty] | 469
471 | [9 empty] | 470
472 | [9 empty] | 471
473 | [9 empty] | 472
474 | [9 empty] | 473
475 | [9 empty] | 474
476 | [9 empty] | 475
477 | [9 empty] | 476
478 | [9 empty] | 477
479 | [9 empty] | 478
480 | [9 empty] | 479
481 | [9 empty] | 480
482 | [9 empty] | 481
483 | [9 empty] | 482
484 | [9 empty] | 483
485 | [9 empty] | 484
486 | [9 empty] | 485
487 | [9 empty] | 486
488 | [9 empty] | 487
489 | [9 empty] | 488
490 | [9 empty] | 489
491 | [9 empty] | 490
492 | [9 empty] | 491
493 | [9 empty] | 492
494 | [9 empty] | 493
495 | [9 empty] | 494
496 | [9 empty] | 495
497 | [9 empty] | 496
498 | [9 empty] | 497
499 | [9 empty] | 498
500 | [9 empty] | 499
501 | [9 empty] | 500
502 | [9 empty] | 501
503 | [9 empty] | 502
504 | [9 empty] | 503
505 | [9 empty] | 504
506 | [9 empty] | 505
507 | [9 empty] | 506
508 | [9 empty] | 507
509 | [9 empty] | 508
510 | [9 empty] | 509
511 | [9 empty] | 510
512 | [9 empty] | 511
513 | [9 empty] | 512
514 | [9 empty] | 513
515 | [9 empty] | 514
516 | [9 empty] | 515
517 | [9 empty] | 516
518 | [9 empty] | 517
519 | [9 empty] | 518
520 | [9 empty] | 519
521 | [9 empty] | 520
522 | [9 empty] | 521
523 | [9 empty] | 522
524 | [9 empty] | 523
525 | [9 empty] | 524
526 | [9 empty] | 525
527 | [9 empty] | 526
528 | [9 empty] | 527
529 | [9 empty] | 528
530 | [9 empty] | 529
531 | [9 empty] | 530
532 | [9 empty] | 531
533 | [9 empty] | 532
534 | [9 empty] | 533
535 | [9 empty] | 534
536 | [9 empty] | 535
537 | [9 empty] | 536
538 | [9 empty] | 537
539 | [9 empty] | 538
540 | [9 empty] | 539
541 | [9 empty] | 540
542 | [9 empty] | 541
543 | [9 empty] | 542
544 | [9 empty] | 543
545 | [9 empty] | 544
546 | [9 empty] | 545
547 | [9 empty] | 546
548 | [9 empty] | 547
549 | [9 empty] | 548
550 | [9 empty] | 549
551 | [9 empty] | 550
552 | [9 empty] | 551
553 | [9 empty] | 552
554 | [9 empty] | 553
555 | [9 empty] | 554
556 | [9 empty] | 555
557 | [9 empty] | 556
558 | [9 empty] | 557
559 | [9 empty] | 558
560 | [9 empty] | 559
561 | [9 empty] | 560
562 | [9 empty] | 561
563 | [9 empty] | 562
564 | [9 empty] | 563
565 | [9 empty] | 564
566 | [9 empty] | 565
567 | [9 empty] | 566
568 | [9 empty] | 567
569 | [9 empty] | 568
570 | [9 empty] | 569
571 | [9 empty] | 570
572 | [9 empty] | 571
573 | [9 empty] | 572
574 | [9 empty] | 573
575 | [9 empty] | 574
576 | [9 empty] | 575
577 | [9 empty] | 576
578 | [9 empty] | 577
579 | [9 empty] | 578
580 | [9 empty] | 579
581 | [9 empty] | 580
582 | [9 empty] | 581
583 | [9 empty] | 582
584 | [9 empty] | 583
585 | [9 empty] | 584
586 | [9 empty] | 585
587 | [9 empty] | 586
588 | [9 empty] | 587
589 | [9 empty] | 588
590 | [9 empty] | 589
591 | [9 empty] | 590
592 | [9 empty] | 591
593 | [9 empty] | 592
594 | [9 empty] | 593
595 | [9 empty] | 594
596 | [9 empty] | 595
597 | [9 empty] | 596
598 | [9 empty] | 597
599 | [9 empty] | 598
600 | [9 empty] | 599
601 | [9 empty] | 600
602 | [9 empty] | 601
603 | [9 empty] | 602
604 | [9 empty] | 603
605 | [9 empty] | 604
606 | [9 empty] | 605
607 | [9 empty] | 606
608 | [9 empty] | 607
609 | [9 empty] | 608
610 | [9 empty] | 609
611 | [9 empty] | 610
612 | [9 empty] | 611
613 | [9 empty] | 612
614 | [9 empty] | 613
615 | [9 empty] | 614
616 | [9 empty] | 615
617 | [9 empty] | 616
618 | [9 empty] | 617
619 | [9 empty] | 618
620 | [9 empty] | 619
621 | [9 empty] | 620
622 | [9 empty] | 621
623 | [9 empty] | 622
624 | [9 empty] | 623
625 | [9 empty] | 624
626 | [9 empty] | 625
627 | [9 empty] | 626
628 | [9 empty] | 627
629 | [9 empty] | 628
630 | [9 empty] | 629
631 | [9 empty] | 630
632 | [9 empty] | 631
633 | [9 empty] | 632
634 | [9 empty] | 633
635 | [9 empty] | 634
636 | [9 empty] | 635
637 | [9 empty] | 636
638 | [9 empty] | 637
639 | [9 empty] | 638
640 | [9 empty] | 639
641 | [9 empty] | 640
642 | [9 empty] | 641
643 | [9 empty] | 642
644 | [9 empty] | 643
645 | [9 empty] | 644
646 | [9 empty] | 645
647 | [9 empty] | 646
648 | [9 empty] | 647
649 | [9 empty] | 648
650 | [9 empty] | 649
651 | [9 empty] | 650
652 | [9 empty] | 651
653 | [9 empty] | 652
654 | [9 empty] | 653
655 | [9 empty] | 654
656 | [9 empty] | 655
657 | [9 empty] | 656
658 | [9 empty] | 657
659 | [9 empty] | 658
660 | [9 empty] | 659
661 | [9 empty] | 660
662 | [9 empty] | 661
663 | [9 empty] | 662
664 | [9 empty] | 663
665 | [9 empty] | 664
666 | [9 empty] | 665
667 | [9 empty] | 666
668 | [9 empty] | 667
669 | [9 empty] | 668
670 | [9 empty] | 669
671 | [9 empty] | 670
672 | [9 empty] | 671
673 | [9 empty] | 672
674 | [9 empty] | 673
675 | [9 empty] | 674
676 | [9 empty] | 675
677 | [9 empty] | 676
678 | [9 empty] | 677
679 | [9 empty] | 678
680 | [9 empty] | 679
681 | [9 empty] | 680
682 | [9 empty] | 681
683 | [9 empty] | 682
684 | [9 empty] | 683
685 | [9 empty] | 684
686 | [9 empty] | 685
687 | [9 empty] | 686
688 | [9 empty] | 687
689 | [9 empty] | 688
690 | [9 empty] | 689
691 | [9 empty] | 690
692 | [9 empty] | 691
693 | [9 empty] | 692
694 | [9 empty] | 693
695 | [9 empty] | 694
696 | [9 empty] | 695
697 | [9 empty] | 696
698 | [9 empty] | 697
699 | [9 empty] | 698
700 | [9 empty] | 699
701 | [9 empty] | 700
702 | [9 empty] | 701
703 | [9 empty] | 702
704 | [9 empty] | 703
705 | [9 empty] | 704
706 | [9 empty] | 705
707 | [9 empty] | 706
708 | [9 empty] | 707
709 | [9 empty] | 708
710 | [9 empty] | 709
711 | [9 empty] | 710
712 | [9 empty] | 711
713 | [9 empty] | 712
714 | [9 empty] | 713
715 | [9 empty] | 714
716 | [9 empty] | 715
717 | [9 empty] | 716
718 | [9 empty] | 717
719 | [9 empty] | 718
720 | [9 empty] | 719
721 | [9 empty] | 720
722 | [9 empty] | 721
723 | [9 empty] | 722
724 | [9 empty] | 723
725 | [9 empty] | 724
726 | [9 empty] | 725
727 | [9 empty] | 726
728 | [9 empty] | 727
729 | [9 empty] | 728
730 | [9 empty] | 729
731 | [9 empty] | 730
732 | [9 empty] | 731
733 | [9 empty] | 732
734 | [9 empty] | 733
735 | [9 empty] | 734
736 | [9 empty] | 735
737 | [9 empty] | 736
738 | [9 empty] | 737
739 | [9 empty] | 738
740 | [9 empty] | 739
741 | [9 empty] | 740
742 | [9 empty] | 741
743 | [9 empty] | 742
744 | [9 empty] | 743
745 | [9 empty] | 744
746 | [9 empty] | 745
747 | [9 empty] | 746
748 | [9 empty] | 747
749 | [9 empty] | 748
750 | [9 empty] | 749
751 | [9 empty] | 750
752 | [9 empty] | 751
753 | [9 empty] | 752
754 | [9 empty] | 753
755 | [9 empty] | 754
756 | [9 empty] | 755
757 | [9 empty] | 756
758 | [9 empty] | 757
759 | [9 empty] | 758
760 | [9 empty] | 759
761 | [9 empty] | 760
762 | [9 empty] | 761
763 | [9 empty] | 762
764 | [9 empty] | 763
765 | [9 empty] | 764
766 | [9 empty] | 765
767 | [9 empty] | 766
768 | [9 empty] | 767
769 | [9 empty] | 768
770 | [9 empty] | 769
771 | [9 empty] | 770
772 | [9 empty] | 771
773 | [9 empty] | 772
774 | [9 empty] | 773
775 | [9 empty] | 774
776 | [9 empty] | 775
777 | [9 empty] | 776
778 | [9 empty] | 777
779 | [9 empty] | 778
780 | [9 empty] | 779
781 | [9 empty] | 780
782 | [9 empty] | 781
783 | [9 empty] | 782
784 | [9 empty] | 783
785 | [9 empty] | 784
786 | [9 empty] | 785
787 | [9 empty] | 786
788 | [9 empty] | 787
789 | [9 empty] | 788
790 | [9 empty] | 789
791 | [9 empty] | 790
792 | [9 empty] | 791
793 | [9 empty] | 792
794 | [9 empty] | 793
795 | [9 empty] | 794
796 | [9 empty] | 795
797 | [9 empty] | 796
798 | [9 empty] | 797
799 | [9 empty] | 798
800 | [9 empty] | 799
801 | [9 empty] | 800
802 | [9 empty] | 801
803 | [9 empty] | 802
804 | [9 empty] | 803
805 | [9 empty] | 804
806 | [9 empty] | 805
807 | [9 empty] | 806
808 | [9 empty] | 807
809 | [9 empty] | 808
810 | [9 empty] | 809
811 | [9 empty] | 810
812 | [9 empty] | 811
813 | [9 empty] | 812
814 | [9 empty] | 813
815 | [9 empty] | 814
816 | [9 empty] | 815
817 | [9 empty] | 816
818 | [9 empty] | 817
819 | [9 empty] | 818
820 | [9 empty] | 819
821 | [9 empty] | 820
822 | [9 empty] | 821
823 | [9 empty] | 822
824 | [9 empty] | 823
825 | [9 empty] | 824
826 | [9 empty] | 825
827 | [9 empty] | 826
828 | [9 empty] | 827
829 | [9 empty] | 828
830 | [9 empty] | 829
831 | [9 empty] | 830
832 | [9 empty] | 831
833 | [9 empty] | 832
834 | [9 empty] | 833
835 | [9 empty] | 834
836 | [9 empty] | 835
837 | [9 empty] | 836
838 | [9 empty] | 837
839 | [9 empty] | 838
840 | [9 empty] | 839
841 | [9 empty] | 840
842 | [9 empty] | 841
843 | [9 empty] | 842
844 | [9 empty] | 843
845 | [9 empty] | 844
846 | [9 empty] | 845
847 | [9 empty] | 846
848 | [9 empty] | 847
849 | [9 empty] | 848
850 | [9 empty] | 849
851 | [9 empty] | 850
852 | [9 empty] | 851
853 | [9 empty] | 852
854 | [9 empty] | 853
855 | [9 empty] | 854
856 | [9 empty] | 855
857 | [9 empty] | 856
858 | [9 empty] | 857
859 | [9 empty] | 858
860 | [9 empty] | 859
861 | [9 empty] | 860
862 | [9 empty] | 861
863 | [9 empty] | 862
864 | [9 empty] | 863
865 | [9 empty] | 864
866 | [9 empty] | 865
867 | [9 empty] | 866
868 | [9 empty] | 867
869 | [9 empty] | 868
870 | [9 empty] | 869
871 | [9 empty] | 870
872 | [9 empty] | 871
873 | [9 empty] | 872
874 | [9 empty] | 873
875 | [9 empty] | 874
876 | [9 empty] | 875
877 | [9 empty] | 876
878 | [9 empty] | 877
879 | [9 empty] | 878
880 | [9 empty] | 879
881 | [9 empty] | 880
882 | [9 empty] | 881
883 | [9 empty] | 882
884 | [9 empty] | 883
885 | [9 empty] | 884
886 | [9 empty] | 885
887 | [9 empty] | 886
888 | [9 empty] | 887
889 | [9 empty] | 888
890 | [9 empty] | 889
891 | [9 empty] | 890
892 | [9 empty] | 891
893 | [9 empty] | 892
894 | [9 empty] | 893
895 | [9 empty] | 894
896 | [9 empty] | 895
897 | [9 empty] | 896
898 | [9 empty] | 897
899 | [9 empty] | 898
900 | [9 empty] | 899
901 | [9 empty] | 900
902 | [9 empty] | 901
903 | [9 empty] | 902
904 | [9 empty] | 903
905 | [9 empty] | 904
906 | [9 empty] | 905
907 | [9 empty] | 906
908 | [9 empty] | 907
909 | [9 empty] | 908
910 | [9 empty] | 909
911 | [9 empty] | 910
912 | [9 empty] | 911
913 | [9 empty] | 912
914 | [9 empty] | 913
915 | [9 empty] | 914
916 | [9 empty] | 915
917 | [9 empty] | 916
918 | [9 empty] | 917
919 | [9 empty] | 918
920 | [9 empty] | 919
921 | [9 empty] | 920
922 | [9 empty] | 921
923 | [9 empty] | 922
924 | [9 empty] | 923
925 | [9 empty] | 924
926 | [9 empty] | 925
927 | [9 empty] | 926
928 | [9 empty] | 927
929 | [9 empty] | 928
930 | [9 empty] | 929
931 | [9 empty] | 930
932 | [9 empty] | 931
933 | [9 empty] | 932
934 | [9 empty] | 933
935 | [9 empty] | 934
936 | [9 empty] | 935
937 | [9 empty] | 936
938 | [9 empty] | 937
939 | [9 empty] | 938
940 | [9 empty] | 939
941 | [9 empty] | 940
942 | [9 empty] | 941
943 | [9 empty] | 942
944 | [9 empty] | 943
945 | [9 empty] | 944
946 | [9 empty] | 945
947 | [9 empty] | 946
948 | [9 empty] | 947
949 | [9 empty] | 948
950 | [9 empty] | 949
951 | [9 empty] | 950
952 | [9 empty] | 951
953 | [9 empty] | 952
954 | [9 empty] | 953
955 | [9 empty] | 954
956 | [9 empty] | 955
957 | [9 empty] | 956
958 | [9 empty] | 957
959 | [9 empty] | 958
960 | [9 empty] | 959
961 | [9 empty] | 960
962 | [9 empty] | 961
963 | [9 empty] | 962
964 | [9 empty] | 963
965 | [9 empty] | 964
966 | [9 empty] | 965
967 | [9 empty] | 966
968 | [9 empty] | 967
969 | [9 empty] | 968
970 | [9 empty] | 969
971 | [9 empty] | 970
972 | [9 empty] | 971
973 | [9 empty] | 972
974 | [9 empty] | 973
975 | [9 empty] | 974
976 | [9 empty] | 975
977 | [9 empty] | 976
978 | [9 empty] | 977
979 | [9 empty] | 978
980 | [9 empty] | 979
981 | [9 empty] | 980
982 | [9 empty] | 981
983 | [9 empty] | 982
984 | [9 empty] | 983
985 | [9 empty] | 984
986 | [9 empty] | 985
987 | [9 empty] | 986
988 | [9 empty] | 987
989 | [9 empty] | 988
990 | [9 empty] | 989
991 | [9 empty] | 990
992 | [9 empty] | 991
993 | [9 empty] | 992
994 | [9 empty] | 993
995 | [9 empty] | 994
996 | [9 empty] | 995
997 | [9 empty] | 996
998 | [9 empty] | 997
999 | [9 empty] | 998
1000 | [9 empty] | 999
1001 | [9 empty] | 1000
1002
1003
1004
1005
1006
1007
1008
1009
1010
1011
1012
1013
1014
1015
1016
1017
1018
1019
1020
1021
1022
1023
1024
1025
1026
1027
1028
1029
1030
1031
1032
1033
1034
1035
1036
1037
1038
1039
1040
1041
1042
1043
1044
1045
1046
1047
1048
1049
1050
1051
1052
1053
1054
1055
1056
1057
1058
1059
1060
1061
1062
1063
1064
1065
1066
1067
1068
1069
1070
1071
1072
1073
1074
1075
1076
1077
1078
1079
1080
1081
1082
1083
1084
1085
1086
1087
1088
1089
1090
1091
1092
1093
1094
1095
1096
1097
1098
1099
1100
1101
1102
1103
1104
1105
1106
1107
1108
1109
1110
1111
1112
1113
1114
1115
1116
1117
1118
1119
1120
1121
1122
1123
1124
1125
1126
1127
1128
1129
1130
1131
1132
1133
1134
1135
1136
1137
1138
1139
1140
1141
1142
1143
1144
1145
1146
1147
1148
1149
1150
1151
1152
1153
1154
1155
1156
1157
1158
1159
1160
1161
1162
1163
1164
1165
1166
1167
1168
1169
1170
1171
1172
1173
1174
1175
1176
1177
1178
1179
1180
1181
1182
1183
1184
1185
1186
1187
1188
1189
1190
1191
1192
1193
1194
1195
1196
1197
1198
1199
1200
1201
1202
1203
1204
1205
1206
1207
1208
1209
1210
1211
1212
1213
1214
1215
1216
1217
1218
1219
1220
1221
1222
1223
1224
1225
1226
1227
1228
1229
1230
1231
1232
1233
1234
1235
1236
1237
1238
1239
1240
1241
1242
1243
1244
1245
1246
1247
1248
1249
1250
1251
1252
1253
1254
1255
1256
1257
1258
1259
1260
1261
1262
1263
1264
1265
1266
1267
1268
1269
1270
1271
1272
1273
1274
1275
1276
1277
1278
1279
1280
1281
1282
1283
1284
1285
1286
1287
1288
1289
1290
1291
1292
1293
1294
1295
1296
1297
1298
1299
1300
1301
1302
1303
1304
1305
1306
1307
1308
1309
1310
1311
1312
1313
1314
1315
1316
1317
1318
1319
1320
1321
1322
1323
1324
1325
1326
1327
1328
1329
1330
1331
1332
1333
1334
1335
1336
1337
1338
1339
1340
1341
1342
1343
1344
1345
1346
1347
1348
1349
1350
1351
1352
1353
1354
1355
1356
1357
1358
1359
1360
1361
1362
1363
1364
1365
1366
1367
1368
1369
1370
1371
1372
1373
1374
1375
1376
1377
1378
1379
1380
1381
1382
1383
1384
1385
1386
1387
1388
1389
1390
1391
1392
1393
1394
1395
1396
1397
1398
1399
1400
1401
1402
1403
1404
1405
1406
1407
1408
1409
1410
1411
1412
1413
1414
1415
1416
1417
1418
1419
1420
1421
1422
1423
1424
1425
1426
1427
1428
1429
1430
1431
1432
1433
1434
1435
1436
1437
1438
1439
1440
1441
1442
1443
1444
1445
1446
1447
1448
1449
1450
1451
1452
1453
1454
1455
1456
1457
1458
1459
1460
1461
1462
1463
1464
1465
1466
1467
1468
1469
1470
1471
1472
1473
1474
1475
1476
1477
1478
1479
1480
1481
1482
1483
1484
1485
1486
1487
1488
1489
1490
1491
1492
1493
1494
1495
1496
1497
1498
1499
1500
1501
1502
1503
1504
1505
1506
1507
1508
1509
1510
1511
1512
1513
1514
1515
1516
1517
1518
1519
1520
1521
1522
1523
1524
1525
1526
1527
1528
1529
1530
1531
1532
1533
1534
1535
1536
1537
1538
1539
1540
1541
1542
1543
1544
1545
1546
1547
1548
1549
1550
1551
1552
1553
1554
1555
1556
1557
1558
1559
1560
1561
1562
1563
1564
1565
1566
1567
1568
1569
1570
1571
1572
1573
1574
1575
1576
1577
1578
1579
1580
1581
1582
1583
1584
1585
1586
1587
1588
1589
1590
1591
1592
1593
1594
1595
1596
1597
1598
1599
1600
1601
1602
1603
1604
1605
1606
1607
1608
1609
1610
1611
1612
1613
1614
1615
1616
1617
1618
1619
1620
1621
1622
1623
1624
1625
1626
1627
1628
1629
1630
1631
1632
1633
1634
1635
1636
1637
1638
1639
1640
1641
1642
1643
1644
1645
1646
1647
1648
1649
1650
1651
1652
1653
1654
1655
1656
1657
1658
1659
1660
1661
1662
1663
1664
1665
1666
1667
1668
1669
1670
1671
1672
1673
1674
1675
1676
1677
1678
1679
1680
1681
1682
1683
1684
1685
1686
1687
1688
1689
1690
1691
1692
1693
1694
1695
1696
1697
1698
1699
1700
1701
1702
1703
1704
1705
1706
1707
1708
1709
1710
1711
1712
1713
1714
1715
1716
1717
1718
1719
1720
1721
1722
1723
1724
1725
1726
1727
1728
1729
1730
1731
1732
1733
1734
1735
1736
1737
1738
1739
1740
1741
1742
1743
1744
1745
1746
1747
1748
1749
1750
1751
1752
1753
1754
1755
1756
1757
1758
1759
1760
1761
1762
1763
1764
1765
1766
1767
1768
1769
1770
1771
1772
1773
1774
1775
1776
1777
1778
1779
1780
1781
1782
1783
1784
1785
1786
1787
1788
1789
1790
1791
1792
1793
1794
1795
1796
1797
1798
1799
1800
1801
1802
1803
1804
1805
1806
1807
1808
1809
1810
1811
1812
1813
1814
1815
1816
1817
1818
1819
1820
1821
1822
1823
1824
1825
1826
1827
1828
1829
1830
1831
1832
1833
1834
1835
1836
1837
1838
1839
1840
1841
1842
1843
1844
1845
1846
1847
1848
1849
1850
1851
1852
1853
1854
1855
1856
1857
1858
1859
1860
1861
1862
1863
1864
1865
1866
1867
1868
1869
1870
1871
1872
1873
1874
1875
1876
1877
1878
1879
1880
1881
1882
1883
1884
1885
1886
1887
1888
1889
1890
1891
1892
1893
1894
1895
1896
1897
1898
1899
1900
1901
1902
1903
1904
1905
1906
1907
1908
1909
1910
1911
1912
1913
1914
1915
1916
1917
1918
1919
1920
1921
1922
1923
1924
1925
1926
1927
1928
1929
1930
1931
1932
1933
1934
1935
1936
1937
1938
1939
1940
1941
1942
1943
1944
1945
1946
1947
1948
1949
1950
1951
1952
1953
1954
1955
1956
1957
1958
1959
1960
1961
1962
1963
1964
1965
1966
1967
1968
1969
1970
1971
1972
1973
1974
1975
1976
1977
1978
1979
1980
1981
1982
1983
1984
1985
1986
1987
1988
1989
1990
1991
1992
1993
1994
1995
1996
1997
1998
1999
2000
2001
2002
2003
2004
2005
2006
2007
2008
2009
2010
2011
2012
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
2023
2024
2025
2026
2027
2028
2029
2030
2031
2032
2033
2034
2035
2036
2037
2038
2039
2040
2041
2042
2043
2044
2045
2046
2047
2048
2049
2050
2051
2052
2053
2054
2055
2056
2057
2058
2059
2060
2061
2062
2063
2064
2065
2066
2067
2068
2069
2070
2071
2072
2073
2074
2075
2076
2077
2078
2079
2080
2081
2082
2083
2084
2085
2086
2087
2088
2089
2090
2091
2092
2093
2094
2095
2096
2097
2098
2099
2100
2101
2102
2103
2104
2105
2106
2107
2108
2109
2110
2111
2112
2113
2114
2115
2116
2117
2118
2119
2120
2121
2122
2123
2124
2125
2126
2127
2128
2129
2130
2131
2132
2133
2134
2135
2136
2137
2138
2139
2140
2141
2142
2143
2144
2145
2146
2147
2148
2149
2150
2151
2152
2153
2154
2155
2156
2157
2158
2159
2160
2161
2162
2163
2164
2165
2166
2167
2168
2169
2170
2171
2172
2173
2174
2175
2176
2177
2178
2179
2180
2181
2182
2183
2184
2185
2186
2187
2188
2189
2190
2191
2192
2193
2194
2195
2196
2197
2198
2199
2200
2201
2202
2203
2204
2205
2206
2207
2208
2209
2210
2211
2212
2213
2214
2215
2216
2217
2218
2219
2220
2221
2222
2223
2224
2225
2226
2227
2228
2229
2230
2231
2232
2233
2234
2235
2236
2237
2238
2239
2240
2241
2242
2243
2244
2245
2246
2247
2248
2249
2250
2251
2252
2253
2254
2255
2256
2257
2258
2259
2260
2261
2262
2263
2264
2265
2266
2267
2268
2269
2270
2271
2272
2273
2274
2275
2276
2277
2278
2279
2280
2281
2282
2283
2284
2285
2286
2287
2288
2289
2290
2291
2292
2293
2294
2295
2296
2297
2298
2299
2300
2301
2302
2303
2304
2305
2306
2307
2308
2309
2310
2311
2312
2313
2314
2315
2316
2317
2318
2319
2320
2321
2322
2323
2324
2325
2326
2327
2328
2329
2330
2331
2332
2333
2334
2335
2336
2337
2338
2339
2340
2341
2342
2343
2344
2345
2346
2347
2348
2349
2350
2351
2352
2353
2354
2355
2356
2357
2358
2359
2360
2361
2362
2363
2364
2365
2366
2367
2368
2369
2370
2371
2372
2373
2374
2375
2376
2377
2378
2379
2380
2381
2382
2383
2384
2385
2386
2387
2388
2389
2390
2391
2392
2393
2394
2395
2396
2397
2398
2399
2400
2401
2402
2403
2404
2405
2406
2407
2408
2409
2410
2411
2412
2413
2414
2415
2416
2417
2418
2419
2420
2421
2422
2423
2424
2425
2426
2427
2428
2429
2430
2431
2432
2433
2434
2435
2436
2437
2438
2439
2440
2441
2442
2443
2444
2445
2446
2447
2448
2449
2450
2451
2452
2453
2454
2455
2456
2457
2458
2459
2460
2461
2462
2463
2464
2465
2466
2467
2468
2469
2470
2471
2472
2473
2474
2475
2476
2477
2478
2479
2480
2481
2482
2483
2484
2485
2486
2487
2488
2489
2490
2491
2492
2493
2494
2495
2496
2497
2498
2499
2500
2501
2502
2503
2504
2505
2506
2507
2508
2509
2510
2511
2512
2513
2514
2515
2516
2517
2518
2519
2520
2521
2522
2523
2524
2525
2526
2527
2528
2529
2530
2531
2532
2533
2534
2535
2536
2537
2538
2539
2540
2541
2542
2543
2544
2545
2546
2547
2548
2549
2550
2551
2552
2553
2554
2555
2556
2557
2558
2559
2560
2561
2562
2563
2564
2565
2566
2567
2568
2569
2570
2571
2572
2573
2574
2575
2576
2577
2578
2579
2580
2581
2582
2583
2584
2585
2586
2587
2588
2589
2590
2591
2592
2593
2594
2595
2596
2597
2598
2599
2600
2601
2602
2603
2604
2605
2606
2607
2608
2609
2610
2611
2612
2613
2614
2615
2616
2617
2618
2619
2620
2621
2622
2623
2624
2625
2626
2627
2628
2629
2630
2631
2632
2633
2634
2635
2636
2637
2638
2639
2640
2641
2642
2643
2644
2645
2646
2647
2648
2649
2650
2651
2652
2653
2654
2655
2656
2657
2658
2659
2660
2661
2662
2663
2664
2665
2666
2667
2668
2669
2670
2671
2672
2673
2674
2675
2676
2677
2678
2679
2680
2681
2682
2683
2684
2685
2686
2687
2688
2689
2690
2691
2692
2693
2694
2695
2696
2697
2698
2699
2700
2701
2702
2703
2704
2705
2706
2707
2708
2709
2710
2711
2712
2713
2714
2715
2716
2717
2718
2719
2720
2721
2722
2723
2724
2725
2726
2727
2728
2729
2730
2731
2732
2733
2734
2735
2736
2737
2738
2739
2740
2741
2742
2743
2744
2745
2746
2747
2748
2749
2750
2751
2752
2753
2754
2755
2756
2757
2758
2759
2760
2761
2762
2763
2764
2765
2766
2767
2768
2769
2770
2771
2772
2773
2774
2775
2776
2777
2778
2779
2780
2781
2782
2783
2784
2785
2786
2787
2788
2789
2790
2791
2792
2793
2794
2795
2796
2797
2798
2799
2800
2801
2802
2803
2804
2805
2806
2807
2808
2809
2810
2811
2812
2813
2814
2815
2816
2817
2818
2819
2820
2821
2822
2823
2824
2825
2826
2827
2828
2829
2830
2831
2832
2833
2834
2835
2836
2837
2838
2839
2840
2841
2842
2843
2844
2845
2846
2847
2848
2849
2850
2851
2852
2853
2854
2855
2856
2857
2858
2859
2860
2861
2862
2863
2864
2865
2866
2867
2868
2869
2870
2871
2872
2873
2874
2875
2876
2877
2878
2879
2880
2881
2882
2883
2884
2885
2886
2887
2888
2889
2890
2891
2892
2893
2894
2895
2896
2897
2898
2899
2900
2901
2902
2903
2904
2905
2906
2907
2908
2909
2910
2911
2912
2913
2914
2915
2916
2917
2918
2919
2920
2921
2922
2923
2924
2925
2926
2927
2928
2929
2930
2931
2932
2933
2934
2935
2936
2937
2938
2939
2940
2941
2942
2943
2944
2945
2946
2947
2948
2949
2950
2951
2952
2953
2954
2955
2956
2957
2958
2959
2960
2961
2962
2963
2964
2965
2966
2967
2968
2969
2970
2971
2972
2973
2974
2975
2976
2977
2978
2979
2980
2981
2982
2983
2984
2985
2986
2987
2988
2989
2990
2991
2992
2993
2994
2995
2996
2997
2998
2999
3000

## Design (numerical)
module : |  |  |  | range | input 1 |  | input 2 |  | input 3
|  |  | modules per string : | 7 - 15
|  |  | no. of strings : | 3 - 7
location :
orientation :
|  | Compatability check | [10 empty] | Kleurcodes
gradient :
[5 empty] | input 1 |  | input 2 |  | input 3 |  | input 4 |  | Ingang 1: | Ingang 2: | Ingang 3: | Ingang 4:
|  |  | string nominal power : |  | 2200 |  | 2200 |  | 1000 |  | 200
temp. of module : |  |  | total PV power : |  | 11000 |  | 11000 |  | 1000 |  | 200
|  |  | orientation correction PV power : |  | 11000 | 0.93718 | 11000 | 0.93718 | 1000 | 10.309 | 200 | 51.545 | 1 | 1 | 3 | 3
| Max. : |  | underdimensionings result : |  | 9900 |  | 9900 |  | 900 |  | 180
|  |  | converted at max irradiation : |  | 9900 | 100% | 9900 | 100% | 0 | 0% | 0 | 0% | 1 | 1 | 4 | 4
| Min. : |  | startup voltage : |  | 418 | OK | 418 | OK | 190 | too low | 38 | too low | 1 | 1 | 3 | 3
|  |  | Umpp at 45°C : |  | 488.015 |  | 488.015 |  | 221.825 |  | 44.365
underdimensioning [UDF] : |  |  | Umpp at 25°C : |  | 522.5 |  | 522.5 |  | 237.5 |  | 47.5
|  |  | Umpp at -10°C : |  | 582.8487 | OK | 582.8487 | OK | 264.9312 | OK | 52.9862 | too low | 1 | 1 | 1 | 3
cos(φ)= |  |  | Uoc at -10°C : |  | 705.5538 | OK | 705.5538 | OK | 320.7063 | OK | 64.1412 | too low | 1 | 1 | 1 | 3
|  |  | possible inverter current at 45°C : |  | 21.1244 |  | 21.1244 |  | 0 |  | 0
inverter : |  |  | Ipv at 45°C : |  | 20.2863 | OK | 20.2863 | OK | 4.0573 | OUT | 4.0573 | OUT | 1 | 1 | 3 | 3
|  |  | no. of modules : |  | 55 |  | 55 |  | 5 |  | 1
|  |  | total no. of modules : |  | 110 | [7 empty] | 2
Note on C23: Set to 1 exc ept for Germany, for more information see HELP page.

## INVERTERS (hidden)
|  | Geselecteerd: | 12
| 1 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51
|  | For Inverter specs | [30 empty] | For Calculations
|  | General Information | [9 empty] | Solar Input (DC) | [10 empty] | Grid Output (AC)
| Model | Typical string length | Operating temperature | Relative humidity | Protection degree | Noise level | Safety class | Galvanic isolation | Dimensions | Weight |  | Nom power | Max DC power | PV power range | MPP Tracker | Min DC voltage | MPP power range | Max MPP voltage | Max voltage | Rated current | String connections | Vnom | Voltage | Nom AC power | Max AC power | Nominal Current | Frequency | Power factor | THD | European efficiency | Max efficiency |  | Nom power | Rated current | U1 (Umin) | U2 (U_Imin) | U3 (Umpp_min) | U4 (Umpp_max) | U5 (Umax) |  | I1 | I2 | I3 | I4 | I5 |  | European efficiency |  | Aantal ingangen | Parallel Mode
| Soladin 120 | - | - | max. 95% | IP23 | -- | class II | class II | - | - |  | - | - | - | - | - | - | - | - | - | - |  | - | - | - | - | - | - | - | - | - | [17 empty] | 1 | UIT
1 | Soladin 600 | 72 cells: 2-3 / 54 cells: 3-4 / 36 cells: 4-6 | -20°C to 40°C | max. 95% | IP23 | -- | class II | class II | 350 x 143 x 75 | 2 kg |  | 550 | 600 | 160 - 700 Wp | 1 Dynamic MPP Tracker | 35 | 40 - 125 | 125 | 155 | 8A | 1 | 90 | 230 | 525 | 525 | 3.15 | 50 Hz | 0.99 | 5% | 0.91 | 0.93 |  | 575 | 8 | 40 | 65 | 71.875 | 139.5 | 155 |  | 4.9231 | 8 | 8 | 4.1219 | 0 |  | 0.91 |  | 1 | UIT
2 | XS6500 IP44 | 4-12 72 cells modules or 8-24 36 cells modules | -20°C to 60°C | max. 95% | IP44 | -- | class I | class II | 725 x 350 x 145 mm | 15 kg |  | 5265 | 5525 | 4000-7000 Wp | 2 Dynamic MPP Trackers | 100 | 180-480V | 480 | 600 | 2 x 15A | 2 | 400 | 230 | 5000 | 5250 | 22 | 50/60Hz | 0.99 | < 3% | 0.95 | 0.96 |  | 2632 | 15 | 100 | 100 | 175.4667 | 540 | 600 |  | 15 | 15 | 15 | 4.8741 | 0 |  | 0.95 |  | 2 | UIT
3 | XS6500 IP44 parallel | 4-12 72 cells modules or 8-24 36 cells modules | -20°C to 60°C | max. 95% | IP44 | -- | class I | class II | 725 x 350 x 145 mm | 15 kg |  | 5265 | 5525 | 4000-7000 Wp | 1 Dynamic MPP Trackers | 100 | 180-480V | 480 | 600 | 1 x 30A | 2 | 400 | 230 | 5000 | 5250 | 22 | 50/60Hz | 0.99 | < 3% | 0.95 | 0.96 |  | 5264 | 30 | 100 | 100 | 175.4667 | 540 | 600 |  | 30 | 30 | 30 | 9.7481 | 0 |  | 0.95 |  | 2 | AAN
4 | XS6500 IP44 (4600W ac) | 4-12 72 cells modules or 8-24 36 cells modules | -20°C to 60°C | max. 95% | IP44 | -- | class I | class II | 725 x 350 x 145 mm | 15 kg |  | 4850 | 5250 | 4000-7000 Wp | 2 Dynamic MPP Trackers | 100 | 180-480V | 480 | 600 | 2 x 20A | 2 | 400 | 230 | 4600 | 5000 | 20 | 50/60Hz | 0.99 | < 3% | 0.95 | 0.96 |  | 2421 | 15 | 100 | 100 | 161.4 | 540 | 600 |  | 15 | 15 | 15 | 4.4833 | 0 |  | 0.95 |  | 2 | UIT
5 | XS6500 IP44 parallel (4600W ac) | 4-12 72 cells modules or 8-24 36 cells modules | -20°C to 60°C | max. 95% | IP44 | -- | class I | class II | 725 x 350 x 145 mm | 15 kg |  | 4850 | 5250 | 4000-7000 Wp | 1 Dynamic MPP Trackers | 100 | 180-480V | 480 | 600 | 1 x 30A | 2 | 400 | 230 | 4600 | 5000 | 20 | 50/60Hz | 0.99 | < 3% | 0.95 | 0.96 |  | 4842 | 30 | 100 | 100 | 161.4 | 540 | 600 |  | 30 | 30 | 30 | 8.9667 | 0 |  | 0.95 |  | 2 | AAN
6 | XS4300 | 5-11 72 cells modules or 8-23 36 cells modules | -20°C to 60°C | max. 95% | IP44 | -- | class I | class II | 540 x 356 x 142 mm | 10 kg |  | 3488.3721 | 3662.7907 | 2900-4350 Wp | 1 Dynamic MPP Trackers | 100 | 230-440V | 440 | 550 | 15A | 2 | 370 | 230 | 3300 | 3465 | 15 | 50/60Hz | 0.99 | < 3% | 0.946 | 0.956 |  | 3488.3721 | 15 | 100 | 100 | 232.5581 | 495 | 550 |  | 15 | 15 | 15 | 7.0472 | 0 |  | 0.946 |  | 1 | UIT
7 | XS3200 | 4-12 72 cells modules or 8-24 36 cells modules | -20°C to 60°C | max. 95% | IP44 | -- | class I | class II | 540 x 356 x 142 mm | 10 kg |  | 2651.1135 | 2783.6691 | 2200-3300 Wp | 1 Dynamic MPP Trackers | 100 | 180-480V | 480 | 600 | 15A | 2 | 400 | 230 | 2500 | 2625 | 11 | 50/60Hz | 0.99 | < 3% | 0.943 | 0.954 |  | 2651.1135 | 15 | 100 | 100 | 176.7409 | 540 | 600 |  | 15 | 15 | 15 | 4.9095 | 0 |  | 0.943 |  | 1 | UIT
8 | XS2000 | 3-9 72 cells modules or 5-18 36 cells modules | -20°C to 60°C | max. 95% | IP44 | -- | class I | class II | 540 x 356 x 142 mm | 10 kg |  | 1588.9831 | 1668.4322 | 1300-2000 Wp | 1 Dynamic MPP Trackers | 100 | 145-360V | 360 | 450 | 11A | 2 | 300 | 230 | 1500 | 1575 | 7 | 50/60Hz | 0.99 | < 3% | 0.944 | 0.957 |  | 1588.9831 | 11 | 100 | 100 | 144.453 | 405 | 450 |  | 11 | 11 | 11 | 3.9234 | 0 |  | 0.944 |  | 1 | UIT
9 | XL10k | 5-11 72 cells modules or 8-23 36 cells modules | -20°C to 60°C | max. 95% | IP55 | -- | class I | class II | 1400 x 650 x 480 mm | 135 kg |  | 10525 | 11000 | 9000-13000 Wp | 3 Dynamic MPP Trackers | 100 | 230-440V | 440 | 550 | 3 x 15A | 3 | 370 | 230 | 10000 | 10500 | 3 x 15 | 50/60Hz | 0.99 | < 3% | 0.95 | 0.96 |  | 3508 | 15 | 100 | 100 | 233.8667 | 495 | 550 |  | 15 | 15 | 15 | 7.0869 | 0 |  | 0.95 |  | 3 | UIT
10 | XL15k | 4-12 72 cells modules or 8-24 36 cells modules | -20°C to 60°C | max. 95% | IP55 | -- | class I | class II | 1400 x 650 x 480 mm | 135 kg |  | 15800 | 16600 | 14000-20000 Wp | 3 Dynamic MPP Trackers | 100 | 180-480V | 480 | 600 | 3 x 30A | 3 | 400 | 230 | 15000 | 15750 | 3 x 22 | 50/60Hz | 0.99 | < 3% | 0.95 | 0.96 |  | 5265 | 30 | 100 | 100 | 175.5 | 540 | 600 |  | 30 | 30 | 30 | 9.75 | 0 |  | 0.95 |  | 3 | UIT
11 | CS15TL | -- | -20°C to 60°C | max. 95% | IP65 | -- | class I | -- | 1000 x 650 x 250 mm | 65 kg |  | 15364 | 16237 | 13500-19000Wp | 2 Dynamic MPP Trackers | 250 | 350-800V | 800 | 950 | 2x 23A | 2 | 650 | 400 | 15000 | 15750 | 3 x 22 | 50/60Hz | 0.99 | < 3% | 0.97 | 0.98 |  | 7682 | 23 | 250 | 250 | 334 | 900 | 1000 |  | 23 | 23 | 23 | 8.5356 | 0 |  | 0.97 |  | 2 | UIT
12 | CS20TL | -- | -20°C to 60°C | max. 95% | IP65 | -- | class I | -- | 1000 x 650 x 250 mm | 65 kg |  | 20618 | 21649 | 18000-25000 Wp | 2 Dynamic MPP Trackers | 250 | 350-800V | 800 | 950 | 2x 30A | 2 | 650 | 400 | 20000 | 21000 | 3 x 30 | 50/60Hz | 0.99 | < 3% | 0.97 | 0.98 |  | 10309 | 30 | 250 | 250 | 343.6333 | 900 | 1000 |  | 30 | 30 | 30 | 11.4544 | 0 |  | 0.97 |  | 2 | UIT
13 | IS10 | 5-11 72 cells modules or 8-23 36 cells modules | -20°C to 60°C | max. 95% | IP23 | -- | class I | class II | 863 x 512 x 405 mm | 61 kg |  | 10525 | 11000 | 9000-13000 Wp | 3 Dynamic MPP Trackers | 100 | 230-440V | 440 | 550 | 3 x 15A | 3 | 370 | 230 | 10000 | 10500 | 3 x 15 | 50/60Hz | 0.99 | < 3% | 0.95 | 0.96 |  | 3508 | 15 | 100 | 100 | 233.8667 | 495 | 550 |  | 15 | 15 | 15 | 7.0869 | 0 |  | 0.95 |  | 3 | UIT
14 | IS15 | 4-12 72 cells modules or 8-24 36 cells modules | -20°C to 60°C | max. 95% | IP23 | -- | class I | class II | 864 x 512 x 405 mm | 61 kg |  | 15800 | 16600 | 14000-20000 Wp | 3 Dynamic MPP Trackers | 100 | 180-480V | 480 | 600 | 3 x 30A | 3 | 400 | 230 | 15000 | 15750 | 3 x 22 | 50/60Hz | 0.99 | < 3% | 0.95 | 0.96 |  | 5265 | 30 | 100 | 100 | 175.5 | 540 | 600 |  | 30 | 30 | 30 | 9.75 | 0 |  | 0.95 |  | 3 | UIT
Ready for insertion
Old Inverters (removed from interface)
2 | QS1200 | 5-9 72 cells modules or 10-18 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 340 x 250 x 107 mm | 4,4 kg |  | 950 | 1100 | 700-1200 Wp | 1 Dynamic MPP Tracker | 100 | 100-380V | 380 | 450 | 5A | 2 |  | 230 | 900 | 1050 | 6.3 | 50/60Hz | 0.99 | < 3% | 0.945 | 0.95 |  | 950 | 5 | 100 | 150 | 190 | 405 | 450 |  | 3.3333 | 5 | 5 | 2.3457 | 0 |  | 0.945 |  | 1 | UIT
3 | QS2000 IP44 | 5-9 72 cells modules or 10-18 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 340 x 250 x 130 mm | 6 kg |  | 1700 | 1800 | 1200-2100 Wp | 1 Dynamic MPP Tracker | 100 | 100-380V | 380 | 450 | 7,5A | 2 |  | 230 | 1600 | 1725 | 10 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 1700 | 7.5 | 100 | 180 | 226.6667 | 405 | 450 |  | 4.1667 | 7.5 | 7.5 | 4.1975 | 0 |  | 0.94 |  | 1 | UIT
8 | QS6400 | 5-9 72 cells modules or 10-18 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 240 mm | 14 kg |  | 5500 | 5900 | 3200-7200 Wp | 4 Dynamic MPP Trackers | 100 | 100-380V | 380 | 450 | 4 x 7,5A | 2 |  | 230 | 5200 | 5500 | 2 x 16 or 1 x 32 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 1375 | 7.5 | 100 | 180 | 183.3333 | 405 | 450 |  | 4.1667 | 7.5 | 7.5 | 3.3951 | 0 |  | 0.94 |  | 4 | UIT
9 | QS6400 parallel | 5-9 72 cells modules or 10-18 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 240 mm | 14 kg |  | 5500 | 5900 | 3200-7200 Wp | 2 Dynamic MPP Trackers | 100 | 100-380V | 380 | 450 | 2 x 15A | 2 |  | 230 | 5200 | 5500 | 2 x 16 or 1 x 32 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 2750 | 15 | 100 | 180 | 183.3333 | 405 | 450 |  | 8.3333 | 15 | 15 | 6.7901 | 0 |  | 0.94 |  | 4 | AAN
10 | QS6400 (4600W ac) | 5-9 72 cells modules or 10-18 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 240 mm | 14 kg |  | 4870 | 4870 | 3200-7200 Wp | 4 Dynamic MPP Trackers | 100 | 100-380V | 380 | 450 | 4 x 7,2A | 2 |  | 230 | 4600 | 4600 | 2 x 16 or 1 x 32 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 1217.5 | 7.1809 | 100 | 180 | 169.5471 | 405 | 450 |  | 4.2 | 7.1809 | 7.1809 | 3.0062 | 0 |  | 0.94 |  | 4 | UIT
11 | QS6400 parallel (4600W ac) | 5-9 72 cells modules or 10-18 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 240 mm | 14 kg |  | 4870 | 4870 | 3200-7200 Wp | 2 Dynamic MPP Trackers | 100 | 100-380V | 380 | 450 | 2 x 14,6A | 2 |  | 230 | 4600 | 4600 | 2 x 16 or 1 x 32 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 2435 | 14.1879 | 100 | 180 | 171.6251 | 405 | 450 |  | 8.3 | 14.1879 | 14.1879 | 6.0123 | 0 |  | 0.94 |  | 4 | AAN
12 | QS6400 Max-I | 4-6 72 cells modules or 8-12 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 240 mm | 14 kg |  | 5500 | 5900 | 3200-7200 Wp | 4 Dynamic MPP Trackers | 70 | 70-260V | 260 | 325 | 4 x 10A | 2 |  | 230 | 5200 | 5500 | 2 x 16 or 1 x 32 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 1375 | 10 | 70 | 125 | 137.5 | 292.5 | 325 |  | 5.6 | 10 | 10 | 4.7009 | 0 |  | 0.94 |  | 4 | UIT
13 | QS6400 Max-I parallel | 4-6 72 cells modules or 8-12 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 240 mm | 14 kg |  | 5500 | 5900 | 3200-7200 Wp | 2 Dynamic MPP Trackers | 70 | 70-260V | 260 | 325 | 2 x 20A | 2 |  | 230 | 5200 | 5500 | 2 x 16 or 1 x 32 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 2750 | 20 | 70 | 125 | 137.5 | 292.5 | 325 |  | 11.2 | 20 | 20 | 9.4017 | 0 |  | 0.94 |  | 4 | AAN
14 | QS6400 Max-I (4600W ac) | 4-6 72 cells modules or 8-12 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 240 mm | 14 kg |  | 4870 | 4870 | 3200-7200 Wp | 4 Dynamic MPP Trackers | 70 | 70-260V | 260 | 325 | 4 x 9,9A | 2 |  | 230 | 4600 | 4600 | 2 x 16 or 1 x 32 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 1217.5 | 9.8712 | 70 | 125 | 123.339 | 292.5 | 325 |  | 5.5279 | 9.8712 | 9.8712 | 4.1624 | 0 |  | 0.94 |  | 4 | UIT
15 | QS6400 Max-I parallel (4600W ac) | 4-6 72 cells modules or 8-12 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 240 mm | 14 kg |  | 4870 | 4870 | 3200-7200 Wp | 2 Dynamic MPP Trackers | 70 | 70-260V | 260 | 325 | 2 x 19,7A | 2 |  | 230 | 4600 | 4600 | 2 x 16 or 1 x 32 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 2435 | 19.7383 | 70 | 125 | 123.3643 | 292.5 | 325 |  | 11.0534 | 19.7383 | 19.7383 | 8.3248 | 0 |  | 0.94 |  | 4 | AAN
4 | QS3500 IP44 | 5-9 72 cells modules or 10-18 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 133 mm | 7 kg |  | 2750 | 2950 | 2000-3600 Wp | 2 Dynamic MPP Trackers | 100 | 100-380V | 380 | 450 | 2 x 7,5A | 2 |  | 230 | 2600 | 2750 | 16 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 1375 | 7.5 | 100 | 180 | 183.3333 | 405 | 450 |  | 4.1667 | 7.5 | 7.5 | 3.3951 | 0 |  | 0.94 |  | 2 | UIT
5 | QS3500 IP44 parallel | 5-9 72 cells modules or 10-18 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 133 mm | 7 kg |  | 2750 | 2950 | 2000-3600 Wp | 1 Dynamic MPP Tracker | 100 | 100-380V | 380 | 450 | 1 x 15A | 2 |  | 230 | 2600 | 2750 | 16 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 2750 | 15 | 100 | 180 | 183.3333 | 405 | 450 |  | 8.3333 | 15 | 15 | 6.7901 | 0 |  | 0.94 |  | 2 | AAN
2 | QS3500 IP44 Max-I | 4-6 72 cells modules or 8-12 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 133 mm | 7 kg |  | 2750 | 2950 | 2000-3600 Wp | 2 Dynamic MPP Tracker | 70 | 70-260V | 260 | 325 | 2 x 10A | 2 |  | 230 | 2600 | 2750 | 16 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 1375 | 10 | 70 | 125 | 137.5 | 292.5 | 325 |  | 5.6 | 10 | 10 | 4.7009 | 0 |  | 0.94 |  | 2 | UIT
3 | QS3500 IP44 Max-I parallel | 4-6 72 cells modules or 8-12 36 cells modules | -20°C to 50°C | max. 95% | IP23 | -- | class I | class II | 470 x 315 x 133 mm | 7 kg |  | 2750 | 2950 | 2000-3600 Wp | 1 Dynamic MPP Tracker | 70 | 70-260V | 260 | 325 | 1 x 20A | 2 |  | 230 | 2600 | 2750 | 16 | 50/60Hz | 0.99 | < 3% | 0.94 | 0.95 |  | 2750 | 20 | 70 | 125 | 137.5 | 292.5 | 325 |  | 11.2 | 20 | 20 | 9.4017 | 0 |  | 0.94 |  | 2 | AAN
15 | CP100TR | -- | 0°C to 50°C | max. 95% | IP20 | -- | class I | class II | 1900 x 1000 x 850 mm | < 1050 kg |  | 104000 | 115000 | 85000-13000 Wp | 1 Dynamic MPP Trackers | 450 | 450-820V | 820 | 900 | 260A | 1, opt 5 |  | 400 | 100000 | 110000 | 160 | 50/60Hz | > 0,98 | < 3% | 0.965 | 0.971 |  | 104000 | 260 | 450 | 450 | 450 | 820 | 900 |  | 260 | 260 | 260 | 126.8293 | 0 |  | 0.965 |  | 1 | UIT
16 | CP200TL | -- | 0°C to 50°C | max. 95% | IP21 | -- | class I | -- | 1900 x 1400 x 850 mm | < 1330 kg |  | 208000 | 230000 | 170000-260000 Wp | 1 Dynamic MPP Trackers | 450 | 450-820V | 820 | 900 | 500A | 1, opt 5 |  | 400 | 200000 | 220000 | 320 | 50/60Hz | > 0,98 | < 3% | 0.966 | 0.97 |  | 208000 | 500 | 450 | 450 | 450 | 820 | 900 |  | 500 | 500 | 500 | 253.6585 | 0 |  | 0.966 |  | 1 | UIT
17 | CP200TR | -- | 0°C to 50°C | max. 95% | IP22 | -- | class I | class II | 1900 x 1400 x 850 mm | < 1000 kg |  | 204000 | 230000 | 165000-255000 Wp | 1 Dynamic MPP Trackers | 450 | 450-820V | 820 | 900 | 500A | 1, opt 5 |  | 270 | 200000 | 224000 | 480 | 50/60Hz | > 0,98 | < 3% | 0.973 | 0.98 |  | 204000 | 500 | 450 | 450 | 450 | 820 | 900 |  | 500 | 500 | 500 | 248.7805 | 0 |  | 0.973 |  | 1 | UIT
18 | CP140TR-LV | -- | 0°C to 50°C | max. 95% | IP23 | -- | class I | class II | 1900 x 1400 x 850 mm | < 1200 kg |  | 147000 | 162000 | 120000-180000 Wp | 1 Dynamic MPP Trackers | 300 | 300-550V | 550 | 600 | 500A | 1, opt 5 |  | 400 | 140000 | 154000 | 500 | 50/60Hz | > 0,98 | < 3% | 0.955 | 0.962 |  | 147000 | 500 | 300 | 300 | 300 | 550 | 600 |  | 500 | 500 | 500 | 267.2727 | 0 |  | 0.955 |  | 1 | UIT

## Compatibiteit (hidden)
Compatibiliteits vergelijking
effect op Kleur
toegestane percentage energieverlies: |  |  | 3% | = | 97%
percentage nog extra toegestane onderdimenionering: |  |  | 5% | = | 0.855
| Kleurcode: | 1 | 2 | 3 | 4
| Betekenis: | OK | Toelaatbaar | Te laag | Te hoog
| input 1 |  |  | input 2 |  |  | input 3 |  |  | input 4
| Waarde | Status | Kleur | Waarde | Status | Kleur | Waarde | Status | Kleur | Waarde | Status | Kleur
Nominaal vermogen per string : | 2200 |  |  | 2200 |  |  | 1000 |  |  | 200
Totaal PV vermogen : | 11000 |  |  | 11000 |  |  | 1000 |  |  | 200
Orientatie correctie PV vermogen : | 11000 | 0.93718 | 1 | 11000 | 0.93718 | 1 | 1000 | 10.309 | 3 | 200 | 51.545 | 3
Onderdimensionerings resultaat : | 9900 |  |  | 9900 |  |  | 900 |  |  | 180
Omgezet vermogen : | 9900 | 100% | 1 | 9900 | 100% | 1 | 0 | 0% | 4 | 0 | 0% | 4
Opstartspanning : | 418 | OK | 1 | 418 | OK | 1 | 190 | too low | 3 | 38 | too low | 3
Umpp bij 50°C : | 488.015 |  |  | 488.015 |  |  | 221.825 |  |  | 44.365
Umpp bij 25°C : | 522.5 |  |  | 522.5 |  |  | 237.5 |  |  | 47.5
Umpp bij -10°C : | 582.8487 | OK | 1 | 582.8487 | OK | 1 | 264.9312 | OK | 1 | 52.9862 | too low | 3
Uoc bij -10°C : | 705.5538 | OK | 1 | 705.5538 | OK | 1 | 320.7063 | OK | 1 | 64.1412 | too low | 3
Mogelijke omvormerstroom bij 50°C : | 21.1244 |  |  | 21.1244 |  |  | 0 |  |  | 0
Ipv bij 50°C : | 20.2863 | OK | 1 | 20.2863 | OK | 1 | 4.0573 | OUT | 3 | 4.0573 | OUT | 3
488.015
522.5
Paneel / omvormer combinatie: | [8 empty] | *
Kleur
Paneel / omvormer combinatie: | 1
Ingang 1: | Onderdimensionering: |  | U1<=Umpp<U2 : |  | The connected PV power is optimal
|  |  | U2<=Umpp<U3 : |  | The connected PV power is optimal
|  |  | U3<=Umpp<U4 : |  | The connected PV power is optimal | [6 empty] | *
|  |  | U4<=Umpp<U5 : |  | The connected PV power is optimal
U1<Umpp of Umpp>U5 :
|  |  | => |  | The connected PV power is optimal
| Stroom: |  | The inverter will convert all the available solar power
| Energieomzetting: |  | Optimal energy conversion of available solar power
| Opstartspanning: |  | The startup voltage is optimal
| Umpp bij -10°C: |  | The MPP-voltage at min module temperature is optimal
| Uoc bij -10°C : |  | The open circuit voltage at min module temperature is within the operating window
Ingang 2: | Onderdimensionering: |  | U1<=Umpp<U2 : |  | The connected PV power is optimal
|  |  | U2<=Umpp<U3 : |  | The connected PV power is optimal
|  |  | U3<=Umpp<U4 : |  | The connected PV power is optimal | [6 empty] | *
|  |  | U4<=Umpp<U5 : |  | The connected PV power is optimal
U1<Umpp of Umpp>U5 :
|  |  | => |  | The connected PV power is optimal
| Stroom: |  | The inverter will convert all the available solar power
| Energieomzetting: |  | Optimal energy conversion of available solar power
| Opstartspanning: |  | The startup voltage is optimal
| Umpp bij -10°C: |  | The MPP-voltage at min module temperature is optimal
| Uoc bij -10°C : |  | The open circuit voltage at min module temperature is within the operating window
Ingang 3: | Onderdimensionering: |  | U1<=Umpp<U2 : |  | No complete conversion
|  |  | U2<=Umpp<U3 : |  | No complete conversion
|  |  | U3<=Umpp<U4 : |  | The connected PV power is too low
|  |  | U4<=Umpp<U5 : |  | No complete conversion
|  |  | U1<Umpp of Umpp>U5 : | [8 empty] | *
|  |  | => |  | No complete conversion
| Stroom: |  | Umpp < 100V
| Energieomzetting: |  | This configuration has a relatively high energy loss at max irradiation
| Opstartspanning: |  | The startup voltage is too low
| Umpp bij -10°C: |  | The MPP-voltage at min module temperature is optimal
| Uoc bij -10°C : |  | The open circuit voltage at min module temperature is within the operating window
Ingang 4: | Onderdimensionering: |  | U1<=Umpp<U2 : |  | No complete conversion
|  |  | U2<=Umpp<U3 : |  | No complete conversion
|  |  | U3<=Umpp<U4 : |  | The connected PV power is too low
|  |  | U4<=Umpp<U5 : |  | No complete conversion
|  |  | U1<Umpp of Umpp>U5 : | [8 empty] | *
|  |  | => |  | No complete conversion
| Stroom: |  | Umpp < 100V
| Energieomzetting: |  | This configuration has a relatively high energy loss at max irradiation
| Opstartspanning: |  | The startup voltage is too low
| Umpp bij -10°C: |  | The MPP-voltage is too low
| Uoc bij -10°C : |  | The open circuit voltage at min module temperature is too low

## Inv. karakteristiek (hidden)
OMVORMER KARAKTERISTIEK
Geselecteerd: |  | V | Pmin | P_OK | Pnom | Pmax |  | Inverter
|  | 0 | 0 | 0 | 0 | 0 |  | 0
Omvormer : | CS20TL | 1 | 0 | 0 | 0 | 0 |  | 0
|  | 2 | 0 | 0 | 0 | 0 |  | 0
Spec data |  | 3 | 0 | 0 | 0 | 0 |  | 0
U1 | 250 | 4 | 0 | 0 | 0 | 0 |  | 0
U2 | 250 | 5 | 0 | 0 | 0 | 0 |  | 0
Imax | 30 | 6 | 0 | 0 | 0 | 0 |  | 0
Pnom | 10309 | 7 | 0 | 0 | 0 | 0 |  | 0
U4 | 900 | 8 | 0 | 0 | 0 | 0 |  | 0
U5 | 1000 | 9 | 0 | 0 | 0 | 0 |  | 0
|  | 10 | 0 | 0 | 0 | 0 |  | 0
Pnom |  | 11 | 0 | 0 | 0 | 0 |  | 0
I1= | 30 | 12 | 0 | 0 | 0 | 0 |  | 0
U3= | 343.6333 | 13 | 0 | 0 | 0 | 0 |  | 0
I4= | 11.4544 | 14 | 0 | 0 | 0 | 0 | 253 | 0 | #REF! | #REF! | #REF! | #REF! | #REF!
|  | 15 | 0 | 0 | 0 | 0 |  | 0
U_f2f3= | 250 | 16 | 0 | 0 | 0 | 0 |  | 0
I_f2f3= | 30 | 17 | 0 | 0 | 0 | 0 |  | 0
|  | 18 | 0 | 0 | 0 | 0 |  | 0
Pmin |  | 19 | 0 | 0 | 0 | 0 |  | 0
factor: | 1.6667 | 20 | 0 | 0 | 0 | 0 |  | 0
Pmin= | 5566.86 | 21 | 0 | 0 | 0 | 0 |  | 0
|  | 22 | 0 | 0 | 0 | 0 |  | 0
I1= | 30 | 23 | 0 | 0 | 0 | 0 |  | 0
U3= | 185.562 | 24 | 0 | 0 | 0 | 0 |  | 0
I4= | 6.1854 | 25 | 0 | 0 | 0 | 0 |  | 0
|  | 26 | 0 | 0 | 0 | 0 |  | 0
U_f2f3= | 215.3845 | 27 | 0 | 0 | 0 | 0 |  | 0
I_f2f3= | 25.8461 | 28 | 0 | 0 | 0 | 0 |  | 0
|  | 29 | 0 | 0 | 0 | 0 |  | 0
U_Pmin_Pmax= | 209.9309 | 30 | 0 | 0 | 0 | 0 |  | 0
|  | 31 | 0 | 0 | 0 | 0 |  | 0
P_OK |  | 32 | 0 | 0 | 0 | 0 |  | 0
factor: | 1.25 | 33 | 0 | 0 | 0 | 0 |  | 0
P_OK= | 7422.48 | 34 | 0 | 0 | 0 | 0 |  | 0
|  | 35 | 0 | 0 | 0 | 0 |  | 0
I1= | 30 | 36 | 0 | 0 | 0 | 0 |  | 0
U3= | 247.416 | 37 | 0 | 0 | 0 | 0 |  | 0
I4= | 8.2472 | 38 | 0 | 0 | 0 | 0 |  | 0
|  | 39 | 0 | 0 | 0 | 0 |  | 0
U_f2f3= | 248.7046 | 40 | 0 | 0 | 0 | 0 |  | 0
I_f2f3= | 29.8446 | 41 | 0 | 0 | 0 | 0 |  | 0
|  | 42 | 0 | 0 | 0 | 0 |  | 0
P_max |  | 43 | 0 | 0 | 0 | 0 |  | 0
factor: | 0.85 | 44 | 0 | 0 | 0 | 0 |  | 0
P_max= | 10915.4118 | 45 | 0 | 0 | 0 | 0 |  | 0
|  | 46 | 0 | 0 | 0 | 0 |  | 0
Imax_Pmax: | 31.5789 | 47 | 0 | 0 | 0 | 0 |  | 0
|  | 48 | 0 | 0 | 0 | 0 |  | 0
I1= | 31.5789 | 49 | 0 | 0 | 0 | 0 |  | 0
U3= | 345.6547 | 50 | 0 | 0 | 0 | 0 |  | 0
I4= | 12.1282 | 51 | 0 | 0 | 0 | 0 |  | 0
|  | 52 | 0 | 0 | 0 | 0 |  | 0
U_f2f3= | 293.962 | 53 | 0 | 0 | 0 | 0 |  | 0
I_f2f3= | 30 | 54 | 0 | 0 | 0 | 0 |  | 0
|  | 55 | 0 | 0 | 0 | 0 |  | 0
U_Duty_Pmax= | 335.5337 | 56 | 0 | 0 | 0 | 0 |  | 0
|  | 57 | 0 | 0 | 0 | 0 |  | 0
Voor Taal bij grafiek: |  | 58 | 0 | 0 | 0 | 0 |  | 0
Inverter & PV-Array Characteristic |  | 59 | 0 | 0 | 0 | 0 |  | 0
inverter |  | 60 | 0 | 0 | 0 | 0 |  | 0
PV-Array 1 |  | 61 | 0 | 0 | 0 | 0 |  | 0
PV-Array 2 |  | 62 | 0 | 0 | 0 | 0 |  | 0
|  | 63 | 0 | 0 | 0 | 0 |  | 0
|  | 64 | 0 | 0 | 0 | 0 |  | 0
|  | 65 | 0 | 0 | 0 | 0 |  | 0
UDF > 1,67 or < 0.85 |  | 66 | 0 | 0 | 0 | 0 |  | 0
UDF 1,67 - 1,25 or 0.9 - 0.85 |  | 67 | 0 | 0 | 0 | 0 |  | 0
UDF 1,25 - 0.9 |  | 68 | 0 | 0 | 0 | 0 |  | 0
|  | 69 | 0 | 0 | 0 | 0 |  | 0
|  | 70 | 0 | 0 | 0 | 0 |  | 0
|  | 71 | 0 | 0 | 0 | 0 |  | 0
|  | 72 | 0 | 0 | 0 | 0 |  | 0
|  | 73 | 0 | 0 | 0 | 0 |  | 0
|  | 74 | 0 | 0 | 0 | 0 |  | 0
|  | 75 | 0 | 0 | 0 | 0 |  | 0
|  | 76 | 0 | 0 | 0 | 0 |  | 0
|  | 77 | 0 | 0 | 0 | 0 |  | 0
|  | 78 | 0 | 0 | 0 | 0 |  | 0
|  | 79 | 0 | 0 | 0 | 0 |  | 0
|  | 80 | 0 | 0 | 0 | 0 |  | 0
|  | 81 | 0 | 0 | 0 | 0 |  | 0
|  | 82 | 0 | 0 | 0 | 0 |  | 0
|  | 83 | 0 | 0 | 0 | 0 |  | 0
|  | 84 | 0 | 0 | 0 | 0 |  | 0
|  | 85 | 0 | 0 | 0 | 0 |  | 0
|  | 86 | 0 | 0 | 0 | 0 |  | 0
|  | 87 | 0 | 0 | 0 | 0 |  | 0
|  | 88 | 0 | 0 | 0 | 0 |  | 0
|  | 89 | 0 | 0 | 0 | 0 |  | 0
|  | 90 | 0 | 0 | 0 | 0 |  | 0
|  | 91 | 0 | 0 | 0 | 0 |  | 0
|  | 92 | 0 | 0 | 0 | 0 |  | 0
|  | 93 | 0 | 0 | 0 | 0 |  | 0
|  | 94 | 0 | 0 | 0 | 0 |  | 0
|  | 95 | 0 | 0 | 0 | 0 |  | 0
|  | 96 | 0 | 0 | 0 | 0 |  | 0
|  | 97 | 0 | 0 | 0 | 0 |  | 0
|  | 98 | 0 | 0 | 0 | 0 |  | 0
|  | 99 | 0 | 0 | 0 | 0 |  | 0
|  | 100 | 0 | 0 | 0 | 0 |  | 0
|  | 101 | 0 | 0 | 0 | 0 |  | 0
|  | 102 | 0 | 0 | 0 | 0 |  | 0
|  | 103 | 0 | 0 | 0 | 0 |  | 0
|  | 104 | 0 | 0 | 0 | 0 |  | 0
|  | 105 | 0 | 0 | 0 | 0 |  | 0
|  | 106 | 0 | 0 | 0 | 0 |  | 0
|  | 107 | 0 | 0 | 0 | 0 |  | 0
|  | 108 | 0 | 0 | 0 | 0 |  | 0
|  | 109 | 0 | 0 | 0 | 0 |  | 0
|  | 110 | 0 | 0 | 0 | 0 |  | 0
|  | 111 | 0 | 0 | 0 | 0 |  | 0
|  | 112 | 0 | 0 | 0 | 0 |  | 0
|  | 113 | 0 | 0 | 0 | 0 |  | 0
|  | 114 | 0 | 0 | 0 | 0 |  | 0
|  | 115 | 0 | 0 | 0 | 0 |  | 0
|  | 116 | 0 | 0 | 0 | 0 |  | 0
|  | 117 | 0 | 0 | 0 | 0 |  | 0
|  | 118 | 0 | 0 | 0 | 0 |  | 0
|  | 119 | 0 | 0 | 0 | 0 |  | 0
|  | 120 | 0 | 0 | 0 | 0 |  | 0
|  | 121 | 0 | 0 | 0 | 0 |  | 0
|  | 122 | 0 | 0 | 0 | 0 |  | 0
|  | 123 | 0 | 0 | 0 | 0 |  | 0
|  | 124 | 0 | 0 | 0 | 0 |  | 0
|  | 125 | 0 | 0 | 0 | 0 |  | 0
|  | 126 | 0 | 0 | 0 | 0 |  | 0
|  | 127 | 0 | 0 | 0 | 0 |  | 0
|  | 128 | 0 | 0 | 0 | 0 |  | 0
|  | 129 | 0 | 0 | 0 | 0 |  | 0
|  | 130 | 0 | 0 | 0 | 0 |  | 0
|  | 131 | 0 | 0 | 0 | 0 |  | 0
|  | 132 | 0 | 0 | 0 | 0 |  | 0
|  | 133 | 0 | 0 | 0 | 0 |  | 0
|  | 134 | 0 | 0 | 0 | 0 |  | 0
|  | 135 | 0 | 0 | 0 | 0 |  | 0
|  | 136 | 0 | 0 | 0 | 0 |  | 0
|  | 137 | 0 | 0 | 0 | 0 |  | 0
|  | 138 | 0 | 0 | 0 | 0 |  | 0
|  | 139 | 0 | 0 | 0 | 0 |  | 0
|  | 140 | 0 | 0 | 0 | 0 |  | 0
|  | 141 | 0 | 0 | 0 | 0 |  | 0
|  | 142 | 0 | 0 | 0 | 0 |  | 0
|  | 143 | 0 | 0 | 0 | 0 |  | 0
|  | 144 | 0 | 0 | 0 | 0 |  | 0
|  | 145 | 0 | 0 | 0 | 0 |  | 0
|  | 146 | 0 | 0 | 0 | 0 |  | 0
|  | 147 | 0 | 0 | 0 | 0 |  | 0
|  | 148 | 0 | 0 | 0 | 0 |  | 0
|  | 149 | 0 | 0 | 0 | 0 |  | 0
|  | 150 | 0 | 0 | 0 | 0 |  | 0
|  | 151 | 0 | 0 | 0 | 0 |  | 0
|  | 152 | 0 | 0 | 0 | 0 |  | 0
|  | 153 | 0 | 0 | 0 | 0 |  | 0
|  | 154 | 0 | 0 | 0 | 0 |  | 0
|  | 155 | 0 | 0 | 0 | 0 |  | 0
|  | 156 | 0 | 0 | 0 | 0 |  | 0
|  | 157 | 0 | 0 | 0 | 0 |  | 0
|  | 158 | 0 | 0 | 0 | 0 |  | 0
|  | 159 | 0 | 0 | 0 | 0 |  | 0
|  | 160 | 0 | 0 | 0 | 0 |  | 0
|  | 161 | 0 | 0 | 0 | 0 |  | 0
|  | 162 | 0 | 0 | 0 | 0 |  | 0
|  | 163 | 0 | 0 | 0 | 0 |  | 0
|  | 164 | 0 | 0 | 0 | 0 |  | 0
|  | 165 | 0 | 0 | 0 | 0 |  | 0
|  | 166 | 0 | 0 | 0 | 0 |  | 0
|  | 167 | 0 | 0 | 0 | 0 |  | 0
|  | 168 | 0 | 0 | 0 | 0 |  | 0
|  | 169 | 0 | 0 | 0 | 0 |  | 0
|  | 170 | 0 | 0 | 0 | 0 |  | 0
|  | 171 | 0 | 0 | 0 | 0 |  | 0
|  | 172 | 0 | 0 | 0 | 0 |  | 0
|  | 173 | 0 | 0 | 0 | 0 |  | 0
|  | 174 | 0 | 0 | 0 | 0 |  | 0
|  | 175 | 0 | 0 | 0 | 0 |  | 0
|  | 176 | 0 | 0 | 0 | 0 |  | 0
|  | 177 | 0 | 0 | 0 | 0 |  | 0
|  | 178 | 0 | 0 | 0 | 0 |  | 0
|  | 179 | 0 | 0 | 0 | 0 |  | 0
|  | 180 | 0 | 0 | 0 | 0 |  | 0
|  | 181 | 0 | 0 | 0 | 0 |  | 0
|  | 182 | 0 | 0 | 0 | 0 |  | 0
|  | 183 | 0 | 0 | 0 | 0 |  | 0
|  | 184 | 0 | 0 | 0 | 0 |  | 0
|  | 185 | 0 | 0 | 0 | 0 |  | 0
|  | 186 | 0 | 0 | 0 | 0 |  | 0
|  | 187 | 0 | 0 | 0 | 0 |  | 0
|  | 188 | 0 | 0 | 0 | 0 |  | 0
|  | 189 | 0 | 0 | 0 | 0 |  | 0
|  | 190 | 0 | 0 | 0 | 0 |  | 0
|  | 191 | 0 | 0 | 0 | 0 |  | 0
|  | 192 | 0 | 0 | 0 | 0 |  | 0
|  | 193 | 0 | 0 | 0 | 0 |  | 0
|  | 194 | 0 | 0 | 0 | 0 |  | 0
|  | 195 | 0 | 0 | 0 | 0 |  | 0
|  | 196 | 0 | 0 | 0 | 0 |  | 0
|  | 197 | 0 | 0 | 0 | 0 |  | 0
|  | 198 | 0 | 0 | 0 | 0 |  | 0
|  | 199 | 0 | 0 | 0 | 0 |  | 0
|  | 200 | 0 | 0 | 0 | 0 |  | 0
|  | 201 | 0 | 0 | 0 | 0 |  | 0
|  | 202 | 0 | 0 | 0 | 0 |  | 0
|  | 203 | 0 | 0 | 0 | 0 |  | 0
|  | 204 | 0 | 0 | 0 | 0 |  | 0
|  | 205 | 0 | 0 | 0 | 0 |  | 0
|  | 206 | 0 | 0 | 0 | 0 |  | 0
|  | 207 | 0 | 0 | 0 | 0 |  | 0
|  | 208 | 0 | 0 | 0 | 0 |  | 0
|  | 209 | 0 | 0 | 0 | 0 |  | 0
|  | 210 | 0 | 0 | 0 | 0 |  | 0
|  | 211 | 0 | 0 | 0 | 0 |  | 0
|  | 212 | 0 | 0 | 0 | 0 |  | 0
|  | 213 | 0 | 0 | 0 | 0 |  | 0
|  | 214 | 0 | 0 | 0 | 0 |  | 0
|  | 215 | 0 | 0 | 0 | 0 |  | 0
|  | 216 | 0 | 0 | 0 | 0 |  | 0
|  | 217 | 0 | 0 | 0 | 0 |  | 0
|  | 218 | 0 | 0 | 0 | 0 |  | 0
|  | 219 | 0 | 0 | 0 | 0 |  | 0
|  | 220 | 0 | 0 | 0 | 0 |  | 0
|  | 221 | 0 | 0 | 0 | 0 |  | 0
|  | 222 | 0 | 0 | 0 | 0 |  | 0
|  | 223 | 0 | 0 | 0 | 0 |  | 0
|  | 224 | 0 | 0 | 0 | 0 |  | 0
|  | 225 | 0 | 0 | 0 | 0 |  | 0
|  | 226 | 0 | 0 | 0 | 0 |  | 0
|  | 227 | 0 | 0 | 0 | 0 |  | 0
|  | 228 | 0 | 0 | 0 | 0 |  | 0
|  | 229 | 0 | 0 | 0 | 0 |  | 0
|  | 230 | 0 | 0 | 0 | 0 |  | 0
|  | 231 | 0 | 0 | 0 | 0 |  | 0
|  | 232 | 0 | 0 | 0 | 0 |  | 0
|  | 233 | 0 | 0 | 0 | 0 |  | 0
|  | 234 | 0 | 0 | 0 | 0 |  | 0
|  | 235 | 0 | 0 | 0 | 0 |  | 0
|  | 236 | 0 | 0 | 0 | 0 |  | 0
|  | 237 | 0 | 0 | 0 | 0 |  | 0
|  | 238 | 0 | 0 | 0 | 0 |  | 0
|  | 239 | 0 | 0 | 0 | 0 |  | 0
|  | 240 | 0 | 0 | 0 | 0 |  | 0
|  | 241 | 0 | 0 | 0 | 0 |  | 0
|  | 242 | 0 | 0 | 0 | 0 |  | 0
|  | 243 | 0 | 0 | 0 | 0 |  | 0
|  | 244 | 0 | 0 | 0 | 0 |  | 0
|  | 245 | 0 | 0 | 0 | 0 |  | 0
|  | 246 | 0 | 0 | 0 | 0 |  | 0
|  | 247 | 0 | 0 | 0 | 0 |  | 0
|  | 248 | 0 | 0 | 0 | 0 |  | 0
|  | 249 | 0 | 0 | 0 | 0 |  | 0
|  | 250 | 22.2674 | 29.6899 | 30 | 31.5789 |  | 30
|  | 251 | 22.1787 | 29.5716 | 30 | 31.5789 |  | 30
|  | 252 | 22.0907 | 29.4543 | 30 | 31.5789 |  | 30
|  | 254 | 21.9168 | 29.2224 | 30 | 31.5789 |  | 30
|  | 255 | 21.8308 | 29.1078 | 30 | 31.5789 |  | 30
|  | 256 | 21.7455 | 28.9941 | 30 | 31.5789 |  | 30
|  | 257 | 21.6609 | 28.8812 | 30 | 31.5789 |  | 30
|  | 258 | 21.577 | 28.7693 | 30 | 31.5789 |  | 30
|  | 259 | 21.4937 | 28.6582 | 30 | 31.5789 |  | 30
|  | 260 | 21.411 | 28.548 | 30 | 31.5789 |  | 30
|  | 261 | 21.329 | 28.4386 | 30 | 31.5789 |  | 30
|  | 262 | 21.2476 | 28.3301 | 30 | 31.5789 |  | 30
|  | 263 | 21.1668 | 28.2224 | 30 | 31.5789 |  | 30
|  | 264 | 21.0866 | 28.1155 | 30 | 31.5789 |  | 30
|  | 265 | 21.007 | 28.0094 | 30 | 31.5789 |  | 30
|  | 266 | 20.928 | 27.9041 | 30 | 31.5789 |  | 30
|  | 267 | 20.8497 | 27.7996 | 30 | 31.5789 |  | 30
|  | 268 | 20.7719 | 27.6958 | 30 | 31.5789 |  | 30
|  | 269 | 20.6946 | 27.5929 | 30 | 31.5789 |  | 30
|  | 270 | 20.618 | 27.4907 | 30 | 31.5789 |  | 30
|  | 271 | 20.5419 | 27.3892 | 30 | 31.5789 |  | 30
|  | 272 | 20.4664 | 27.2885 | 30 | 31.5789 |  | 30
|  | 273 | 20.3914 | 27.1886 | 30 | 31.5789 |  | 30
|  | 274 | 20.317 | 27.0893 | 30 | 31.5789 |  | 30
|  | 275 | 20.2431 | 26.9908 | 30 | 31.5789 |  | 30
|  | 276 | 20.1698 | 26.893 | 30 | 31.5789 |  | 30
|  | 277 | 20.097 | 26.796 | 30 | 31.5789 |  | 30
|  | 278 | 20.0247 | 26.6996 | 30 | 31.5789 |  | 30
|  | 279 | 19.9529 | 26.6039 | 30 | 31.5789 |  | 30
|  | 280 | 19.8816 | 26.5089 | 30 | 31.5789 |  | 30
|  | 281 | 19.8109 | 26.4145 | 30 | 31.5789 |  | 30
|  | 282 | 19.7406 | 26.3209 | 30 | 31.5789 |  | 30
|  | 283 | 19.6709 | 26.2278 | 30 | 31.5789 |  | 30
|  | 284 | 19.6016 | 26.1355 | 30 | 31.5789 |  | 30
|  | 285 | 19.5328 | 26.0438 | 30 | 31.5789 |  | 30
|  | 286 | 19.4645 | 25.9527 | 30 | 31.5789 |  | 30
|  | 287 | 19.3967 | 25.8623 | 30 | 31.5789 |  | 30
|  | 288 | 19.3294 | 25.7725 | 30 | 31.5789 |  | 30
|  | 289 | 19.2625 | 25.6833 | 30 | 31.5789 |  | 30
|  | 290 | 19.1961 | 25.5948 | 30 | 31.5789 |  | 30
|  | 291 | 19.1301 | 25.5068 | 30 | 31.5789 |  | 30
|  | 292 | 19.0646 | 25.4195 | 30 | 31.5789 |  | 30
|  | 293 | 18.9995 | 25.3327 | 30 | 31.5789 |  | 30
|  | 294 | 18.9349 | 25.2465 | 30 | 31.5789 |  | 30
|  | 295 | 18.8707 | 25.1609 | 30 | 31.5789 |  | 30
|  | 296 | 18.807 | 25.0759 | 30 | 31.5789 |  | 30
|  | 297 | 18.7436 | 24.9915 | 30 | 31.5789 |  | 30
|  | 298 | 18.6807 | 24.9077 | 30 | 31.5789 |  | 30
|  | 299 | 18.6183 | 24.8243 | 30 | 31.5789 |  | 30
|  | 300 | 18.5562 | 24.7416 | 30 | 31.5789 |  | 30
|  | 301 | 18.4946 | 24.6594 | 30 | 31.5789 |  | 30
|  | 302 | 18.4333 | 24.5777 | 30 | 31.5789 |  | 30
|  | 303 | 18.3725 | 24.4966 | 30 | 31.5789 |  | 30
|  | 304 | 18.312 | 24.4161 | 30 | 31.5789 |  | 30
|  | 305 | 18.252 | 24.336 | 30 | 31.5789 |  | 30
|  | 306 | 18.1924 | 24.2565 | 30 | 31.5789 |  | 30
|  | 307 | 18.1331 | 24.1775 | 30 | 31.5789 |  | 30
|  | 308 | 18.0742 | 24.099 | 30 | 31.5789 |  | 30
|  | 309 | 18.0157 | 24.021 | 30 | 31.5789 |  | 30
|  | 310 | 17.9576 | 23.9435 | 30 | 31.5789 |  | 30
|  | 311 | 17.8999 | 23.8665 | 30 | 31.5789 |  | 30
|  | 312 | 17.8425 | 23.79 | 30 | 31.5789 |  | 30
|  | 313 | 17.7855 | 23.714 | 30 | 31.5789 |  | 30
|  | 314 | 17.7289 | 23.6385 | 30 | 31.5789 |  | 30
|  | 315 | 17.6726 | 23.5634 | 30 | 31.5789 |  | 30
|  | 316 | 17.6166 | 23.4889 | 30 | 31.5789 |  | 30
|  | 317 | 17.5611 | 23.4148 | 30 | 31.5789 |  | 30
|  | 318 | 17.5058 | 23.3411 | 30 | 31.5789 |  | 30
|  | 319 | 17.451 | 23.268 | 30 | 31.5789 |  | 30
|  | 320 | 17.3964 | 23.1953 | 30 | 31.5789 |  | 30
|  | 321 | 17.3422 | 23.123 | 30 | 31.5789 |  | 30
|  | 322 | 17.2884 | 23.0512 | 30 | 31.5789 |  | 30
|  | 323 | 17.2349 | 22.9798 | 30 | 31.5789 |  | 30
|  | 324 | 17.1817 | 22.9089 | 30 | 31.5789 |  | 30
|  | 325 | 17.1288 | 22.8384 | 30 | 31.5789 |  | 30
|  | 326 | 17.0763 | 22.7683 | 30 | 31.5789 |  | 30
|  | 327 | 17.024 | 22.6987 | 30 | 31.5789 |  | 30
|  | 328 | 16.9721 | 22.6295 | 30 | 31.5789 |  | 30
|  | 329 | 16.9205 | 22.5607 | 30 | 31.5789 |  | 30
|  | 330 | 16.8693 | 22.4924 | 30 | 31.5789 |  | 30
|  | 331 | 16.8183 | 22.4244 | 30 | 31.5789 |  | 30
|  | 332 | 16.7677 | 22.3569 | 30 | 31.5789 |  | 30
|  | 333 | 16.7173 | 22.2897 | 30 | 31.5789 |  | 30
|  | 334 | 16.6672 | 22.223 | 30 | 31.5789 |  | 30
|  | 335 | 16.6175 | 22.1567 | 30 | 31.5789 |  | 30
|  | 336 | 16.568 | 22.0907 | 30 | 31.5789 |  | 30
|  | 337 | 16.5189 | 22.0252 | 30 | 31.5789 |  | 30
|  | 338 | 16.47 | 21.96 | 30 | 31.5789 |  | 30
|  | 339 | 16.4214 | 21.8952 | 30 | 31.5789 |  | 30
|  | 340 | 16.3731 | 21.8308 | 30 | 31.5789 |  | 30
|  | 341 | 16.3251 | 21.7668 | 30 | 31.5789 |  | 30
|  | 342 | 16.2774 | 21.7032 | 30 | 31.5789 |  | 30
|  | 343 | 16.2299 | 21.6399 | 30 | 31.5789 |  | 30
|  | 344 | 16.1827 | 21.577 | 29.968 | 31.5453 |  | 29.968
|  | 345 | 16.1358 | 21.5144 | 29.8812 | 31.4539 |  | 29.8812
|  | 346 | 16.0892 | 21.4523 | 29.7948 | 31.3629 |  | 29.7948
|  | 347 | 16.0428 | 21.3904 | 29.7089 | 31.2726 |  | 29.7089
|  | 348 | 15.9967 | 21.329 | 29.6236 | 31.1827 |  | 29.6236
|  | 349 | 15.9509 | 21.2679 | 29.5387 | 31.0933 |  | 29.5387
|  | 350 | 15.9053 | 21.2071 | 29.4543 | 31.0045 |  | 29.4543
|  | 351 | 15.86 | 21.1467 | 29.3704 | 30.9162 |  | 29.3704
|  | 352 | 15.8149 | 21.0866 | 29.2869 | 30.8283 |  | 29.2869
|  | 353 | 15.7701 | 21.0269 | 29.204 | 30.741 |  | 29.204
|  | 354 | 15.7256 | 20.9675 | 29.1215 | 30.6542 |  | 29.1215
|  | 355 | 15.6813 | 20.9084 | 29.0394 | 30.5678 |  | 29.0394
|  | 356 | 15.6372 | 20.8497 | 28.9579 | 30.482 |  | 28.9579
|  | 357 | 15.5934 | 20.7913 | 28.8768 | 30.3966 |  | 28.8768
|  | 358 | 15.5499 | 20.7332 | 28.7961 | 30.3117 |  | 28.7961
|  | 359 | 15.5066 | 20.6754 | 28.7159 | 30.2272 |  | 28.7159
|  | 360 | 15.4635 | 20.618 | 28.6361 | 30.1433 |  | 28.6361
|  | 361 | 15.4207 | 20.5609 | 28.5568 | 30.0598 |  | 28.5568
|  | 362 | 15.3781 | 20.5041 | 28.4779 | 29.9767 |  | 28.4779
|  | 363 | 15.3357 | 20.4476 | 28.3994 | 29.8942 |  | 28.3994
|  | 364 | 15.2936 | 20.3914 | 28.3214 | 29.812 |  | 28.3214
|  | 365 | 15.2517 | 20.3356 | 28.2438 | 29.7304 |  | 28.2438
|  | 366 | 15.21 | 20.28 | 28.1667 | 29.6491 |  | 28.1667
|  | 367 | 15.1686 | 20.2247 | 28.0899 | 29.5683 |  | 28.0899
|  | 368 | 15.1273 | 20.1698 | 28.0136 | 29.488 |  | 28.0136
|  | 369 | 15.0863 | 20.1151 | 27.9377 | 29.4081 |  | 27.9377
|  | 370 | 15.0456 | 20.0608 | 27.8622 | 29.3286 |  | 27.8622
|  | 371 | 15.005 | 20.0067 | 27.7871 | 29.2495 |  | 27.7871
|  | 372 | 14.9647 | 19.9529 | 27.7124 | 29.1709 |  | 27.7124
|  | 373 | 14.9246 | 19.8994 | 27.6381 | 29.0927 |  | 27.6381
|  | 374 | 14.8847 | 19.8462 | 27.5642 | 29.0149 |  | 27.5642
|  | 375 | 14.845 | 19.7933 | 27.4907 | 28.9375 |  | 27.4907
|  | 376 | 14.8055 | 19.7406 | 27.4176 | 28.8606 |  | 27.4176
|  | 377 | 14.7662 | 19.6883 | 27.3448 | 28.784 |  | 27.3448
|  | 378 | 14.7271 | 19.6362 | 27.2725 | 28.7079 |  | 27.2725
|  | 379 | 14.6883 | 19.5844 | 27.2005 | 28.6321 |  | 27.2005
|  | 380 | 14.6496 | 19.5328 | 27.1289 | 28.5568 |  | 27.1289
|  | 381 | 14.6112 | 19.4816 | 27.0577 | 28.4818 |  | 27.0577
|  | 382 | 14.5729 | 19.4306 | 26.9869 | 28.4073 |  | 26.9869
|  | 383 | 14.5349 | 19.3798 | 26.9164 | 28.3331 |  | 26.9164
|  | 384 | 14.497 | 19.3294 | 26.8464 | 28.2593 |  | 26.8464
|  | 385 | 14.4594 | 19.2792 | 26.7766 | 28.1859 |  | 26.7766
|  | 386 | 14.4219 | 19.2292 | 26.7073 | 28.1129 |  | 26.7073
|  | 387 | 14.3847 | 19.1795 | 26.6382 | 28.0403 |  | 26.6382
|  | 388 | 14.3476 | 19.1301 | 26.5696 | 27.968 |  | 26.5696
|  | 389 | 14.3107 | 19.0809 | 26.5013 | 27.8961 |  | 26.5013
|  | 390 | 14.274 | 19.032 | 26.4333 | 27.8246 |  | 26.4333
|  | 391 | 14.2375 | 18.9833 | 26.3657 | 27.7534 |  | 26.3657
|  | 392 | 14.2012 | 18.9349 | 26.2985 | 27.6826 |  | 26.2985
|  | 393 | 14.165 | 18.8867 | 26.2316 | 27.6122 |  | 26.2316
|  | 394 | 14.1291 | 18.8388 | 26.165 | 27.5421 |  | 26.165
|  | 395 | 14.0933 | 18.7911 | 26.0987 | 27.4724 |  | 26.0987
|  | 396 | 14.0577 | 18.7436 | 26.0328 | 27.403 |  | 26.0328
|  | 397 | 14.0223 | 18.6964 | 25.9673 | 27.334 |  | 25.9673
|  | 398 | 13.9871 | 18.6494 | 25.902 | 27.2653 |  | 25.902
|  | 399 | 13.952 | 18.6027 | 25.8371 | 27.1969 |  | 25.8371
|  | 400 | 13.9171 | 18.5562 | 25.7725 | 27.1289 |  | 25.7725
|  | 401 | 13.8824 | 18.5099 | 25.7082 | 27.0613 |  | 25.7082
|  | 402 | 13.8479 | 18.4639 | 25.6443 | 26.994 |  | 25.6443
|  | 403 | 13.8135 | 18.4181 | 25.5806 | 26.927 |  | 25.5806
|  | 404 | 13.7794 | 18.3725 | 25.5173 | 26.8603 |  | 25.5173
|  | 405 | 13.7453 | 18.3271 | 25.4543 | 26.794 |  | 25.4543
|  | 406 | 13.7115 | 18.282 | 25.3916 | 26.728 |  | 25.3916
|  | 407 | 13.6778 | 18.2371 | 25.3292 | 26.6624 |  | 25.3292
|  | 408 | 13.6443 | 18.1924 | 25.2672 | 26.597 |  | 25.2672
|  | 409 | 13.6109 | 18.1479 | 25.2054 | 26.532 |  | 25.2054
|  | 410 | 13.5777 | 18.1036 | 25.1439 | 26.4673 |  | 25.1439
|  | 411 | 13.5447 | 18.0596 | 25.0827 | 26.4029 |  | 25.0827
|  | 412 | 13.5118 | 18.0157 | 25.0218 | 26.3388 |  | 25.0218
|  | 413 | 13.4791 | 17.9721 | 24.9613 | 26.275 |  | 24.9613
|  | 414 | 13.4465 | 17.9287 | 24.901 | 26.2115 |  | 24.901
|  | 415 | 13.4141 | 17.8855 | 24.841 | 26.1484 |  | 24.841
|  | 416 | 13.3819 | 17.8425 | 24.7812 | 26.0855 |  | 24.7812
|  | 417 | 13.3498 | 17.7997 | 24.7218 | 26.023 |  | 24.7218
|  | 418 | 13.3178 | 17.7571 | 24.6627 | 25.9607 |  | 24.6627
|  | 419 | 13.2861 | 17.7147 | 24.6038 | 25.8988 |  | 24.6038
|  | 420 | 13.2544 | 17.6726 | 24.5452 | 25.8371 |  | 24.5452
|  | 421 | 13.2229 | 17.6306 | 24.4869 | 25.7757 |  | 24.4869
|  | 422 | 13.1916 | 17.5888 | 24.4289 | 25.7146 |  | 24.4289
|  | 423 | 13.1604 | 17.5472 | 24.3712 | 25.6539 |  | 24.3712
|  | 424 | 13.1294 | 17.5058 | 24.3137 | 25.5933 |  | 24.3137
|  | 425 | 13.0985 | 17.4647 | 24.2565 | 25.5331 |  | 24.2565
|  | 426 | 13.0677 | 17.4237 | 24.1995 | 25.4732 |  | 24.1995
|  | 427 | 13.0371 | 17.3829 | 24.1429 | 25.4135 |  | 24.1429
|  | 428 | 13.0067 | 17.3422 | 24.0864 | 25.3542 |  | 24.0864
|  | 429 | 12.9764 | 17.3018 | 24.0303 | 25.2951 |  | 24.0303
|  | 430 | 12.9462 | 17.2616 | 23.9744 | 25.2362 |  | 23.9744
|  | 431 | 12.9161 | 17.2215 | 23.9188 | 25.1777 |  | 23.9188
|  | 432 | 12.8863 | 17.1817 | 23.8634 | 25.1194 |  | 23.8634
|  | 433 | 12.8565 | 17.142 | 23.8083 | 25.0614 |  | 23.8083
|  | 434 | 12.8269 | 17.1025 | 23.7535 | 25.0036 |  | 23.7535
|  | 435 | 12.7974 | 17.0632 | 23.6989 | 24.9462 |  | 23.6989
|  | 436 | 12.768 | 17.024 | 23.6445 | 24.8889 |  | 23.6445
|  | 437 | 12.7388 | 16.9851 | 23.5904 | 24.832 |  | 23.5904
|  | 438 | 12.7097 | 16.9463 | 23.5365 | 24.7753 |  | 23.5365
|  | 439 | 12.6808 | 16.9077 | 23.4829 | 24.7189 |  | 23.4829
|  | 440 | 12.652 | 16.8693 | 23.4295 | 24.6627 |  | 23.4295
|  | 441 | 12.6233 | 16.831 | 23.3764 | 24.6068 |  | 23.3764
|  | 442 | 12.5947 | 16.7929 | 23.3235 | 24.5511 |  | 23.3235
|  | 443 | 12.5663 | 16.755 | 23.2709 | 24.4957 |  | 23.2709
|  | 444 | 12.538 | 16.7173 | 23.2185 | 24.4405 |  | 23.2185
|  | 445 | 12.5098 | 16.6797 | 23.1663 | 24.3856 |  | 23.1663
|  | 446 | 12.4817 | 16.6423 | 23.1143 | 24.3309 |  | 23.1143
|  | 447 | 12.4538 | 16.6051 | 23.0626 | 24.2765 |  | 23.0626
|  | 448 | 12.426 | 16.568 | 23.0112 | 24.2223 |  | 23.0112
|  | 449 | 12.3984 | 16.5311 | 22.9599 | 24.1683 |  | 22.9599
|  | 450 | 12.3708 | 16.4944 | 22.9089 | 24.1146 |  | 22.9089
|  | 451 | 12.3434 | 16.4578 | 22.8581 | 24.0612 |  | 22.8581
|  | 452 | 12.3161 | 16.4214 | 22.8075 | 24.0079 |  | 22.8075
|  | 453 | 12.2889 | 16.3852 | 22.7572 | 23.9549 |  | 22.7572
|  | 454 | 12.2618 | 16.3491 | 22.707 | 23.9022 |  | 22.707
|  | 455 | 12.2349 | 16.3131 | 22.6571 | 23.8496 |  | 22.6571
|  | 456 | 12.208 | 16.2774 | 22.6075 | 23.7973 |  | 22.6075
|  | 457 | 12.1813 | 16.2418 | 22.558 | 23.7452 |  | 22.558
|  | 458 | 12.1547 | 16.2063 | 22.5087 | 23.6934 |  | 22.5087
|  | 459 | 12.1282 | 16.171 | 22.4597 | 23.6418 |  | 22.4597
|  | 460 | 12.1019 | 16.1358 | 22.4109 | 23.5904 |  | 22.4109
|  | 461 | 12.0756 | 16.1008 | 22.3623 | 23.5392 |  | 22.3623
|  | 462 | 12.0495 | 16.066 | 22.3139 | 23.4883 |  | 22.3139
|  | 463 | 12.0235 | 16.0313 | 22.2657 | 23.4375 |  | 22.2657
|  | 464 | 11.9975 | 15.9967 | 22.2177 | 23.387 |  | 22.2177
|  | 465 | 11.9717 | 15.9623 | 22.1699 | 23.3367 |  | 22.1699
|  | 466 | 11.9461 | 15.9281 | 22.1223 | 23.2867 |  | 22.1223
|  | 467 | 11.9205 | 15.894 | 22.0749 | 23.2368 |  | 22.0749
|  | 468 | 11.895 | 15.86 | 22.0278 | 23.1871 |  | 22.0278
|  | 469 | 11.8696 | 15.8262 | 21.9808 | 23.1377 |  | 21.9808
|  | 470 | 11.8444 | 15.7925 | 21.934 | 23.0885 |  | 21.934
|  | 471 | 11.8192 | 15.759 | 21.8875 | 23.0394 |  | 21.8875
|  | 472 | 11.7942 | 15.7256 | 21.8411 | 22.9906 |  | 21.8411
|  | 473 | 11.7693 | 15.6923 | 21.7949 | 22.942 |  | 21.7949
|  | 474 | 11.7444 | 15.6592 | 21.7489 | 22.8936 |  | 21.7489
|  | 475 | 11.7197 | 15.6263 | 21.7032 | 22.8454 |  | 21.7032
|  | 476 | 11.6951 | 15.5934 | 21.6576 | 22.7974 |  | 21.6576
|  | 477 | 11.6706 | 15.5608 | 21.6122 | 22.7496 |  | 21.6122
|  | 478 | 11.6462 | 15.5282 | 21.5669 | 22.702 |  | 21.5669
|  | 479 | 11.6218 | 15.4958 | 21.5219 | 22.6547 |  | 21.5219
|  | 480 | 11.5976 | 15.4635 | 21.4771 | 22.6075 |  | 21.4771
|  | 481 | 11.5735 | 15.4314 | 21.4324 | 22.5605 |  | 21.4324
|  | 482 | 11.5495 | 15.3993 | 21.388 | 22.5136 |  | 21.388
|  | 483 | 11.5256 | 15.3675 | 21.3437 | 22.467 |  | 21.3437
|  | 484 | 11.5018 | 15.3357 | 21.2996 | 22.4206 |  | 21.2996
|  | 485 | 11.4781 | 15.3041 | 21.2557 | 22.3744 |  | 21.2557
|  | 486 | 11.4544 | 15.2726 | 21.2119 | 22.3284 |  | 21.2119
|  | 487 | 11.4309 | 15.2412 | 21.1684 | 22.2825 |  | 21.1684
|  | 488 | 11.4075 | 15.21 | 21.125 | 22.2368 |  | 21.125
|  | 489 | 11.3842 | 15.1789 | 21.0818 | 22.1914 |  | 21.0818
|  | 490 | 11.3609 | 15.1479 | 21.0388 | 22.1461 |  | 21.0388
|  | 491 | 11.3378 | 15.1171 | 20.9959 | 22.101 |  | 20.9959
|  | 492 | 11.3148 | 15.0863 | 20.9533 | 22.0561 |  | 20.9533
|  | 493 | 11.2918 | 15.0557 | 20.9108 | 22.0113 |  | 20.9108
|  | 494 | 11.2689 | 15.0253 | 20.8684 | 21.9668 |  | 20.8684
|  | 495 | 11.2462 | 14.9949 | 20.8263 | 21.9224 |  | 20.8263
|  | 496 | 11.2235 | 14.9647 | 20.7843 | 21.8782 |  | 20.7843
|  | 497 | 11.2009 | 14.9346 | 20.7425 | 21.8342 |  | 20.7425
|  | 498 | 11.1784 | 14.9046 | 20.7008 | 21.7903 |  | 20.7008
|  | 499 | 11.156 | 14.8747 | 20.6593 | 21.7467 |  | 20.6593
|  | 500 | 11.1337 | 14.845 | 20.618 | 21.7032 |  | 20.618
|  | 501 | 11.1115 | 14.8153 | 20.5768 | 21.6598 |  | 20.5768
|  | 502 | 11.0894 | 14.7858 | 20.5359 | 21.6167 |  | 20.5359
|  | 503 | 11.0673 | 14.7564 | 20.495 | 21.5737 |  | 20.495
|  | 504 | 11.0454 | 14.7271 | 20.4544 | 21.5309 |  | 20.4544
|  | 505 | 11.0235 | 14.698 | 20.4139 | 21.4883 |  | 20.4139
|  | 506 | 11.0017 | 14.6689 | 20.3735 | 21.4458 |  | 20.3735
|  | 507 | 10.98 | 14.64 | 20.3333 | 21.4035 |  | 20.3333
|  | 508 | 10.9584 | 14.6112 | 20.2933 | 21.3614 |  | 20.2933
|  | 509 | 10.9369 | 14.5825 | 20.2534 | 21.3194 |  | 20.2534
|  | 510 | 10.9154 | 14.5539 | 20.2137 | 21.2776 |  | 20.2137
|  | 511 | 10.8941 | 14.5254 | 20.1742 | 21.236 |  | 20.1742
|  | 512 | 10.8728 | 14.497 | 20.1348 | 21.1945 |  | 20.1348
|  | 513 | 10.8516 | 14.4688 | 20.0955 | 21.1532 |  | 20.0955
|  | 514 | 10.8305 | 14.4406 | 20.0564 | 21.112 |  | 20.0564
|  | 515 | 10.8094 | 14.4126 | 20.0175 | 21.071 |  | 20.0175
|  | 516 | 10.7885 | 14.3847 | 19.9787 | 21.0302 |  | 19.9787
|  | 517 | 10.7676 | 14.3568 | 19.94 | 20.9895 |  | 19.94
|  | 518 | 10.7468 | 14.3291 | 19.9015 | 20.949 |  | 19.9015
|  | 519 | 10.7261 | 14.3015 | 19.8632 | 20.9086 |  | 19.8632
|  | 520 | 10.7055 | 14.274 | 19.825 | 20.8684 |  | 19.825
|  | 521 | 10.685 | 14.2466 | 19.7869 | 20.8284 |  | 19.7869
|  | 522 | 10.6645 | 14.2193 | 19.749 | 20.7885 |  | 19.749
|  | 523 | 10.6441 | 14.1921 | 19.7113 | 20.7487 |  | 19.7113
|  | 524 | 10.6238 | 14.165 | 19.6737 | 20.7091 |  | 19.6737
|  | 525 | 10.6035 | 14.1381 | 19.6362 | 20.6697 |  | 19.6362
|  | 526 | 10.5834 | 14.1112 | 19.5989 | 20.6304 |  | 19.5989
|  | 527 | 10.5633 | 14.0844 | 19.5617 | 20.5912 |  | 19.5617
|  | 528 | 10.5433 | 14.0577 | 19.5246 | 20.5522 |  | 19.5246
|  | 529 | 10.5234 | 14.0312 | 19.4877 | 20.5134 |  | 19.4877
|  | 530 | 10.5035 | 14.0047 | 19.4509 | 20.4747 |  | 19.4509
|  | 531 | 10.4837 | 13.9783 | 19.4143 | 20.4361 |  | 19.4143
|  | 532 | 10.464 | 13.952 | 19.3778 | 20.3977 |  | 19.3778
|  | 533 | 10.4444 | 13.9259 | 19.3415 | 20.3594 |  | 19.3415
|  | 534 | 10.4248 | 13.8998 | 19.3052 | 20.3213 |  | 19.3052
|  | 535 | 10.4053 | 13.8738 | 19.2692 | 20.2833 |  | 19.2692
|  | 536 | 10.3859 | 13.8479 | 19.2332 | 20.2455 |  | 19.2332
|  | 537 | 10.3666 | 13.8221 | 19.1974 | 20.2078 |  | 19.1974
|  | 538 | 10.3473 | 13.7964 | 19.1617 | 20.1702 |  | 19.1617
|  | 539 | 10.3281 | 13.7708 | 19.1262 | 20.1328 |  | 19.1262
|  | 540 | 10.309 | 13.7453 | 19.0907 | 20.0955 |  | 19.0907
|  | 541 | 10.2899 | 13.7199 | 19.0555 | 20.0584 |  | 19.0555
|  | 542 | 10.271 | 13.6946 | 19.0203 | 20.0214 |  | 19.0203
|  | 543 | 10.252 | 13.6694 | 18.9853 | 19.9845 |  | 18.9853
|  | 544 | 10.2332 | 13.6443 | 18.9504 | 19.9478 |  | 18.9504
|  | 545 | 10.2144 | 13.6192 | 18.9156 | 19.9112 |  | 18.9156
|  | 546 | 10.1957 | 13.5943 | 18.881 | 19.8747 |  | 18.881
|  | 547 | 10.1771 | 13.5694 | 18.8464 | 19.8384 |  | 18.8464
|  | 548 | 10.1585 | 13.5447 | 18.812 | 19.8022 |  | 18.812
|  | 549 | 10.14 | 13.52 | 18.7778 | 19.7661 |  | 18.7778
|  | 550 | 10.1216 | 13.4954 | 18.7436 | 19.7301 |  | 18.7436
|  | 551 | 10.1032 | 13.4709 | 18.7096 | 19.6943 |  | 18.7096
|  | 552 | 10.0849 | 13.4465 | 18.6757 | 19.6587 |  | 18.6757
|  | 553 | 10.0667 | 13.4222 | 18.642 | 19.6231 |  | 18.642
|  | 554 | 10.0485 | 13.398 | 18.6083 | 19.5877 |  | 18.6083
|  | 555 | 10.0304 | 13.3738 | 18.5748 | 19.5524 |  | 18.5748
|  | 556 | 10.0123 | 13.3498 | 18.5414 | 19.5172 |  | 18.5414
|  | 557 | 9.9944 | 13.3258 | 18.5081 | 19.4822 |  | 18.5081
|  | 558 | 9.9765 | 13.3019 | 18.4749 | 19.4473 |  | 18.4749
|  | 559 | 9.9586 | 13.2781 | 18.4419 | 19.4125 |  | 18.4419
|  | 560 | 9.9408 | 13.2544 | 18.4089 | 19.3778 |  | 18.4089
|  | 561 | 9.9231 | 13.2308 | 18.3761 | 19.3433 |  | 18.3761
|  | 562 | 9.9054 | 13.2073 | 18.3434 | 19.3089 |  | 18.3434
|  | 563 | 9.8879 | 13.1838 | 18.3108 | 19.2746 |  | 18.3108
|  | 564 | 9.8703 | 13.1604 | 18.2784 | 19.2404 |  | 18.2784
|  | 565 | 9.8528 | 13.1371 | 18.246 | 19.2063 |  | 18.246
|  | 566 | 9.8354 | 13.1139 | 18.2138 | 19.1724 |  | 18.2138
|  | 567 | 9.8181 | 13.0908 | 18.1817 | 19.1386 |  | 18.1817
|  | 568 | 9.8008 | 13.0677 | 18.1496 | 19.1049 |  | 18.1496
|  | 569 | 9.7836 | 13.0448 | 18.1178 | 19.0713 |  | 18.1178
|  | 570 | 9.7664 | 13.0219 | 18.086 | 19.0379 |  | 18.086
|  | 571 | 9.7493 | 12.9991 | 18.0543 | 19.0045 |  | 18.0543
|  | 572 | 9.7323 | 12.9764 | 18.0227 | 18.9713 |  | 18.0227
|  | 573 | 9.7153 | 12.9537 | 17.9913 | 18.9382 |  | 17.9913
|  | 574 | 9.6984 | 12.9311 | 17.9599 | 18.9052 |  | 17.9599
|  | 575 | 9.6815 | 12.9087 | 17.9287 | 18.8723 |  | 17.9287
|  | 576 | 9.6647 | 12.8863 | 17.8976 | 18.8395 |  | 17.8976
|  | 577 | 9.6479 | 12.8639 | 17.8666 | 18.8069 |  | 17.8666
|  | 578 | 9.6312 | 12.8417 | 17.8356 | 18.7744 |  | 17.8356
|  | 579 | 9.6146 | 12.8195 | 17.8048 | 18.7419 |  | 17.8048
|  | 580 | 9.598 | 12.7974 | 17.7741 | 18.7096 |  | 17.7741
|  | 581 | 9.5815 | 12.7754 | 17.7435 | 18.6774 |  | 17.7435
|  | 582 | 9.5651 | 12.7534 | 17.7131 | 18.6453 |  | 17.7131
|  | 583 | 9.5486 | 12.7315 | 17.6827 | 18.6133 |  | 17.6827
|  | 584 | 9.5323 | 12.7097 | 17.6524 | 18.5815 |  | 17.6524
|  | 585 | 9.516 | 12.688 | 17.6222 | 18.5497 |  | 17.6222
|  | 586 | 9.4998 | 12.6663 | 17.5922 | 18.5181 |  | 17.5922
|  | 587 | 9.4836 | 12.6448 | 17.5622 | 18.4865 |  | 17.5622
|  | 588 | 9.4674 | 12.6233 | 17.5323 | 18.4551 |  | 17.5323
|  | 589 | 9.4514 | 12.6018 | 17.5025 | 18.4237 |  | 17.5025
|  | 590 | 9.4354 | 12.5805 | 17.4729 | 18.3925 |  | 17.4729
|  | 591 | 9.4194 | 12.5592 | 17.4433 | 18.3614 |  | 17.4433
|  | 592 | 9.4035 | 12.538 | 17.4139 | 18.3304 |  | 17.4139
|  | 593 | 9.3876 | 12.5168 | 17.3845 | 18.2995 |  | 17.3845
|  | 594 | 9.3718 | 12.4958 | 17.3552 | 18.2687 |  | 17.3552
|  | 595 | 9.3561 | 12.4748 | 17.3261 | 18.2379 |  | 17.3261
|  | 596 | 9.3404 | 12.4538 | 17.297 | 18.2073 |  | 17.297
|  | 597 | 9.3247 | 12.433 | 17.268 | 18.1768 |  | 17.268
|  | 598 | 9.3091 | 12.4122 | 17.2391 | 18.1465 |  | 17.2391
|  | 599 | 9.2936 | 12.3915 | 17.2104 | 18.1162 |  | 17.2104
|  | 600 | 9.2781 | 12.3708 | 17.1817 | 18.086 |  | 17.1817
|  | 601 | 9.2627 | 12.3502 | 17.1531 | 18.0559 |  | 17.1531
|  | 602 | 9.2473 | 12.3297 | 17.1246 | 18.0259 |  | 17.1246
|  | 603 | 9.2319 | 12.3093 | 17.0962 | 17.996 |  | 17.0962
|  | 604 | 9.2167 | 12.2889 | 17.0679 | 17.9662 |  | 17.0679
|  | 605 | 9.2014 | 12.2686 | 17.0397 | 17.9365 |  | 17.0397
|  | 606 | 9.1862 | 12.2483 | 17.0116 | 17.9069 |  | 17.0116
|  | 607 | 9.1711 | 12.2281 | 16.9835 | 17.8774 |  | 16.9835
|  | 608 | 9.156 | 12.208 | 16.9556 | 17.848 |  | 16.9556
|  | 609 | 9.141 | 12.188 | 16.9278 | 17.8187 |  | 16.9278
|  | 610 | 9.126 | 12.168 | 16.9 | 17.7895 |  | 16.9
|  | 611 | 9.1111 | 12.1481 | 16.8723 | 17.7604 |  | 16.8723
|  | 612 | 9.0962 | 12.1282 | 16.8448 | 17.7313 |  | 16.8448
|  | 613 | 9.0813 | 12.1085 | 16.8173 | 17.7024 |  | 16.8173
|  | 614 | 9.0665 | 12.0887 | 16.7899 | 17.6736 |  | 16.7899
|  | 615 | 9.0518 | 12.0691 | 16.7626 | 17.6448 |  | 16.7626
|  | 616 | 9.0371 | 12.0495 | 16.7354 | 17.6162 |  | 16.7354
|  | 617 | 9.0225 | 12.03 | 16.7083 | 17.5876 |  | 16.7083
|  | 618 | 9.0079 | 12.0105 | 16.6812 | 17.5592 |  | 16.6812
|  | 619 | 8.9933 | 11.9911 | 16.6543 | 17.5308 |  | 16.6543
|  | 620 | 8.9788 | 11.9717 | 16.6274 | 17.5025 |  | 16.6274
|  | 621 | 8.9643 | 11.9525 | 16.6006 | 17.4744 |  | 16.6006
|  | 622 | 8.9499 | 11.9332 | 16.574 | 17.4463 |  | 16.574
|  | 623 | 8.9356 | 11.9141 | 16.5474 | 17.4183 |  | 16.5474
|  | 624 | 8.9213 | 11.895 | 16.5208 | 17.3904 |  | 16.5208
|  | 625 | 8.907 | 11.876 | 16.4944 | 17.3625 |  | 16.4944
|  | 626 | 8.8927 | 11.857 | 16.4681 | 17.3348 |  | 16.4681
|  | 627 | 8.8786 | 11.8381 | 16.4418 | 17.3071 |  | 16.4418
|  | 628 | 8.8644 | 11.8192 | 16.4156 | 17.2796 |  | 16.4156
|  | 629 | 8.8503 | 11.8004 | 16.3895 | 17.2521 |  | 16.3895
|  | 630 | 8.8363 | 11.7817 | 16.3635 | 17.2247 |  | 16.3635
|  | 631 | 8.8223 | 11.763 | 16.3376 | 17.1974 |  | 16.3376
|  | 632 | 8.8083 | 11.7444 | 16.3117 | 17.1702 |  | 16.3117
|  | 633 | 8.7944 | 11.7259 | 16.2859 | 17.1431 |  | 16.2859
|  | 634 | 8.7805 | 11.7074 | 16.2603 | 17.1161 |  | 16.2603
|  | 635 | 8.7667 | 11.6889 | 16.2346 | 17.0891 |  | 16.2346
|  | 636 | 8.7529 | 11.6706 | 16.2091 | 17.0622 |  | 16.2091
|  | 637 | 8.7392 | 11.6522 | 16.1837 | 17.0354 |  | 16.1837
|  | 638 | 8.7255 | 11.634 | 16.1583 | 17.0087 |  | 16.1583
|  | 639 | 8.7118 | 11.6158 | 16.133 | 16.9821 |  | 16.133
|  | 640 | 8.6982 | 11.5976 | 16.1078 | 16.9556 |  | 16.1078
|  | 641 | 8.6846 | 11.5795 | 16.0827 | 16.9291 |  | 16.0827
|  | 642 | 8.6711 | 11.5615 | 16.0576 | 16.9028 |  | 16.0576
|  | 643 | 8.6576 | 11.5435 | 16.0327 | 16.8765 |  | 16.0327
|  | 644 | 8.6442 | 11.5256 | 16.0078 | 16.8503 |  | 16.0078
|  | 645 | 8.6308 | 11.5077 | 15.9829 | 16.8242 |  | 15.9829
|  | 646 | 8.6174 | 11.4899 | 15.9582 | 16.7981 |  | 15.9582
|  | 647 | 8.6041 | 11.4721 | 15.9335 | 16.7721 |  | 15.9335
|  | 648 | 8.5908 | 11.4544 | 15.909 | 16.7463 |  | 15.909
|  | 649 | 8.5776 | 11.4368 | 15.8844 | 16.7205 |  | 15.8844
|  | 650 | 8.5644 | 11.4192 | 15.86 | 16.6947 |  | 15.86
|  | 651 | 8.5512 | 11.4017 | 15.8356 | 16.6691 |  | 15.8356
|  | 652 | 8.5381 | 11.3842 | 15.8113 | 16.6435 |  | 15.8113
|  | 653 | 8.5251 | 11.3667 | 15.7871 | 16.618 |  | 15.7871
|  | 654 | 8.512 | 11.3494 | 15.763 | 16.5926 |  | 15.763
|  | 655 | 8.499 | 11.332 | 15.7389 | 16.5673 |  | 15.7389
|  | 656 | 8.4861 | 11.3148 | 15.7149 | 16.542 |  | 15.7149
|  | 657 | 8.4732 | 11.2975 | 15.691 | 16.5169 |  | 15.691
|  | 658 | 8.4603 | 11.2804 | 15.6672 | 16.4918 |  | 15.6672
|  | 659 | 8.4474 | 11.2632 | 15.6434 | 16.4667 |  | 15.6434
|  | 660 | 8.4346 | 11.2462 | 15.6197 | 16.4418 |  | 15.6197
|  | 661 | 8.4219 | 11.2292 | 15.5961 | 16.4169 |  | 15.5961
|  | 662 | 8.4092 | 11.2122 | 15.5725 | 16.3921 |  | 15.5725
|  | 663 | 8.3965 | 11.1953 | 15.549 | 16.3674 |  | 15.549
|  | 664 | 8.3838 | 11.1784 | 15.5256 | 16.3427 |  | 15.5256
|  | 665 | 8.3712 | 11.1616 | 15.5023 | 16.3182 |  | 15.5023
|  | 666 | 8.3586 | 11.1449 | 15.479 | 16.2937 |  | 15.479
|  | 667 | 8.3461 | 11.1282 | 15.4558 | 16.2692 |  | 15.4558
|  | 668 | 8.3336 | 11.1115 | 15.4326 | 16.2449 |  | 15.4326
|  | 669 | 8.3212 | 11.0949 | 15.4096 | 16.2206 |  | 15.4096
|  | 670 | 8.3087 | 11.0783 | 15.3866 | 16.1964 |  | 15.3866
|  | 671 | 8.2964 | 11.0618 | 15.3636 | 16.1722 |  | 15.3636
|  | 672 | 8.284 | 11.0454 | 15.3408 | 16.1482 |  | 15.3408
|  | 673 | 8.2717 | 11.0289 | 15.318 | 16.1242 |  | 15.318
|  | 674 | 8.2594 | 11.0126 | 15.2953 | 16.1003 |  | 15.2953
|  | 675 | 8.2472 | 10.9963 | 15.2726 | 16.0764 |  | 15.2726
|  | 676 | 8.235 | 10.98 | 15.25 | 16.0526 |  | 15.25
|  | 677 | 8.2228 | 10.9638 | 15.2275 | 16.0289 |  | 15.2275
|  | 678 | 8.2107 | 10.9476 | 15.205 | 16.0053 |  | 15.205
|  | 679 | 8.1986 | 10.9315 | 15.1826 | 15.9817 |  | 15.1826
|  | 680 | 8.1866 | 10.9154 | 15.1603 | 15.9582 |  | 15.1603
|  | 681 | 8.1745 | 10.8994 | 15.138 | 15.9348 |  | 15.138
|  | 682 | 8.1626 | 10.8834 | 15.1158 | 15.9114 |  | 15.1158
|  | 683 | 8.1506 | 10.8675 | 15.0937 | 15.8881 |  | 15.0937
|  | 684 | 8.1387 | 10.8516 | 15.0716 | 15.8649 |  | 15.0716
|  | 685 | 8.1268 | 10.8357 | 15.0496 | 15.8417 |  | 15.0496
|  | 686 | 8.115 | 10.8199 | 15.0277 | 15.8186 |  | 15.0277
|  | 687 | 8.1031 | 10.8042 | 15.0058 | 15.7956 |  | 15.0058
|  | 688 | 8.0914 | 10.7885 | 14.984 | 15.7726 |  | 14.984
|  | 689 | 8.0796 | 10.7728 | 14.9623 | 15.7498 |  | 14.9623
|  | 690 | 8.0679 | 10.7572 | 14.9406 | 15.7269 |  | 14.9406
|  | 691 | 8.0562 | 10.7416 | 14.919 | 15.7042 |  | 14.919
|  | 692 | 8.0446 | 10.7261 | 14.8974 | 15.6815 |  | 14.8974
|  | 693 | 8.033 | 10.7106 | 14.8759 | 15.6588 |  | 14.8759
|  | 694 | 8.0214 | 10.6952 | 14.8545 | 15.6363 |  | 14.8545
|  | 695 | 8.0099 | 10.6798 | 14.8331 | 15.6138 |  | 14.8331
|  | 696 | 7.9984 | 10.6645 | 14.8118 | 15.5913 |  | 14.8118
|  | 697 | 7.9869 | 10.6492 | 14.7905 | 15.569 |  | 14.7905
|  | 698 | 7.9754 | 10.6339 | 14.7693 | 15.5467 |  | 14.7693
|  | 699 | 7.964 | 10.6187 | 14.7482 | 15.5244 |  | 14.7482
|  | 700 | 7.9527 | 10.6035 | 14.7271 | 15.5023 |  | 14.7271
|  | 701 | 7.9413 | 10.5884 | 14.7061 | 15.4801 |  | 14.7061
|  | 702 | 7.93 | 10.5733 | 14.6852 | 15.4581 |  | 14.6852
|  | 703 | 7.9187 | 10.5583 | 14.6643 | 15.4361 |  | 14.6643
|  | 704 | 7.9075 | 10.5433 | 14.6435 | 15.4142 |  | 14.6435
|  | 705 | 7.8963 | 10.5283 | 14.6227 | 15.3923 |  | 14.6227
|  | 706 | 7.8851 | 10.5134 | 14.602 | 15.3705 |  | 14.602
|  | 707 | 7.8739 | 10.4986 | 14.5813 | 15.3488 |  | 14.5813
|  | 708 | 7.8628 | 10.4837 | 14.5607 | 15.3271 |  | 14.5607
|  | 709 | 7.8517 | 10.4689 | 14.5402 | 15.3055 |  | 14.5402
|  | 710 | 7.8406 | 10.4542 | 14.5197 | 15.2839 |  | 14.5197
|  | 711 | 7.8296 | 10.4395 | 14.4993 | 15.2624 |  | 14.4993
|  | 712 | 7.8186 | 10.4248 | 14.4789 | 15.241 |  | 14.4789
|  | 713 | 7.8077 | 10.4102 | 14.4586 | 15.2196 |  | 14.4586
|  | 714 | 7.7967 | 10.3956 | 14.4384 | 15.1983 |  | 14.4384
|  | 715 | 7.7858 | 10.3811 | 14.4182 | 15.177 |  | 14.4182
|  | 716 | 7.7749 | 10.3666 | 14.398 | 15.1558 |  | 14.398
|  | 717 | 7.7641 | 10.3521 | 14.378 | 15.1347 |  | 14.378
|  | 718 | 7.7533 | 10.3377 | 14.3579 | 15.1136 |  | 14.3579
|  | 719 | 7.7425 | 10.3233 | 14.338 | 15.0926 |  | 14.338
|  | 720 | 7.7317 | 10.309 | 14.3181 | 15.0716 |  | 14.3181
|  | 721 | 7.721 | 10.2947 | 14.2982 | 15.0507 |  | 14.2982
|  | 722 | 7.7103 | 10.2804 | 14.2784 | 15.0299 |  | 14.2784
|  | 723 | 7.6997 | 10.2662 | 14.2586 | 15.0091 |  | 14.2586
|  | 724 | 7.689 | 10.252 | 14.239 | 14.9884 |  | 14.239
|  | 725 | 7.6784 | 10.2379 | 14.2193 | 14.9677 |  | 14.2193
|  | 726 | 7.6679 | 10.2238 | 14.1997 | 14.9471 |  | 14.1997
|  | 727 | 7.6573 | 10.2097 | 14.1802 | 14.9265 |  | 14.1802
|  | 728 | 7.6468 | 10.1957 | 14.1607 | 14.906 |  | 14.1607
|  | 729 | 7.6363 | 10.1817 | 14.1413 | 14.8856 |  | 14.1413
|  | 730 | 7.6258 | 10.1678 | 14.1219 | 14.8652 |  | 14.1219
|  | 731 | 7.6154 | 10.1539 | 14.1026 | 14.8448 |  | 14.1026
|  | 732 | 7.605 | 10.14 | 14.0833 | 14.8246 |  | 14.0833
|  | 733 | 7.5946 | 10.1262 | 14.0641 | 14.8043 |  | 14.0641
|  | 734 | 7.5843 | 10.1124 | 14.045 | 14.7842 |  | 14.045
|  | 735 | 7.574 | 10.0986 | 14.0259 | 14.7641 |  | 14.0259
|  | 736 | 7.5637 | 10.0849 | 14.0068 | 14.744 |  | 14.0068
|  | 737 | 7.5534 | 10.0712 | 13.9878 | 14.724 |  | 13.9878
|  | 738 | 7.5432 | 10.0576 | 13.9688 | 14.704 |  | 13.9688
|  | 739 | 7.533 | 10.044 | 13.9499 | 14.6841 |  | 13.9499
|  | 740 | 7.5228 | 10.0304 | 13.9311 | 14.6643 |  | 13.9311
|  | 741 | 7.5126 | 10.0168 | 13.9123 | 14.6445 |  | 13.9123
|  | 742 | 7.5025 | 10.0033 | 13.8935 | 14.6248 |  | 13.8935
|  | 743 | 7.4924 | 9.9899 | 13.8748 | 14.6051 |  | 13.8748
|  | 744 | 7.4823 | 9.9765 | 13.8562 | 14.5855 |  | 13.8562
|  | 745 | 7.4723 | 9.9631 | 13.8376 | 14.5659 |  | 13.8376
|  | 746 | 7.4623 | 9.9497 | 13.819 | 14.5464 |  | 13.819
|  | 747 | 7.4523 | 9.9364 | 13.8005 | 14.5269 |  | 13.8005
|  | 748 | 7.4423 | 9.9231 | 13.7821 | 14.5075 |  | 13.7821
|  | 749 | 7.4324 | 9.9099 | 13.7637 | 14.4881 |  | 13.7637
|  | 750 | 7.4225 | 9.8966 | 13.7453 | 14.4688 |  | 13.7453
|  | 751 | 7.4126 | 9.8835 | 13.727 | 14.4495 |  | 13.727
|  | 752 | 7.4027 | 9.8703 | 13.7088 | 14.4303 |  | 13.7088
|  | 753 | 7.3929 | 9.8572 | 13.6906 | 14.4111 |  | 13.6906
|  | 754 | 7.3831 | 9.8441 | 13.6724 | 14.392 |  | 13.6724
|  | 755 | 7.3733 | 9.8311 | 13.6543 | 14.373 |  | 13.6543
|  | 756 | 7.3636 | 9.8181 | 13.6362 | 14.3539 |  | 13.6362
|  | 757 | 7.3538 | 9.8051 | 13.6182 | 14.335 |  | 13.6182
|  | 758 | 7.3441 | 9.7922 | 13.6003 | 14.3161 |  | 13.6003
|  | 759 | 7.3345 | 9.7793 | 13.5823 | 14.2972 |  | 13.5823
|  | 760 | 7.3248 | 9.7664 | 13.5645 | 14.2784 |  | 13.5645
|  | 761 | 7.3152 | 9.7536 | 13.5466 | 14.2596 |  | 13.5466
|  | 762 | 7.3056 | 9.7408 | 13.5289 | 14.2409 |  | 13.5289
|  | 763 | 7.296 | 9.728 | 13.5111 | 14.2223 |  | 13.5111
|  | 764 | 7.2865 | 9.7153 | 13.4935 | 14.2036 |  | 13.4935
|  | 765 | 7.2769 | 9.7026 | 13.4758 | 14.1851 |  | 13.4758
|  | 766 | 7.2674 | 9.6899 | 13.4582 | 14.1666 |  | 13.4582
|  | 767 | 7.258 | 9.6773 | 13.4407 | 14.1481 |  | 13.4407
|  | 768 | 7.2485 | 9.6647 | 13.4232 | 14.1297 |  | 13.4232
|  | 769 | 7.2391 | 9.6521 | 13.4057 | 14.1113 |  | 13.4057
|  | 770 | 7.2297 | 9.6396 | 13.3883 | 14.093 |  | 13.3883
|  | 771 | 7.2203 | 9.6271 | 13.3709 | 14.0747 |  | 13.3709
|  | 772 | 7.211 | 9.6146 | 13.3536 | 14.0564 |  | 13.3536
|  | 773 | 7.2016 | 9.6022 | 13.3364 | 14.0383 |  | 13.3364
|  | 774 | 7.1923 | 9.5898 | 13.3191 | 14.0201 |  | 13.3191
|  | 775 | 7.183 | 9.5774 | 13.3019 | 14.002 |  | 13.3019
|  | 776 | 7.1738 | 9.5651 | 13.2848 | 13.984 |  | 13.2848
|  | 777 | 7.1646 | 9.5527 | 13.2677 | 13.966 |  | 13.2677
|  | 778 | 7.1553 | 9.5405 | 13.2506 | 13.948 |  | 13.2506
|  | 779 | 7.1462 | 9.5282 | 13.2336 | 13.9301 |  | 13.2336
|  | 780 | 7.137 | 9.516 | 13.2167 | 13.9123 |  | 13.2167
|  | 781 | 7.1279 | 9.5038 | 13.1997 | 13.8945 |  | 13.1997
|  | 782 | 7.1187 | 9.4917 | 13.1829 | 13.8767 |  | 13.1829
|  | 783 | 7.1097 | 9.4795 | 13.166 | 13.859 |  | 13.166
|  | 784 | 7.1006 | 9.4674 | 13.1492 | 13.8413 |  | 13.1492
|  | 785 | 7.0915 | 9.4554 | 13.1325 | 13.8237 |  | 13.1325
|  | 786 | 7.0825 | 9.4434 | 13.1158 | 13.8061 |  | 13.1158
|  | 787 | 7.0735 | 9.4314 | 13.0991 | 13.7885 |  | 13.0991
|  | 788 | 7.0645 | 9.4194 | 13.0825 | 13.771 |  | 13.0825
|  | 789 | 7.0556 | 9.4075 | 13.0659 | 13.7536 |  | 13.0659
|  | 790 | 7.0467 | 9.3955 | 13.0494 | 13.7362 |  | 13.0494
|  | 791 | 7.0377 | 9.3837 | 13.0329 | 13.7188 |  | 13.0329
|  | 792 | 7.0289 | 9.3718 | 13.0164 | 13.7015 |  | 13.0164
|  | 793 | 7.02 | 9.36 | 13 | 13.6842 |  | 13
|  | 794 | 7.0112 | 9.3482 | 12.9836 | 13.667 |  | 12.9836
|  | 795 | 7.0023 | 9.3365 | 12.9673 | 13.6498 |  | 12.9673
|  | 796 | 6.9935 | 9.3247 | 12.951 | 13.6326 |  | 12.951
|  | 797 | 6.9848 | 9.313 | 12.9348 | 13.6155 |  | 12.9348
|  | 798 | 6.976 | 9.3014 | 12.9185 | 13.5985 |  | 12.9185
|  | 799 | 6.9673 | 9.2897 | 12.9024 | 13.5815 |  | 12.9024
|  | 800 | 6.9586 | 9.2781 | 12.8863 | 13.5645 |  | 12.8863
|  | 801 | 6.9499 | 9.2665 | 12.8702 | 13.5475 |  | 12.8702
|  | 802 | 6.9412 | 9.255 | 12.8541 | 13.5306 |  | 12.8541
|  | 803 | 6.9326 | 9.2434 | 12.8381 | 13.5138 |  | 12.8381
|  | 804 | 6.924 | 9.2319 | 12.8221 | 13.497 |  | 12.8221
|  | 805 | 6.9154 | 9.2205 | 12.8062 | 13.4802 |  | 12.8062
|  | 806 | 6.9068 | 9.209 | 12.7903 | 13.4635 |  | 12.7903
|  | 807 | 6.8982 | 9.1976 | 12.7745 | 13.4468 |  | 12.7745
|  | 808 | 6.8897 | 9.1862 | 12.7587 | 13.4302 |  | 12.7587
|  | 809 | 6.8812 | 9.1749 | 12.7429 | 13.4136 |  | 12.7429
|  | 810 | 6.8727 | 9.1636 | 12.7272 | 13.397 |  | 12.7272
|  | 811 | 6.8642 | 9.1523 | 12.7115 | 13.3805 |  | 12.7115
|  | 812 | 6.8557 | 9.141 | 12.6958 | 13.364 |  | 12.6958
|  | 813 | 6.8473 | 9.1297 | 12.6802 | 13.3476 |  | 12.6802
|  | 814 | 6.8389 | 9.1185 | 12.6646 | 13.3312 |  | 12.6646
|  | 815 | 6.8305 | 9.1073 | 12.6491 | 13.3148 |  | 12.6491
|  | 816 | 6.8221 | 9.0962 | 12.6336 | 13.2985 |  | 12.6336
|  | 817 | 6.8138 | 9.085 | 12.6181 | 13.2822 |  | 12.6181
|  | 818 | 6.8055 | 9.0739 | 12.6027 | 13.266 |  | 12.6027
|  | 819 | 6.7971 | 9.0629 | 12.5873 | 13.2498 |  | 12.5873
|  | 820 | 6.7889 | 9.0518 | 12.572 | 13.2336 |  | 12.572
|  | 821 | 6.7806 | 9.0408 | 12.5566 | 13.2175 |  | 12.5566
|  | 822 | 6.7723 | 9.0298 | 12.5414 | 13.2014 |  | 12.5414
|  | 823 | 6.7641 | 9.0188 | 12.5261 | 13.1854 |  | 12.5261
|  | 824 | 6.7559 | 9.0079 | 12.5109 | 13.1694 |  | 12.5109
|  | 825 | 6.7477 | 8.9969 | 12.4958 | 13.1534 |  | 12.4958
|  | 826 | 6.7395 | 8.9861 | 12.4806 | 13.1375 |  | 12.4806
|  | 827 | 6.7314 | 8.9752 | 12.4655 | 13.1216 |  | 12.4655
|  | 828 | 6.7233 | 8.9643 | 12.4505 | 13.1058 |  | 12.4505
|  | 829 | 6.7152 | 8.9535 | 12.4355 | 13.09 |  | 12.4355
|  | 830 | 6.7071 | 8.9427 | 12.4205 | 13.0742 |  | 12.4205
|  | 831 | 6.699 | 8.932 | 12.4055 | 13.0585 |  | 12.4055
|  | 832 | 6.6909 | 8.9213 | 12.3906 | 13.0428 |  | 12.3906
|  | 833 | 6.6829 | 8.9105 | 12.3758 | 13.0271 |  | 12.3758
|  | 834 | 6.6749 | 8.8999 | 12.3609 | 13.0115 |  | 12.3609
|  | 835 | 6.6669 | 8.8892 | 12.3461 | 12.9959 |  | 12.3461
|  | 836 | 6.6589 | 8.8786 | 12.3313 | 12.9804 |  | 12.3313
|  | 837 | 6.651 | 8.868 | 12.3166 | 12.9648 |  | 12.3166
|  | 838 | 6.643 | 8.8574 | 12.3019 | 12.9494 |  | 12.3019
|  | 839 | 6.6351 | 8.8468 | 12.2872 | 12.9339 |  | 12.2872
|  | 840 | 6.6272 | 8.8363 | 12.2726 | 12.9185 |  | 12.2726
|  | 841 | 6.6193 | 8.8258 | 12.258 | 12.9032 |  | 12.258
|  | 842 | 6.6115 | 8.8153 | 12.2435 | 12.8879 |  | 12.2435
|  | 843 | 6.6036 | 8.8048 | 12.2289 | 12.8726 |  | 12.2289
|  | 844 | 6.5958 | 8.7944 | 12.2145 | 12.8573 |  | 12.2145
|  | 845 | 6.588 | 8.784 | 12.2 | 12.8421 |  | 12.2
|  | 846 | 6.5802 | 8.7736 | 12.1856 | 12.8269 |  | 12.1856
|  | 847 | 6.5724 | 8.7633 | 12.1712 | 12.8118 |  | 12.1712
|  | 848 | 6.5647 | 8.7529 | 12.1568 | 12.7967 |  | 12.1568
|  | 849 | 6.557 | 8.7426 | 12.1425 | 12.7816 |  | 12.1425
|  | 850 | 6.5492 | 8.7323 | 12.1282 | 12.7666 |  | 12.1282
|  | 851 | 6.5416 | 8.7221 | 12.114 | 12.7516 |  | 12.114
|  | 852 | 6.5339 | 8.7118 | 12.0998 | 12.7366 |  | 12.0998
|  | 853 | 6.5262 | 8.7016 | 12.0856 | 12.7217 |  | 12.0856
|  | 854 | 6.5186 | 8.6914 | 12.0714 | 12.7068 |  | 12.0714
|  | 855 | 6.5109 | 8.6813 | 12.0573 | 12.6919 |  | 12.0573
|  | 856 | 6.5033 | 8.6711 | 12.0432 | 12.6771 |  | 12.0432
|  | 857 | 6.4958 | 8.661 | 12.0292 | 12.6623 |  | 12.0292
|  | 858 | 6.4882 | 8.6509 | 12.0152 | 12.6475 |  | 12.0152
|  | 859 | 6.4806 | 8.6408 | 12.0012 | 12.6328 |  | 12.0012
|  | 860 | 6.4731 | 8.6308 | 11.9872 | 12.6181 |  | 11.9872
|  | 861 | 6.4656 | 8.6208 | 11.9733 | 12.6035 |  | 11.9733
|  | 862 | 6.4581 | 8.6108 | 11.9594 | 12.5888 |  | 11.9594
|  | 863 | 6.4506 | 8.6008 | 11.9455 | 12.5743 |  | 11.9455
|  | 864 | 6.4431 | 8.5908 | 11.9317 | 12.5597 |  | 11.9317
|  | 865 | 6.4357 | 8.5809 | 11.9179 | 12.5452 |  | 11.9179
|  | 866 | 6.4282 | 8.571 | 11.9042 | 12.5307 |  | 11.9042
|  | 867 | 6.4208 | 8.5611 | 11.8904 | 12.5162 |  | 11.8904
|  | 868 | 6.4134 | 8.5512 | 11.8767 | 12.5018 |  | 11.8767
|  | 869 | 6.4061 | 8.5414 | 11.8631 | 12.4874 |  | 11.8631
|  | 870 | 6.3987 | 8.5316 | 11.8494 | 12.4731 |  | 11.8494
|  | 871 | 6.3913 | 8.5218 | 11.8358 | 12.4588 |  | 11.8358
|  | 872 | 6.384 | 8.512 | 11.8222 | 12.4445 |  | 11.8222
|  | 873 | 6.3767 | 8.5023 | 11.8087 | 12.4302 |  | 11.8087
|  | 874 | 6.3694 | 8.4925 | 11.7952 | 12.416 |  | 11.7952
|  | 875 | 6.3621 | 8.4828 | 11.7817 | 12.4018 |  | 11.7817
|  | 876 | 6.3549 | 8.4732 | 11.7683 | 12.3876 |  | 11.7683
|  | 877 | 6.3476 | 8.4635 | 11.7548 | 12.3735 |  | 11.7548
|  | 878 | 6.3404 | 8.4538 | 11.7415 | 12.3594 |  | 11.7415
|  | 879 | 6.3332 | 8.4442 | 11.7281 | 12.3454 |  | 11.7281
|  | 880 | 6.326 | 8.4346 | 11.7148 | 12.3313 |  | 11.7148
|  | 881 | 6.3188 | 8.4251 | 11.7015 | 12.3173 |  | 11.7015
|  | 882 | 6.3116 | 8.4155 | 11.6882 | 12.3034 |  | 11.6882
|  | 883 | 6.3045 | 8.406 | 11.675 | 12.2894 |  | 11.675
|  | 884 | 6.2974 | 8.3965 | 11.6618 | 12.2755 |  | 11.6618
|  | 885 | 6.2902 | 8.387 | 11.6486 | 12.2617 |  | 11.6486
|  | 886 | 6.2831 | 8.3775 | 11.6354 | 12.2478 |  | 11.6354
|  | 887 | 6.2761 | 8.3681 | 11.6223 | 12.234 |  | 11.6223
|  | 888 | 6.269 | 8.3586 | 11.6092 | 12.2202 |  | 11.6092
|  | 889 | 6.2619 | 8.3492 | 11.5962 | 12.2065 |  | 11.5962
|  | 890 | 6.2549 | 8.3399 | 11.5831 | 12.1928 |  | 11.5831
|  | 891 | 6.2479 | 8.3305 | 11.5701 | 12.1791 |  | 11.5701
|  | 892 | 6.2409 | 8.3212 | 11.5572 | 12.1654 |  | 11.5572
|  | 893 | 6.2339 | 8.3118 | 11.5442 | 12.1518 |  | 11.5442
|  | 894 | 6.2269 | 8.3026 | 11.5313 | 12.1382 |  | 11.5313
|  | 895 | 6.22 | 8.2933 | 11.5184 | 12.1247 |  | 11.5184
|  | 896 | 6.213 | 8.284 | 11.5056 | 12.1111 |  | 11.5056
|  | 897 | 6.2061 | 8.2748 | 11.4928 | 12.0976 |  | 11.4928
|  | 898 | 6.1992 | 8.2656 | 11.48 | 12.0842 |  | 11.48
|  | 899 | 6.1923 | 8.2564 | 11.4672 | 12.0707 |  | 11.4672
|  | 900 | 6.1854 | 8.2472 | 11.4544 | 12.0573 |  | 11.4544
|  | 901 | 0 | 0 | 0 | 0 |  | 11.3399
|  | 902 | 0 | 0 | 0 | 0 |  | 11.2254
|  | 903 | 0 | 0 | 0 | 0 |  | 11.1108
|  | 904 | 0 | 0 | 0 | 0 |  | 10.9963
|  | 905 | 0 | 0 | 0 | 0 |  | 10.8817
|  | 906 | 0 | 0 | 0 | 0 |  | 10.7672
|  | 907 | 0 | 0 | 0 | 0 |  | 10.6526
|  | 908 | 0 | 0 | 0 | 0 |  | 10.5381
|  | 909 | 0 | 0 | 0 | 0 |  | 10.4235
|  | 910 | 0 | 0 | 0 | 0 |  | 10.309
|  | 911 | 0 | 0 | 0 | 0 |  | 10.1945
|  | 912 | 0 | 0 | 0 | 0 |  | 10.0799
|  | 913 | 0 | 0 | 0 | 0 |  | 9.9654
|  | 914 | 0 | 0 | 0 | 0 |  | 9.8508
|  | 915 | 0 | 0 | 0 | 0 |  | 9.7363
|  | 916 | 0 | 0 | 0 | 0 |  | 9.6217
|  | 917 | 0 | 0 | 0 | 0 |  | 9.5072
|  | 918 | 0 | 0 | 0 | 0 |  | 9.3926
|  | 919 | 0 | 0 | 0 | 0 |  | 9.2781
|  | 920 | 0 | 0 | 0 | 0 |  | 9.1636
|  | 921 | 0 | 0 | 0 | 0 |  | 9.049
|  | 922 | 0 | 0 | 0 | 0 |  | 8.9345
|  | 923 | 0 | 0 | 0 | 0 |  | 8.8199
|  | 924 | 0 | 0 | 0 | 0 |  | 8.7054
|  | 925 | 0 | 0 | 0 | 0 |  | 8.5908
|  | 926 | 0 | 0 | 0 | 0 |  | 8.4763
|  | 927 | 0 | 0 | 0 | 0 |  | 8.3617
|  | 928 | 0 | 0 | 0 | 0 |  | 8.2472
|  | 929 | 0 | 0 | 0 | 0 |  | 8.1327
|  | 930 | 0 | 0 | 0 | 0 |  | 8.0181
|  | 931 | 0 | 0 | 0 | 0 |  | 7.9036
|  | 932 | 0 | 0 | 0 | 0 |  | 7.789
|  | 933 | 0 | 0 | 0 | 0 |  | 7.6745
|  | 934 | 0 | 0 | 0 | 0 |  | 7.5599
|  | 935 | 0 | 0 | 0 | 0 |  | 7.4454
|  | 936 | 0 | 0 | 0 | 0 |  | 7.3308
|  | 937 | 0 | 0 | 0 | 0 |  | 7.2163
|  | 938 | 0 | 0 | 0 | 0 |  | 7.1018
|  | 939 | 0 | 0 | 0 | 0 |  | 6.9872
|  | 940 | 0 | 0 | 0 | 0 |  | 6.8727
|  | 941 | 0 | 0 | 0 | 0 |  | 6.7581
|  | 942 | 0 | 0 | 0 | 0 |  | 6.6436
|  | 943 | 0 | 0 | 0 | 0 |  | 6.529
|  | 944 | 0 | 0 | 0 | 0 |  | 6.4145
|  | 945 | 0 | 0 | 0 | 0 |  | 6.2999
|  | 946 | 0 | 0 | 0 | 0 |  | 6.1854
|  | 947 | 0 | 0 | 0 | 0 |  | 6.0709
|  | 948 | 0 | 0 | 0 | 0 |  | 5.9563
|  | 949 | 0 | 0 | 0 | 0 |  | 5.8418
|  | 950 | 0 | 0 | 0 | 0 |  | 5.7272
|  | 951 | 0 | 0 | 0 | 0 |  | 5.6127
|  | 952 | 0 | 0 | 0 | 0 |  | 5.4981
|  | 953 | 0 | 0 | 0 | 0 |  | 5.3836
|  | 954 | 0 | 0 | 0 | 0 |  | 5.269
|  | 955 | 0 | 0 | 0 | 0 |  | 5.1545
|  | 956 | 0 | 0 | 0 | 0 |  | 5.04
|  | 957 | 0 | 0 | 0 | 0 |  | 4.9254
|  | 958 | 0 | 0 | 0 | 0 |  | 4.8109
|  | 959 | 0 | 0 | 0 | 0 |  | 4.6963
|  | 960 | 0 | 0 | 0 | 0 |  | 4.5818
|  | 961 | 0 | 0 | 0 | 0 |  | 4.4672
|  | 962 | 0 | 0 | 0 | 0 |  | 4.3527
|  | 963 | 0 | 0 | 0 | 0 |  | 4.2381
|  | 964 | 0 | 0 | 0 | 0 |  | 4.1236
|  | 965 | 0 | 0 | 0 | 0 |  | 4.0091
|  | 966 | 0 | 0 | 0 | 0 |  | 3.8945
|  | 967 | 0 | 0 | 0 | 0 |  | 3.78
|  | 968 | 0 | 0 | 0 | 0 |  | 3.6654
|  | 969 | 0 | 0 | 0 | 0 |  | 3.5509
|  | 970 | 0 | 0 | 0 | 0 |  | 3.4363
|  | 971 | 0 | 0 | 0 | 0 |  | 3.3218
|  | 972 | 0 | 0 | 0 | 0 |  | 3.2072
|  | 973 | 0 | 0 | 0 | 0 |  | 3.0927
|  | 974 | 0 | 0 | 0 | 0 |  | 2.9782
|  | 975 | 0 | 0 | 0 | 0 |  | 2.8636
|  | 976 | 0 | 0 | 0 | 0 |  | 2.7491
|  | 977 | 0 | 0 | 0 | 0 |  | 2.6345
|  | 978 | 0 | 0 | 0 | 0 |  | 2.52
|  | 979 | 0 | 0 | 0 | 0 |  | 2.4054
|  | 980 | 0 | 0 | 0 | 0 |  | 2.2909
|  | 981 | 0 | 0 | 0 | 0 |  | 2.1763
|  | 982 | 0 | 0 | 0 | 0 |  | 2.0618
|  | 983 | 0 | 0 | 0 | 0 |  | 1.9473
|  | 984 | 0 | 0 | 0 | 0 |  | 1.8327
|  | 985 | 0 | 0 | 0 | 0 |  | 1.7182
|  | 986 | 0 | 0 | 0 | 0 |  | 1.6036
|  | 987 | 0 | 0 | 0 | 0 |  | 1.4891
|  | 988 | 0 | 0 | 0 | 0 |  | 1.3745
|  | 989 | 0 | 0 | 0 | 0 |  | 1.26
|  | 990 | 0 | 0 | 0 | 0 |  | 1.1454
|  | 991 | 0 | 0 | 0 | 0 |  | 1.0309
|  | 992 | 0 | 0 | 0 | 0 |  | 0.91636
|  | 993 | 0 | 0 | 0 | 0 |  | 0.80181
|  | 994 | 0 | 0 | 0 | 0 |  | 0.68727
|  | 995 | 0 | 0 | 0 | 0 |  | 0.57272
|  | 996 | 0 | 0 | 0 | 0 |  | 0.45818
|  | 997 | 0 | 0 | 0 | 0 |  | 0.34363
|  | 998 | 0 | 0 | 0 | 0 |  | 0.22909
|  | 999 | 0 | 0 | 0 | 0 |  | 0.11454
|  | 1000 | 0 | 0 | 0 | 0 |  | 0

## TAAL (hidden)
| 2 | 1 | Nederlands | English | Deutsch | Español | Français | Italiano
|  | 2 | Taal | Language | Sprache | Lenguaje | Langue | Lingua
1 | Nederlands | 3
2 | English | 4 | Omvormer | inverter | WR | Inversor | Onduleur | Inverter
3 | Deutsch | 5 | Type aanduiding | type | Typenbezeichnung | Tipo | Type | Tipo
4 | Español | 6 | Typische String lengte | Typical String Length | typische String Länge | Cantidad típica de módulos | Nombre typique de modules | Lunghezza tipica della stringa
5 | Français | 7 | Toegestane omgevingstemperatuur | allowed ambient temperature | Zulässige Umgebungstemperatur | Temperatura admisible | Température ambiante admissible | Temperatura d'ambiente ammissibile
6 | Italiano | 8 | Toegestane luchtvochtigheid | allowed rel. humidity | Luftfeuchte, rel. (zulässig) | Humedad relativa tolerable | Humidité relative (admissible) | Umiditá, relativa (ammissibile)
|  | 9 | Beschermingsgraad | protection Degree | Schutzklasse | Grado de protección | Indice de protection | Grado di protezione
|  | 10 | Geluidsniveau | Noise level | Schallpegel | Nivel Sonoro | Niveau sonore | Livello di rumore
|  | 11 | Veiligheidsklasse | Safety class | Sicherheidsklasse | Clase Seguridad | Classe de protection | Classe di sicurezza
|  | 12 | Galvanische scheiding | Galvanic isolation | galvanische Trennung | Aislamiento Galvánico | Isolation galvanique | Isolamento galvanico
|  | 13 | Afmeting | dimensions | Abmessung | Dimensiones | Dimensions | Dimensioni
|  | 14 | Gewicht | weight | Gewicht | Peso | Poids | Peso
|  | 15 | Solar Ingang (DC) | solar input (DC) | Solar Anslusse | Entrada solar CC | Entrée solaire (CC) | Ingresso solare (C.C.)
|  | 16 | Nominaal DC-vermogen | nominal DC power | DC-Nennleistung | Potencia nominal CC | Puissance nominale CC | Potenza nominale C.C.
|  | 17 | Max DC-vermogen | max. DC power | max. DC-Leistung | Potencia máx. CC | Puissance CC max. | Potenza massima DC
|  | 18 | Aanbevolen PV-belasting | suggested PV power | Empfohlene PV-Leistung | Potencia PV recomendada | Puissance PV recommandée | Potenza FV consigliata
|  | 19 | MPP tracker | MPP tracker | MPP Regler | MPP tracker | Tracker MPP | Insegutore MPP
|  | 20 | Min DC-spanning | min. DC voltage | min. DC-Spannung | Voltaje mín. CC | Tension CC min. | Tensione minima CC
|  | 21 | MPP-spanning | MPP voltage | MPP-Spannung | Voltaje MPP | Tension MPP | Tensione MPP
|  | 22 | Max DC-spanning | max. DC voltage | max. DC-Spannung | Voltaje máx. CC | Tension CC max. | Tensione massima CC
|  | 23 | max DC-stroom | max. DC current | max. DC-Strom | Corriente máx. CC | Courant CC max. | Corrente massima CC
|  | 24 | Aantal Strings / MPP-ingang | no. of strings by MPP-input | Stringzahl / MPP-Eingang | Nº de series por entrada MPP | No. de boucles / entrée MPP | Numero di stringhe
|  | 25 | Net uitgang (AC) | Grid output (AC) | Wechselstromseite | Salida a red CA | Sortie réseau (CA) | Uscita di rete (CA)
|  | 26 | Netspanning | AC voltage | Netzspannung | Voltaje CA | tension réseau | Tensione di rete
|  | 27 | Nominaal AC-vermogen | nominal AC power | AC-Nennleistung | Potencia nominal CA | Puissance nominale CA | Potenza nominale CA
|  | 28 | Max AC-vermogen | max. AC power | max. AC-Leistung | Potencia Máx. CA | Puissance CA max. | Potenza massima CA
|  | 29 | Nominaal AC-stroom | nominal AC-current | AC- Nennstrom | Corriente nominal CA | Intensité nominale CA | Corrente nominale CA
|  | 30 | Frequentie | frequency | Häufigkeit | Frecuencia | Fréquence | Frequenza
|  | 31 | Power Factor | Power Factor | Leistungsfaktor | Factor de potencia | Facteur de puissance | Fattore di potenza
|  | 32 | THD | THD | Klirrfaktor | THD | Distorsion THD | Distorsione armonica totale
|  | 33 | Efficientie europees gemiddelde | efficiency, european related | Wirkungsgrad, europ. gewichtet | Eficiencia, ponderación europea | Rendement, pondération européenne | Rendimento, standard europeo
|  | 34 | Max. efficientie | max. efficiency | Max. Wirkungsgrad | Eficiencia máx. | Rendement max. | Massimo rendimento
|  | 35 | Aantal MPP-ingangen | number of MPP-inputs | Zahl der MPP eingänge | Número de entradas MPP | Nombre d'entrées MPP | Nimero ingressi MPP
|  | 36 | Nominale DC spanning | Nominal DC voltage | Nominal DC voltage | Voltaje nominal CC | Tension CC nominale | Tensione nominale CC
37
38
39
40
41
42
43
44
|  | 45 | Module | module | Modul | Módulo | Module | Modulo
|  | 46 | Specificaties bij | specifications at | Technische Spezifikation bei | Especificaciones a | Spécifications à | Specifiche a
|  | 47 | STC (25°C / 1.000W m²) | STC (25°C / 1.000W m²) | STC (25°C / 1.000W m²) | STC (25°C / 1.000W m²) | STC (25°C / 1.000W m²) | STC (25°C / 1.000W m²)
|  | 48 | Producent | manufacturer | Hersteller | Fabricante | Fabricant | Produttore
|  | 49 | Module type | type of module | Modultyp | Tipo de módulo | Type de module | Tipo del modulo
|  | 50 | Nominaal vermogen | nominal power | Nennleistung | Potencia nominal | Puissance nominale | Potenza nominale
|  | 51 | Openklemspanning | open circuit voltage | Leerlaufspannung | Voltaje en vacío | Tension à circuit ouvert | Tensione a vuoto
|  | 52 | MPP-spanning | MPP voltage | MPP-Spannung | Voltaje MPP | Tension MPP | Tensione MPP
|  | 53 | Kortsluitstroom | short circuit current | Kurzschlußstrom | Corriente de cortocircuito | Courant de court-circuit | Corrente di corto circuito
|  | 54 | MPP-Stroom | MPP current | MPP-Strom | Corriente MPP | Intensité MPP | Corrente MPP
|  | 55 | Materiaal | material | Technologie | Material | Materiaux | Materiale
|  | 56 | Aantal cellen per module | no. of cells | Anzahl der Zellen im Modul | Nº de células | Nombre de cellules dans le module | Quantità di cellule per modulo
|  | 57 | max. String spanning | max. String voltage | max. Strings Spannung | Voltaje máximo en serie | Tension max. de boucle | Massima tensione di stringa
|  | 58 | *Controleer altijd of de maximale systeem spanning van de modules niet overschreden wordt | *Please make sure the maximum system voltage of the modules is not exceeded. | *Bitte kontrollieren Sie, dass die Maximale Systemspannung der PV Module eingehalten wird. | *Please make sure the maximum system voltage of the modules is not exceeded. | *Veuillez contrôler que le voltage système maximale des panneaux solaires est respecté | *Please make sure the maximum system voltage of the modules is not exceeded.
59
60
61
62
63
64
65
66
|  | 67 | Ingave | input | Eingabe | Entrada | Entrée | Ingresso
|  | 68 | Totaal aantal modules | total number of modules | Gesamt Module | Número total de paneles | Nombre total de modules | Numerototale di moduli
|  | 69 | Locatie | location | Lokation | Localización | Emplacement | Località
|  | 70 | Oriëntatie | orientation | Orientierung | Orientación | Orientation | Orientazione
|  | 71 | Hellingshoek | gradient | Neigungswinkel | Inclinación | Inclinaison | Gradiente
|  | 72 | Module temperatuur | temp. of module | Modultemperatur | Temperatura de los módulos | Température de module | Temperatura del modulo
|  | 73 | Min. | Min. | Min. | Min. | Min. | Min.
|  | 74 | Max. | Max. | Max. | Max. | Max. | Max.
|  | 75 | Onderdimensionering [ODF] | underdimensioning [UDF] | Unterdimensionierung [UDF] | Sobredimensionado [UDF] | Surdimensionnement [UDF] | Sottodimensionamento
|  | 76 | Parallel Mode | parallel mode | Parallel Modus | Modo paralelo | Mode parallèle | Modalità parallela
|  | 77 | Print | PCB | Platine | PCB | Platine | Circuito stampato
|  | 78 | Bereik | range | Bereich | Rango | Plage | Gamma
|  | 79 | Ingang | input | Eingang | Entrada | entrée | Ingresso
|  | 80 | Modules per string | modules per string | Module pro String | Módulos por serie | Modules par boucle | Moduli per stringa
|  | 81 | Aantal strings | no. of strings | Stringzahl | Número de series | Nombre de boucles | Numero di stringhe
|  | 82 | Omvormer & PV-Array karakteristiek | Inverter & PV-Array Characteristic | Wechselrichter und PV-Glied Charakteristik | Características del inversor y Campo FV | Caractéristiques onduleur & champ PV | Caratteristiche dell'inverter e del campo FV
|  | 83 | PV-Array | PV-Array | PV-Glied | Campo FV | Champ PV | Campo FV
|  | 84 | ODF > 1,67 of < 0.85 | UDF > 1,67 or < 0.85 | UDF > 1,67 oder < 0.85 | UDF > 1,67 o < 0.85 | UDF > 1,67 ou < 0.85 | UDF<1,67 o<0,76
|  | 85 | ODF 1,67 - 1,25 of 0.9 - 0.85 | UDF 1,67 - 1,25 or 0.9 - 0.85 | UDF 1,67 - 1,25 oder 0.9 - 0.85 | UDF 1,67 - 1,25 o 0.9 - 0.85 | UDF 1,67 - 1,25 ou 0.9 - 0.85 | UDF 1,67 - 1,27 o 0,8 - 0,76
|  | 86 | ODF 1,25 - 0.9 | UDF 1,25 - 0.9 | UDF 1,25 - 0.9 | UDF 1,25 - 0.9 | UDF 1,25 - 0.9 | Udf 1,25 - 0,8
87
88
89
90
91
92
93
94
95
96
|  | 97 | Compatibiliteits vergelijking | Compatability check | Auswertung | Compruebe compatibilidad | Vérification de compatibilité | Prova di compatibilità
|  | 98 | Nominaal vermogen per string | string nominal power | Stringleistung | Potencia nominal por serie | Puissance par boucle | Potenza nominale stringa
|  | 99 | Totaal PV vermogen | total PV power | Gesamtleistung | Potencia total FV | Puissance totale | Potenza totale
|  | 100 | Orientatie correctie | orientation correction | Orientierung Korrektur | Corrección orientación | Correction d'orientation | Correzione orientamento
|  | 101 | Omgezet bij max instraling | converted at max irradiation | umgesetzt bei max Einstrahlung | Convertido a máx. radiación | Convertion à irradiation max | Conversione per irraggiamento max
|  | 102 | Opstartspanning | startup voltage | Anlaufspannung | Voltaje de arranque | Tension de départ | Tensione di avvio
|  | 103 | Umpp bij | Umpp at | Umpp bei | Umpp a | Umpp à | Umpp a
|  | 104 | Uoc bij | Uoc at | Uoc bei | Uoc a | Uoc à | Uoc a
|  | 105 | Mogelijke omvormerstroom bij | possible inverter current at | mögliche WR strom bei | Corriente posible del inversor a | Intensité onduleur possible à | Corrente ammissibile l'inverter a
|  | 106 | Ipv bij | Ipv at | Ipv bei | lpv a | Ipv à | Ifv a
|  | 107 | PV vermogen | PV power | PV Leistung | Potencia FV | Puissance PV | capacità FV
|  | 108 | Onderdimensionerings resultaat | underdimensionings result | Unterdimensionierungs Ergebnis | Resultado dimensionado escaso | Résultat surdimensionné | Il sottodimensionamento risulta
|  | 109 | Aantal modules | no. of modules | Anzahl Module | Nº de módulo | Nombre de modules | Numero di moduli
|  | 110 | Totaal aantal modules | total no. of modules | total Anzahl Module | Nº total de módulos | Nombre total de modules | Numero totale di moduli
111
112
113
114
115
116
|  | 117 | te laag | too low | zu tief | Muy bajo | Trop bas | Basso
|  | 118 | te hoog | too high | zu hoch | Muy alto | Trop élevé | Alto
|  | 119 | Toelaatbaar | permissible | noch zulassing | Admisible | Admissible | Ammissibile
|  | 120 | Geen volledige omzetting | No complete conversion | Energie Ertrag nicht optimal | Conversión no completa | Convertion non complète | Nessuna conversione completa
|  | 121 | stroombegrenzing | currentlimiting | Strombegrenzung | Limite de intensidad | Intensité limitée | Limitazione di corrente
|  | 122 | Vermogen begrenst | powerlimiting | Leistungsbegrenzung | Limite de potencia | Puissance limitée | Limitazione di potenza
|  | 123 | Duty cycle begrenst | Duty Cycle limiting | Duty Cycle Begrenzung | Limitación del ciclo | Limitation de cycle nécessaire | Limitazione del duty cicle
|  | 124 | GEEN OPLOSSING! | NO SOLUTION! | KEINE LOSUNG! | SIN SOLUCIÓN | PAS DE SOLUTION ! | Nessuna soluzione!
|  | 125 | begrensd | limited | begrenzt | Limitado | Limité | Limitato
|  | 126 | UIT | OUT | AUS | Fuera | En dehors | Out
127
128
129
130
131
132
133
134
|  | 135 | DC Bekabeling | DC cabling | DC Verkabelung | Cableado CC | Cablage CC | Cablaggio CC
|  | 136 | AC Bekabeling | AC cabling | AC Verkabelung | Cableado CA | Cablage CA | Cablaggio CA
|  | 137 | Kabelmateriaal | cable material | Kabelmaterial | Material cable | Matériaux des cables | Materiale del cavo
|  | 138 | Koper | copper | Kupfer | Cobre | Cuivre | Rame
|  | 139 | Aluminium | aluminium | Aluminium | Aluminio | Aluminium | Alluminio
|  | 140 | Kabeldoorsnede | cable diameter | Kabeldurchschnitt | Diámetro del cable | Section des cables | Diametro del cavo
|  | 141 | Enkelvoudige kabellengte | cable length | einfache Kabellänge | Longitud del cable | Longueur des cables | Lunghezza del cavo
|  | 142 | Totale lengte | total length | total Kabellänge | Longitud total | Longeur totale | Lunghezza totale
|  | 143 | Totale kabelweerstand | total cableresistance | total Kabelwiderstand | Resistencia total cable | Résistance totale du cable | Resistenza totale del cavo
|  | 144 | DC-stroom String | DC-current String | DC-strom String | Corriente CC por serie | Intensité de boucle CC | Corrente di stringa
|  | 145 | Energieverlies per String | energieloss by String | Energieverlust | Perdidas por serie | Perte d'énergie par boucle | Perdite di stringa
|  | 146 | Totale energieverlies per ingang | total energyloss by input | total Energieverlust pro Eingang | Total perdidas por entrada | Perte totale d'énergie par entrée | Perdita totale in ingresso
|  | 147 | Beschikbaar vermogen | Available power | Verfügbare Leistung | Potencia disponible | Puissance disponible | Potenza disponibile
|  | 148 | Energieverlies bij max instraling | energieloss at max irradiance | Energieverlust bei max. Einstrahlung | Perdidas de energía a máx. radiación | Perte d'énergie à irradiation max | Perdite a radiazione max.
|  | 149 | Energieverlies in W/m | energieloss in W/m | Energieverlust in W/m2 | Perdidas de energía en W/m | Perte d'énergie en W/m | Perdite in W/m
|  | 150 | Totale verlies in de bekabeling | total loss in cabling | total Verlust in Verkabelung | Perdidas totales en cableados | Perte totale dans le cablage | Perdite totale nei cavi
|  | 151 | AC vermogen | AC Power | AC Leistung | Potencia CA | Puissance CA | Potenza CA
|  | 152 | Netspanning | Grid voltage | Netzspannung | Voltaje de red | Tension du réseau | Tensione di rete
|  | 153 | Netstroom | Grid current | Netzstrom | Corriente de red. | Intensité du réseau | Corrente di rete
|  | 154 | Spanningsval over kabel | Voltagedrop across cable | Spannungsabfall uber Kabel | Caida del voltaje a través del cable. | Chute de tension dûe au cablage | Caduta sui cavi
155
156
157
158
159
160
161
|  | 162 | Nederland | The Netherlands | die Niederlande | Países Bajos | Pays-Bas | Olanda
|  | 163 | Noord Duitsland | Germany - north | Nord - Deutschland | Alemania - Norte | Alemagne - nord | Germania settentrionale
|  | 164 | Centraal Duitsland | Germany - central | zentral - Deutschland | Alemania - Central | Alemagne - centre | Germania centrale
|  | 165 | Zuid Duitsland | Germany - south | Süd - Deutschland | Alemania - Sur | Alemagne - sud | Germania meridionale
|  | 166 | Noord Italie | Italy - north | Nord - Italien | Italia - Norte | Italie - nord | Italia settentrionale
|  | 167 | Zuid Italie | Italy - south | Süd - Italien | Italia - Sur | Italie - sud | Italia meridionale
|  | 168 | Engeland | United Kingdom | England | Reino Unido | Angleterre | Regno unito
|  | 169 | Zwitserland | Switzerland | die Schweiz | Suiza | Suisse | Svizzera
|  | 170 | Noord Spanje | Spain - north | Nord - Spanien | España - Norte | Espagne - nord | Spagna settentrionale
|  | 171 | Zuid Spanje | Spain - south | Süd - Spanien | España - Sur | Espagne - sud | Spagna meridionale
|  | 172 | Zuid Frankrijk | France - north | Nord - Frankreich | Francia - Norte | France - nord | Francia settentrionale
|  | 173 | Noord Frankrijk | France - south | Süd - Frankreich | Francia - Sur | France - sud | Francia meridionale
|  | 174 | Denemarken | Denmark | Dänemark | Dinamarca | Danemark | Danimarca
|  | 175 | Belgie | Belgium | Belgien | Belgica | Belgique | Belgio
|  | 176 | Oostenrijk | Austria | Österreich | Austria | Autriche | Austria
|  | 177 | Ierland | Ireland | Irland | Irlanda | Irlande | Irlanda
|  | 178 | Luxemburg | Luxemburg | Luxemburg | Luxemburgo | Luxembourg | Lussemburgo
|  | 179 | Portugal | Portugal | Portugal | Portugal | Portugal | Portogallo
|  | 180 | Noord Europa | Europe - north | Nord - Europa | Europa - Norte | Europe -nord | Europa settentrionale
|  | 181 | Oost Europa | Europe - east | Ost - Europa | Europa - Este | Europe - ouest | Europa orientale
|  | 182 | Zuid Oost Europa | Europe - south east | Süd - Europa | Europa - Sur Este | Europe - sud est | Sud est europa
|  | 183 | Centraal Afrika | Afrika - central | Zentral - Afrika | Africa - central | Afrique - centre | Africa centrale
|  | 184 | Noord Afrika | Afrika - north | Nord - Afrika | Africa - norte | Afrique - nord | Africa settentrionale
|  | 185 | Zuid Afrika | Afrika - south | Süd - Afrika | Africa - sur | Afrique - sud | Africa meridionale
|  | 186 | Oost Azie | Asia - east | Ost - Asien | Asia - este | Asie - est | Asia orientale
|  | 187 | Zuid Azie | Asia - south | Süd - Asien | Aisa - sur | Asie- sud | Asia meridionale
|  | 188 | Centraal Azie | Asia - south east | Süd - Asien | Asia - sur este | Asie - sud est | Sud est asiatico
|  | 189 | Centraal Australie | Australia - central | Zentral - Australien | Australia - central | Australie - centre | Australia centrale
|  | 190 | Oost Australie | Australia - east | Ost - Australien | Australia - este | Australie - est | Australia orientale
|  | 191 | Noord Australie | Australia - north | Nord - Australien | Australia - norte | Australie - nord | Australia settentrionale
|  | 192 | Zuid Australie | Australia - south | Süd - Australien | Australia - sur | Australie - sud | Australia meridionale
|  | 193 | West Australie | Australia - west | West - Australien | Australia - oeste | Australie - ouest | Australia occidentale
|  | 194 | Canada | Canada | Kanada | Canada | Canada | Canada
|  | 195 | Midden Amerika | Central America | Mittelamerika | Centro América | Amérique centrale | America centrale
|  | 196 | Midden Oosten | Middle East | der Mittlere Orient | Medio Este | Moyen-orient | Medio oriente
|  | 197 | Nieuw Zeeland | New Zealand | Neuseeland | Nueva Zelanda | Nouvelle zellande | Nuova zelanda
|  | 198 | Zuid Amerika - Centraal | Southern America - central | Zentral - Südamerika | Sudamérica - central | Amérique du sud - centre | Sud America centrale
|  | 199 | Zuid Amerika - Noord | Southern America - north | Nord - Südamerika | Sudamérica - norte | Amérique du sud - nord | Sud america settentrionale
|  | 200 | Zuid Amerika - Zuid | Southern America - south | Süd - Südamerika | Sudamérica - sur | Amérique du sud - sud | Sud america meridionale
|  | 201 | USA - Centraal | United States - central | Zentral - Amerika | Estados Unidos - central | USA - centre | Stati uniti centrali
|  | 202 | USA - Noord | United States - north | Nord - Amerika | Estados Unidos - norte | USA - nord | Stati uniti settentrionali
|  | 203 | USA - Zuid | United States - south | Süd - Amerika | Estados Unidos - sur | USA - sud | Stati uniti meridionali
204
205
206
207
208
209
210
211
|  | 212 | MODULE_BETA MOET EEN NEGATIEF GETAL ZIJN! | MODULE_BETA HAS TO BE A NEGATIVE NUMBER! | MODULE_BETA MUSS NEGATIV SEIN! | MODULE_BETA TIENE QUE SER NEGATIVO! | MODULE_BETA HAS TO BE A NEGATIVE NUMBER! | MODULE_BETA HAS TO BE A NEGATIVE NUMBER!
213
214
215
216
217
218
219
220
221
222
223
|  | 224 | QS3500 IP44 parallel | QS3500 IP44 parallel | QS3500 IP44 parallele | QS3500 IP44 paralelo | QS3500 IP44 parallèle | QS 3500 IP44 parallelo
|  | 225 | QS6400 parallel | QS6400 parallel | QS6400 parallele | QS6400 paralelo | QS6400 parallèle | QS 6400 parallelo
|  | 226 | QS6400 (4600W ac) | QS6400 (4600W ac) | QS6400 (4600W ac) | QS6400 (4600W ac) | QS6400 (4600W ac) | QS 6400 (4600W ac)
|  | 227 | QS6400 parallel (4600W ac) | QS6400 parallel (4600W ac) | QS6400 parallele (4600W ac) | QS6400 paralelo (4600W ac) | QS6400 parallèle (4600W ac) | QS 6400 prallelo (4600W ac)
|  | 228 | QS3500 IP44 Max-I parallel | QS3500 IP44 Max-I parallel | QS3500 IP44 Max-I parallele | QS3500 IP44 Max-I paralelo | QS3500 IP44 Max-I parallèle | QS 3500 IP44 Max-I parallelo
|  | 229 | QS6400 Max-I parallel | QS6400 Max-I parallel | QS6400 Max-I parallele | QS6400 Max-I paralelo | QS6400 Max-I parallèle | QS 3200 Max-I parallelo
|  | 230 | QS6400 Max-I (4600W ac) | QS6400 Max-I (4600W ac) | QS6400 Max-I (4600W ac) | QS6400 Max-I (4600W ac) | QS6400 Max-I (4600W ac) | QS 6400 Max-I (4600W ac)
|  | 231 | QS6400 Max-I parallel (4600W ac) | QS6400 Max-I parallel (4600W ac) | QS6400 Max-I parallele (4600W ac) | QS6400 Max-I paralelo (4600W ac) | QS6400 Max-I parallèle (4600W ac) | QS 6400 Max-I parallelo (4600W ac)
232
233
234
235
236
237
238
|  | 239 | De gekozen module en omvormer combinatie heeft geen optimale energie opbrengst | The chosen module and inverter combination has no optimal energy yield | Das gewählte Modul liefert mit den gewählten WR keine optimale Energieumwandlung | La cominación de inversor y paneles elegida no tiene un resultado optimo. | La combinaison choisie de module et de onduleur n'est pas optimale en énergie produite | La configurazione scelta moduli-inverter non ha una resa ottimale
|  | 240 | Het aangesloten PV vermogen is onder de gegeven systeem parameters te laag | The connected PV power is too low | Selektierte PV Leistung ist zu niedrig | La potencia FV conectada es demasiado baja | La puissance PV connectée est trop basse | La potenza FV collegata è troppo bassa
|  | 241 | Het aangesloten PV vermogen is toelaatbaar | The connected PV power is acceptable | Selektierte PV Leistung is zulässig | La potencia FV conectada es aceptable | La puissance PV connectée est acceptable | La potenza FV collegata è accettabile
|  | 242 | Het aangesloten PV vermogen sluit goed aan bij de gekozen omvormer | The connected PV power is optimal | Selektierte PV Leistung ist optimal | La potencia FV conectada es óptima | La puissance Photovoltaïque est optimale | La potenza FV è ottimale
|  | 243 | De onderdimensionering van de omvormer is kleiner dan de | The underdimensioning of the inverter is larger than the | Die resultierende Unterdimensionierungsfaktor ist kleiner als | El dimensionado inferior del inversor es mayor que | Le surdimensionnement du onduleur est plus large que | Il sottodimensionamento dell'inverter è maggiore di
|  | 244 | die u gespecificeerd heeft | that you specified |  | lo especificado. | vous avez spécifié | Quanto specificato
|  | 245 | De omvormer kan alle energie uit de PV modules omzetten | The inverter will convert all the available solar power | Die Anlage hat eine optimale Energieumwandlung | El sistema tiene un campo de energía óptimo | Le système à une production optimale d'énergie | Il sistema ha una resa energetica ottimale
|  | 246 | De omvormer kan niet alle energie omzetten wegens stroombegrenzing | no optimal energy yield because of DC current limiting | nicht optimale Energieumwandlung wegend Begrenzung der DC-Strom | Producción de energía no optima por la limitación de la intensidad CC | pas de production optimale d'énergie à cause d'une intensité CC limitée | La resa non è ottimale per limitazione di corrente
|  | 247 | Incidenteel zal de omvormer de stroom begrenzen | no optimal energy yield because of DC current limiting | nicht optimale Energieumwandlung wegend Begrenzung der DC-Strom | Producción de energía no óptima por la limitación de la intensidad CC | pas de production optimale d'énergie à cause d'une intensité CC limitée | La resa non è ottimale per limitazione di corrente
|  | 248 | De omvormer kan niet alle energie omzetten wegens vermogensbegrenzing | no optimal energy yield because of power limiting | nicht optimale Energieumwandlung wegend Leistungsbegrenzung | Producción de energía no óptima por la limitación de potencia. | pas de production optimale d'énergie à cause d'une puissance limitée | Resa non ottimale per limitazione di potenza
|  | 249 | De energie-omzetting is optimaal | Optimal energy conversion of available solar power | Optimale Energieumwandlung | Producción de energía óptima | production optimale d'énergie | Resa ottimale
|  | 250 | Er is een minmaal energieverlies doordat de omvormer aan het begrenzen is bij max instraling | minimal energy loss because of power limiting at max irradiation | kleine Verluste durch Leistungsbegrenzung bei max Einstrahlung | Perdidas de energías mínimas debido a la limitación de potencia a máx. raciación | perte minimum d'énergie car la puissance est limitée à irradiation max | Perdite minime per limitazione di potenza ad irraggiamento massimo
|  | 251 | Deze configuratie heeft relatief veel energieverlies bij max instraling | This configuration has a relatively high energy loss at max irradiation | nicht-optimale Energieumwandlung bei max Einstrahlung | Esta configuración tiene unas perdidas relativamente altas a la máx. radiación. | Cette configuration a relativement une perte importante à irradiation max | La configurazione ha perdite relativamente alte a massimo irraggiamento
|  | 252 | De opstartspanning is te laag | The startup voltage is too low | Anlaufspannung zu niedrig | El voltaje de arranque es demasiado bajo | La tension de départ est trop basse | La tensione di avvio è troppo bassa
|  | 253 | De opstartspanning is te hoog | The startup voltage is too high | Anlaufspannung zu hoch | El voltaje de arranque es demasiado alto | La tension de départ est trop élevée | La tensione di avvio è troppo alta
|  | 254 | De opstartspanning is goed | The startup voltage is optimal | Anlaufspannung ist optimal | El voltaje de arranque es óptimo | La tension de départ est optimale | La tensione di avvio è ottimale
|  | 255 | De MPP-spanning bij de min module temperatuur is te laag | The MPP-voltage is too low | Mpp-Spannung bei untere Modultemperatur zu niedrig | El voltaje MPP es demasiado bajo | La tension MPP est trop basse | La tensione MPP è troppo bassa
|  | 256 | De MPP-spanning bij de min module temperatuur is goed | The MPP-voltage at min module temperature is optimal | MPP-Spannung bei untere Modultemperatur innerhalb des Arbeitsbereichs | El voltaje MPP a la temperatura mínima del módulo es optimo. | La tension MPP à température min de module est optimale | La tensione di MPP a bassa temperatura del modulo è ottimale
|  | 257 | De MPP-spanning bij de min module temperatuur is te hoog | The MPP-voltage at min module temperature is too high | MPP-Spannung bei untere Modultemperatur ist zu hoch | El voltaje MPP a la temperatura mínima de los módulos es demasiado alto. | La tension MPP à température min de module est trop élevée | La tensione di MPP a bassa temperatura del modulo è troppo alta
|  | 258 | De openklemspanning bij de min module temperatuur is te laag | The open circuit voltage at min module temperature is too low | Leerlaufaspannung bei untere Modultemperatur zu niedrig | El voltaje en circuito abierto de los módulos a la temperatura mín. es demasiado bajo. | La tension de circuit ouvert à température min de module est trop basse | La tensione a circuito aperto è troppo bassa
|  | 259 | De openklemspanning bij de min module temperatuur is goed | The open circuit voltage at min module temperature is within the operating window | Leerlaufaspannung bei untere Modultemperatur innerhalb des Arbeitsbereichs | El voltaje en circuito abierto a la temperatura mín. esta dentro del rango operativo. | La tension de circuit ouvert à t° min de module est optimale | Latensione a circuito aperto a bassa temperatura è nella finestra ammessa
|  | 260 | De openklemspanning bij de min module temperatuur is te hoog | The open circuit voltage at min module temperature is too high | Leerlaufaspannung bei untere Modultemperatur ist zu hoch | El voltaje en circuito abierto de los módulos a la temperatura mín. es demasiado alto. | La tension de circuit ouvert à température min est trop élevée | La tensione a circuito aperto a bassa temperatura è troppo alta
|  | 261 | Het aantal aangesloten modules overschrijdt het ingegeven totaal aantal modules! | The number of connected modules on the inverter exceeds the indicated total modules range! | Gesamt Modulzahl überschritten! | El número de módulos conectados al inversor excede al rango indicado. | Le nombre de modules connectés sur le onduleur excède la plage indiquée | Il numero dei moduli collegato all'inverter supera il massimo consentito
|  | 262 | Het aantal aangesloten modules ligt onder het door u ingegeven totaal aantal | The number of connected modules is within the indicated total modules range | Gewählte Modulzahl ist unterhalb gesamt Modulzahl | El número de módulos conectados esta dentro del rango de módulos indicado. | Le nombre de modules connectés sur le onduleur est dans la plage indiquée | Il numero di moduli collegatirientra nella gamma ammessa
|  | 263 | Het aantal aangesloten modules is gelijk aan het ingegeven totaal aantal modules | The number of connected modules is lower than the indicated total modules range | Gewählte Modulzahl ist gleich gesamt Modulzahl | El número de módulos conectados es menor que el número total indicado. | Le nombre de modules connectés sur le onduleur est inférieur à celui de la plage indiquée | Il numero di moduli collegati è inferiore al minimo consentito
|  | 264 | De omvormer efficiëntie zal het meest optimaal zijn rond de | Inverter efficiency will be most optimal for DC voltages close to | Wirkungsgrad des Wechselrichters wird optimal für DC-Spannungen Nähe | La eficiencia del convertidor será óptima con un voltaje CC cerca de | Le rendement de l’onduleur sera optimal avec des tensions CC proches de | L'efficienza del convertitore è ottimale con una tensione continua circa
265
266
267
268
269
|  | 270 | NOG NIET FUNCTIONEEL | NOT YET FUNCTIONAL | NOCH NICHT FUNKTIONELL | NO DISPONIBLE | FONCTIONALITE NON DISPONIBLE | Non ancora funzionale
271
272
273
274
|  | 275 | Resultaatblad SysCalc | Result page SysCalc | SysCalc Ergebnisse | Pagína de resultados SysCalc | Page du résultat SysCalc | Syscalc pagina dei risultati
|  | 276 | Met behulp van de Mastervolt PV System Calculator is onderstaande systeemconfiguratie samengesteld. | The following system configuration was designed using the Mastervolt PV System Calculator | Unterstehende Projektierung wurde mit Hilfe vom Mastervolt System Calculator ausgeführt. | Con la ayuda del PV System Calculator, la configuración del sistema se compone de. | A l'aide du Mastervolt PV System Calculator une configuration de système est composée. | Con l'aiuto di Mastervolt PV System Calculator è stata definita la configurazione.
277
|  | 278 | Bij de berekening van deze configuratie is uitgegaan van de volgende gegevens. | The system design is based on the following data. | Die Projektierung basiert auf nachfolgende Daten. | Se han usado los siguientes datos para los cálculos. | Les données suivantes sont utilisées pour le calcul de cette configuration. | Per il calcolo di questa configurazione si usano i seguenti dati.
|  | 279 | Module temperatuur | module temperature | Modultemperatur | Temperatura de modulo | Température de panneau | Temperatura di modulo
280
281
|  | 282 | EU efficientie | EU efficiency | EU Wirkungsgrad | Eficiencia EU | Rendement EU | Rendimento EU
283
|  | 284 | De volgende configuratie is ingesteld | The following configuration was set | Folgende Konfiguration wurde eingestellt | Se ha fijado la siguiente configuración | La configuration suivante a été entrée | E' sata scelta la configurazione seguente
|  | 285 | Totaal aantal modules | Total number of modules | Gesamt Module | Número total de módulos | Nombre total de panneaux | Numero totale di moduli
|  | 286 | Belangrijkste configuratie specificaties | Key configuration data | Kennzahlen der Projektierung | Especificaciones importantes de configuración | Spécifications importantes de configuration | Parametri importanti della configurazione
|  | 287 | Pnom @ 25°C | Pnom @ 25°C | Pnom @ 25°C | Pnom @ 25ºC | Pnom @ 25°C | Pnom @ 25°C
|  | 288 | Totaal Pnom | Total Pnom | Gesamtleistung | Pnom Total | Pnom total | Pnom totale
|  | 289 | Result. Onderdim. (ODF) | Result. Underdim. Fact. (UDF) | Result. Unterdim. (UDF) | UDF resultante | UDF résultante | UDF attuale
|  | 290 | Impp bij | Impp at | MPP-Strom bei | Impp a | Impp à | Impp a
291
292
293
294
295
296
297
298
299
300

## Module Specs
module :
specifications at STC (25°C / 1.000W m²)
manufacturer : |  | Scheuten
type of module : |  | MULTISOL 200A 200Wp
nominal power : |  | 200
open circuit voltage : | * / ** | 57.5
MPP voltage : |  | 47.5
short circuit current : |  | 5.01
MPP current : |  | 4.21
*Please make sure the maximum system voltage of the modules is not exceeded.
**Warning! Be aware of aging effects (>Voc) of Thin-film modules in the first 8-10 weeks

## Inverter Specs
inverter :
type : | CS20TL
Typical String Length : | --
allowed ambient temperature : | -20°C to 60°C
allowed rel. humidity : | max. 95%
protection Degree : | IP65
Safety class : | class I
Galvanic isolation : | --
dimensions : | 1000 x 650 x 250 mm
weight : | 65 kg
solar input (DC)
nominal DC power : | 20618
max. DC power : | 21649
suggested PV power : | 18000-25000 Wp
number of MPP-inputs : | 2
no. of strings by MPP-input : | 2
MPP tracker : | 2 Dynamic MPP Trackers
min. DC voltage : | 250
MPP voltage : | 350-800V
max. DC voltage : | 950
max. DC current : | 2x 30A
Nominal DC voltage : | 650
Grid output (AC)
AC voltage : | 400
nominal AC power : | 20000
max. AC power : | 21000
nominal AC-current : | 3 x 30
frequency : | 50/60Hz
Power Factor : | 0.99
THD : | < 3%
efficiency, european related : | 97%
max. efficiency : | 98%

## Cable losses
| DC cabling |  |  |  |  | AC cabling
| input 1 | input 2 | input 3 | input 4
no. of strings : | 5 | 5 | 1 | 1
cable material : |  |  |  |  | cable material :
cable diameter : |  |  |  |  | cable diameter :
cable length : |  |  |  |  | cable length :
total length : | 50 | 50 | 190 | 10 | total length : | 40
total cableresistance : | 0.14583 | 0.14583 | 0.83125 | 0.07 | total cableresistance : | 0.058333
DC-current String : | 4.0573 | 4.0573 | 0 | 0 | AC Power : | 19206
energieloss by String : | 2.4006 | 2.4006 | 0 | 0 | Grid voltage : | 400
total energyloss by input : | 12.003 | 12.003 | 0 | 0 | Grid current : | 27.8348
Available power : | 9900 | 9900 | 0 | 0 | Voltagedrop across cable : | 1.6237
energieloss at max irradiance : | 0.1212% | 0.1212% | 0% | 0%
total loss in cabling : | 24.0061 |  |  |  | total loss in cabling : | 135.5856
Available power : | 19800 |  |  |  | Available power : | 19070.4144
energieloss at max irradiance : | 0.1212% |  |  |  | energieloss at max irradiance : | 0.706%

## Results
Result page SysCalc
The following system configuration was designed using the Mastervolt PV System Calculator
The system design is based on the following data.
location : | Germany - central
module temperature : | -10°C - 45°C
orientation : | S
gradient : | 30°
inverter : | CS20TL
| - | suggested PV power : |  |  | 18000-25000 Wp
| - | number of MPP-inputs : |  |  | 2
| - | no. of strings by MPP-input : |  |  | 2
| - | nominal DC power : |  |  | 20618
| - | max. DC voltage : |  |  | 950
| - | MPP voltage : |  |  | 350-800V
| - | max. DC current : |  |  | 2x 30A
| - | max. efficiency : |  |  | 98%
| - | EU efficiency : |  |  | 97%
| - | protection Degree : |  |  | IP65
module : | Scheuten : MULTISOL 200A 200Wp
specifications at STC (25°C / 1.000W m²) :
| - | nominal power : |  | 200
| - | open circuit voltage : |  | 57.5
| - | MPP voltage : |  | 47.5
| - | short circuit current : |  | 5.01
| - | MPP current : |  | 4.21
The following configuration was set :
|  | input 1 | input 2 | input 3
modules per string : |  | 11 | 11 | 5 | 1
no. of strings : |  | 5 | 5 | h | 1
Total number of modules : |  | 110
Key configuration data :
|  | input 1 | input 2 | input 3 | input 4
Pnom @ 25°C : |  | 11000 | 11000 | 1000 | 200
Total Pnom : |  | 22000
Result. Underdim. Fact. (UDF) : |  | 0.93718 | 0.93718 | 10.309 | 51.545
Uoc at -10°C : |  | 705.5538 | 705.5538 | 320.7063 | 64.1412
Umpp at 45°C : |  | 488.015 | 488.015 | 221.825 | 44.365
Impp at 45°C : |  | 20.2863 | 20.2863 | 4.0573 | 4.0573
Output
Sac: |  | 19070.4144
Pac: |  | 19070.4144
Note on A54: Complex power at Tmax, including the UDF, cable losses and inverter efficiency
Note on A55: Real Power (The value from which the final kWh can be calculated)

## Kabelverlies (hidden)
KABELVERLIEZEN
effect op Kleur
Bovengrens toegestane energieverlies in de bekabeling: |  |  |  | 2%
Ondergrens toegestane energieverlies in de bekabeling: |  |  |  | 1%
Ondergrens max toelaatbare spanningsval over AC bekabeling: |  |  |  | 9
Bovengrens max toelaatbare spanningsval over AC bekabeling: |  |  |  | 7
Max weerstand AC bekabeling ivm ENS: |  |  |  | 0.5
| input 1 |  | input 2 | [6 empty] | AC
| Waarde | Kleur | Waarde | Kleur | Waarde | Kleur | Waarde | Kleur |  | Waarde | Kleur
Aantal strings : | 5 |  | 5 |  | 1 |  | 1
Kabelmateriaal : | copper |  | copper |  | copper |  | copper |  | Kabelmateriaal : | copper
Soortelijke weerstand : | 1.75e-08 |  | 1.75e-08 |  | 1.75e-08 |  | 1.75e-08 |  | Soortelijke weerstand : | 1.75e-08
Kabeldoorsnede (mm²) : | 6 |  | 6 |  | 4 |  | 2.5 |  | Kabeldoorsnede (mm²) : | 6
Enkelvoudige kabellengte : | 25 |  | 25 |  | 95 |  | 5 |  | Enkelvoudige kabellengte : | 20
Totale lengte : | 50 |  | 50 |  | 190 |  | 10 |  | Totale lengte : | 40
Totale kabelweerstand : | 0.14583 |  | 0.14583 |  | 0.83125 |  | 0.07 |  | Totale kabelweerstand : | 0.058333 | 1
DC-stroom String : | 4.0573 |  | 4.0573 |  | 0 |  | 0 |  | European efficiency: | 0.97
Energieverlies per String : | 2.4006 |  | 2.4006 |  | 0 |  | 0 |  | AC vermogen: | 19206
Totale energieverlies per ingang : | 12.003 |  | 12.003 |  | 0 |  | 0 |  | Netspanning: | 400
Totale omgezette energie: : | 9900 |  | 9900 |  | 0 |  | 0 |  | Netstroom | 27.8348
Energieverlies bij max instraling in % : | 0.1212% | 1 | 0.1212% | 1 | 0% | 1 | 0% | 1 | Spanningsval over kabel: | 1.6237 | 1
Energieverlies in W/m : | 0.24006 |  | 0.24006 |  | 0 |  | 0
Totale verlies in de bekabeling : | 24.0061 | [7 empty] | 135.5856 | 45.1952
Totale omgezette energie: : | 19800 | [7 empty] | 19070.4144 | 19160.8048
Energieverlies bij max instraling in % : | 0.1212% | [6 empty] | 1 | 0.706% |  | 1

## MODULES
|  | Juiste Beta? | FALSE
|  | Geselecteerde Module: | 2293
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
| module_brand | module_type | Combination brand & type | module_beta [%/°C] | module_Voc [V] | module_Isc [A] | module_Pmppt [W] | module_Vmppt [V] | module_Imppt [A]
**Please note: module_beta (=Temperature coefficient) definition has been changed from previous SysCals version**
**Enter beta in [%/°C] which is specified in most datasheets**
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
| BRAND | TYPE | BRAND : TYPE | CALCULATE!
1 | Advent Solar | Advent 160 | Advent Solar : Advent 160 | -0.345 | 42.7 | 5.37 | 160 | 32.7 | 4.9
2 | Advent Solar | Advent 165 | Advent Solar : Advent 165 | -0.345 | 42.8 | 5.52 | 165 | 33.4 | 4.95
3 | Advent Solar | Advent 170 | Advent Solar : Advent 170 | -0.345 | 42.9 | 5.66 | 170 | 34 | 5.01
4 | Advent Solar | Advent 175 | Advent Solar : Advent 175 | -0.345 | 43 | 5.76 | 175 | 34.3 | 5.12
5 | Advent Solar | Advent 180 | Advent Solar : Advent 180 | -0.345 | 43.1 | 5.9 | 180 | 34.6 | 5.22
6 | Advent Solar | Advent 210 | Advent Solar : Advent 210 | -0.36 | 35.1 | 8.23 | 210 | 28.43 | 7.39
7 | Advent Solar | Advent 215 | Advent Solar : Advent 215 | -0.36 | 35.4 | 8.27 | 215 | 28.74 | 7.49
8 | Advent Solar | Advent 220 | Advent Solar : Advent 220 | -0.36 | 35.7 | 8.4 | 220 | 29.06 | 7.62
9 | Advent Solar | Advent 225 | Advent Solar : Advent 225 | -0.36 | 36 | 8.52 | 225 | 29.34 | 7.75
10 | Advent Solar | Advent 230 | Advent Solar : Advent 230 | -0.36 | 36.3 | 8.57 | 230 | 29.66 | 7.83
11 | Advent Solar | Advent 235 | Advent Solar : Advent 235 | -0.36 | 36.3 | 8.64 | 235 | 29.69 | 7.93
12 | Advent Solar | Advent 240 | Advent Solar : Advent 240 | -0.36 | 36.6 | 8.69 | 240 | 30.01 | 7.99
13 | AET | Sunglobe E 165P | AET : Sunglobe E 165P | -0.34 | 30.2 | 7.5 | 165 | 23.8 | 6.94
14 | AET | Sunglobe E 175P | AET : Sunglobe E 175P | -0.34 | 30.7 | 7.8 | 175 | 24.3 | 7.21
15 | AIDE Solar | XZST170-24/A mono | AIDE Solar : XZST170-24/A mono | -0.37 | 43.8 | 5.15 | 170 | 35.2 | 4.83
16 | AIDE Solar | XZST170-24/B poly | AIDE Solar : XZST170-24/B poly | -0.37 | 43.8 | 5.14 | 170 | 35.2 | 4.83
17 | AIDE Solar | XZST180-24/B poly | AIDE Solar : XZST180-24/B poly | -0.37 | 44.8 | 5.3 | 180 | 36 | 5
18 | AIDE Solar | XZST190-24/A mono | AIDE Solar : XZST190-24/A mono | -0.37 | 45.2 | 5.39 | 190 | 36.8 | 5.16
19 | AIDE Solar | XZST190-24/B poly | AIDE Solar : XZST190-24/B poly | -0.37 | 45.2 | 5.39 | 190 | 36.8 | 5.16
20 | AIDE Solar | XZST200-18/A mono | AIDE Solar : XZST200-18/A mono | -0.37 | 32.8 | 8 | 200 | 26.2 | 7.63
21 | AIDE Solar | XZST200-18/B poly | AIDE Solar : XZST200-18/B poly | -0.37 | 32.8 | 8 | 200 | 26.2 | 7.63
22 | AIDE Solar | XZST210-18/A mono | AIDE Solar : XZST210-18/A mono | -0.37 | 33.2 | 8.1 | 210 | 26.6 | 7.89
23 | AIDE Solar | XZST210-18/B poly | AIDE Solar : XZST210-18/B poly | -0.37 | 33.2 | 8.1 | 210 | 26.6 | 7.89
24 | AIDE Solar | XZST220-18/A mono | AIDE Solar : XZST220-18/A mono | -0.37 | 34.3 | 8.52 | 220 | 26.8 | 8.2
25 | AIDE Solar | XZST220-18/B poly | AIDE Solar : XZST220-18/B poly | -0.37 | 34.3 | 8.52 | 220 | 26.8 | 8.2
26 | AIDE Solar | ZXST175-24/A mono | AIDE Solar : ZXST175-24/A mono | -0.37 | 44 | 5.21 | 175 | 35.6 | 4.91
27 | AIDE Solar | ZXST180-24/A mono | AIDE Solar : ZXST180-24/A mono | -0.37 | 44.8 | 5.3 | 180 | 36 | 5
28 | Air Water | H-5510 | Air Water : H-5510 | -0.348 | 22.1 | 3.68 | 58 | 17.8 | 3.26
29 | Air Water | H-7410 | Air Water : H-7410 | -0.349 | 27.2 | 3.68 | 74 | 21.8 | 3.39
30 | Air Water | H-8620 | Air Water : H-8620 | -0.352 | 21.9 | 5.31 | 86 | 17.6 | 4.89
31 | Aleo Solar | 150 L | Aleo Solar : 150 L | -0.33 | 43.6 | 4.9 | 160 | 35.5 | 4.5
32 | Aleo Solar | 150 M | Aleo Solar : 150 M | -0.33 | 43.5 | 4.85 | 155 | 35.4 | 4.4
33 | Aleo Solar | 150 S | Aleo Solar : 150 S | -0.33 | 43.4 | 4.7 | 150 | 35.4 | 4.25
34 | Aleo Solar | 150 Super S | Aleo Solar : 150 Super S | -0.33 | 43 | 4.5 | 135 | 34.5 | 3.9
35 | Aleo Solar | 150 XL | Aleo Solar : 150 XL | -0.33 | 43.7 | 5.05 | 165 | 35.6 | 4.65
36 | Aleo Solar | 150 XS | Aleo Solar : 150 XS | -0.33 | 43.3 | 4.6 | 145 | 35.3 | 4.1
37 | Aleo Solar | 150 XXL | Aleo Solar : 150 XXL | -0.33 | 43.8 | 5.1 | 170 | 35.7 | 4.75
38 | Aleo Solar | 150 XXS | Aleo Solar : 150 XXS | -0.33 | 43.1 | 4.55 | 140 | 35 | 4
39 | Aleo Solar | 150-6 XL | Aleo Solar : 150-6 XL | -0.35 | 30.6 | 7.35 | 165 | 23.5 | 7
40 | Aleo Solar | 150-6 L | Aleo Solar : 150-6 L | -0.35 | 30.5 | 7.2 | 160 | 23.4 | 6.8
41 | Aleo Solar | 150-6 M | Aleo Solar : 150-6 M | -0.35 | 30.4 | 7.05 | 155 | 23.3 | 6.6
42 | Aleo Solar | 150-6 S | Aleo Solar : 150-6 S | -0.35 | 30.3 | 6.9 | 150 | 23.2 | 6.4
43 | Aleo Solar | 150-6 XXL | Aleo Solar : 150-6 XXL | -0.35 | 30.7 | 7.5 | 170 | 23.6 | 7.2
44 | Aleo Solar | 180 L 175Wp | Aleo Solar : 180 L 175Wp | -0.35 | 30.7 | 7.7 | 175 | 24.9 | 7.1
45 | Aleo Solar | 180 M 170Wp | Aleo Solar : 180 M 170Wp | -0.35 | 30.6 | 7.6 | 170 | 24.5 | 7
46 | Aleo Solar | 180 XL 180Wp | Aleo Solar : 180 XL 180Wp | -0.35 | 30.8 | 7.8 | 180 | 25.3 | 7.2
47 | Aleo Solar | 180 XXL 185Wp | Aleo Solar : 180 XXL 185Wp | -0.35 | 30.95 | 7.9 | 185 | 25.7 | 7.3
48 | Aleo Solar | 200 L-6 | Aleo Solar : 200 L-6 | -0.35 | 36.85 | 7.6 | 205 | 29.3 | 7
49 | Aleo Solar | 200 M-6 | Aleo Solar : 200 M-6 | -0.35 | 36.7 | 7.5 | 200 | 29.15 | 6.85
50 | Aleo Solar | 200 S-6 | Aleo Solar : 200 S-6 | -0.35 | 36.6 | 7.35 | 195 | 28.85 | 6.75
51 | Aleo Solar | 200 XL-6 | Aleo Solar : 200 XL-6 | -0.35 | 37 | 7.65 | 210 | 29.4 | 7.15
52 | Aleo Solar | 200 XS-6 | Aleo Solar : 200 XS-6 | -0.35 | 36.5 | 7.2 | 190 | 28.4 | 6.7
53 | Aleo Solar | 200 XXL-6 | Aleo Solar : 200 XXL-6 | -0.35 | 37.15 | 7.8 | 215 | 29.7 | 7.25
54 | Aleo Solar | S_03/155 | Aleo Solar : S_03/155 | -0.35 | 43.2 | 5 | 155 | 35.3 | 4.39
55 | Aleo Solar | S_03/160 | Aleo Solar : S_03/160 | -0.35 | 43.4 | 5.05 | 160 | 35.4 | 4.52
56 | Aleo Solar | S_03/165 | Aleo Solar : S_03/165 | -0.35 | 43.6 | 5.1 | 165 | 35.5 | 4.65
57 | Aleo Solar | S_03/170 | Aleo Solar : S_03/170 | -0.35 | 43.8 | 5.15 | 170 | 35.6 | 4.78
58 | Aleo Solar | S_03/175 | Aleo Solar : S_03/175 | -0.35 | 44 | 5.2 | 175 | 35.7 | 4.9
59 | Aleo Solar | S_13 / 150 | Aleo Solar : S_13 / 150 | -0.35 | 30.4 | 7 | 150 | 23.1 | 6.5
60 | Aleo Solar | S_13 / 155 | Aleo Solar : S_13 / 155 | -0.35 | 30.5 | 7.2 | 155 | 30.5 | 6.6
61 | Aleo Solar | S_13 / 160 | Aleo Solar : S_13 / 160 | -0.35 | 30.6 | 7.3 | 160 | 23.9 | 6.7
62 | Aleo Solar | S_13 / 165 | Aleo Solar : S_13 / 165 | -0.35 | 30.7 | 7.4 | 165 | 24.3 | 6.8
63 | Aleo Solar | S_15 / 175 | Aleo Solar : S_15 / 175 | -0.35 | 36.4 | 6.95 | 175 | 27 | 6.6
64 | Aleo Solar | S_15 / 180 | Aleo Solar : S_15 / 180 | -0.35 | 36.5 | 7 | 180 | 27.5 | 6.7
65 | Aleo Solar | S_15 / 185 | Aleo Solar : S_15 / 185 | -0.35 | 36.6 | 7.1 | 185 | 28 | 6.75
66 | Aleo Solar | S_15 / 190 | Aleo Solar : S_15 / 190 | -0.35 | 36.7 | 7.2 | 190 | 28.5 | 6.8
67 | Aleo Solar | S_16/165 | Aleo Solar : S_16/165 | -0.33 | 30 | 7.9 | 165 | 23.3 | 7.08
68 | Aleo Solar | S_16/170 | Aleo Solar : S_16/170 | -0.33 | 30.1 | 7.95 | 170 | 23.5 | 7.23
69 | Aleo Solar | S_16/175 | Aleo Solar : S_16/175 | -0.33 | 30.2 | 8.1 | 175 | 23.7 | 7.38
70 | Aleo Solar | S_16/180 | Aleo Solar : S_16/180 | -0.33 | 30.3 | 8.15 | 180 | 23.9 | 7.53
71 | Aleo Solar | S_16/185 | Aleo Solar : S_16/185 | -0.33 | 30.5 | 8.2 | 185 | 24.1 | 7.47
72 | Aleo Solar | S_17/170 | Aleo Solar : S_17/170 | -0.34 | 30.2 | 8.4 | 170 | 22.6 | 7.5
73 | Aleo Solar | S_17/175 | Aleo Solar : S_17/175 | -0.34 | 30.3 | 8.41 | 175 | 23.1 | 7.57
74 | Aleo Solar | S_17/180 | Aleo Solar : S_17/180 | -0.34 | 30.4 | 8.42 | 180 | 23.6 | 7.63
75 | Aleo Solar | S_17/185 | Aleo Solar : S_17/185 | -0.34 | 30.5 | 8.43 | 185 | 24.1 | 7.67
76 | Aleo Solar | S_17/190 | Aleo Solar : S_17/190 | -0.34 | 30.6 | 8.44 | 190 | 24.6 | 7.72
77 | Aleo Solar | S_18/210 | Aleo Solar : S_18/210 | -0.33 | 36.2 | 8 | 210 | 28.4 | 7.39
78 | Aleo Solar | S_18/215 | Aleo Solar : S_18/215 | -0.33 | 36.3 | 8.11 | 215 | 28.6 | 7.5
79 | Aleo Solar | S_18/220 | Aleo Solar : S_18/220 | -0.33 | 36.4 | 8.22 | 220 | 28.8 | 7.62
80 | Aleo Solar | S_18/225 | Aleo Solar : S_18/225 | -0.33 | 36.5 | 8.33 | 225 | 29 | 7.76
81 | Aleo Solar | S_18/230 | Aleo Solar : S_18/230 | -0.33 | 36.6 | 8.44 | 230 | 29.2 | 7.88
82 | Aleo Solar | S_18/235 | Aleo Solar : S_18/235 | -0.34 | 36.8 | 8.54 | 235 | 29.3 | 8.01
83 | Aleo Solar | S_18/240 | Aleo Solar : S_18/240 | -0.34 | 37 | 8.65 | 240 | 29.5 | 8.13
84 | Aleo Solar | S_24/175 | Aleo Solar : S_24/175 | -0.34 | 29.2 | 7.97 | 175 | 23.3 | 7.51
85 | Aleo Solar | S_24/180 | Aleo Solar : S_24/180 | -0.34 | 29.3 | 8.14 | 180 | 23.4 | 7.68
86 | Aleo Solar | S_24/185 | Aleo Solar : S_24/185 | -0.34 | 29.4 | 8.31 | 185 | 23.6 | 7.85
87 | Aleo Solar | S_24/190 | Aleo Solar : S_24/190 | -0.34 | 29.5 | 8.47 | 190 | 23.7 | 8.01
88 | Aleo Solar | S_24/195 | Aleo Solar : S_24/195 | -0.34 | 29.6 | 8.64 | 195 | 23.8 | 8.18
89 | Aleo Solar | S_19/225 | Aleo Solar : S_19/225 | -0.34 | 36.6 | 8.43 | 225 | 29.3 | 7.68
90 | Aleo Solar | S_19/230 | Aleo Solar : S_19/230 | -0.34 | 36.7 | 8.44 | 230 | 29.8 | 7.72
91 | Aleo Solar | S_19/235 | Aleo Solar : S_19/235 | -0.34 | 36.8 | 8.45 | 235 | 30.3 | 7.76
92 | Aleo Solar | S_77/180 | Aleo Solar : S_77/180 | -0.34 | 30.4 | 8.42 | 180 | 23.6 | 7.63
93 | Aleo Solar | S_77/185 | Aleo Solar : S_77/185 | -0.34 | 30.5 | 8.43 | 185 | 24.1 | 7.68
94 | Aleo Solar | S_77/190 | Aleo Solar : S_77/190 | -0.34 | 30.6 | 8.44 | 190 | 24.6 | 7.72
95 | Alfasolar | 105P/12 | Alfasolar : 105P/12 | -0.33 | 21.4 | 6.54 | 105 | 17.8 | 5.89
96 | Alfasolar | 105P/24 | Alfasolar : 105P/24 | -0.33 | 42.84 | 3.27 | 105 | 35.64 | 2.95
97 | Alfasolar | 112P | Alfasolar : 112P | -0.36 | 22.37 | 6.82 | 112 | 17.68 | 6.34
98 | Alfasolar | 120M/12 | Alfasolar : 120M/12 | -0.34 | 21.7 | 7.38 | 120 | 17.9 | 6.7
99 | Alfasolar | 120M/24 | Alfasolar : 120M/24 | -0.34 | 43.4 | 3.69 | 120 | 35.8 | 3.35
100 | Alfasolar | 160P/12 | Alfasolar : 160P/12 | -0.33 | 21.42 | 9.96 | 160 | 17.82 | 8.98
101 | Alfasolar | 160P/24 | Alfasolar : 160P/24 | -0.33 | 42.8 | 4.98 | 160 | 35.64 | 4.49
102 | Alfasolar | 170P (12V) | Alfasolar : 170P (12V) | -0.35 | 22.1 | 10.8 | 170 | 17.2 | 9.88
103 | Alfasolar | 170P (24V) | Alfasolar : 170P (24V) | -0.35 | 44.2 | 5.4 | 170 | 34.4 | 4.94
104 | Alfasolar | 180 M (12V) | Alfasolar : 180 M (12V) | -0.32 | 22.6 | 11.5 | 180 | 17.3 | 10.4
105 | Alfasolar | 180 M (24V) | Alfasolar : 180 M (24V) | -0.32 | 45.2 | 5.75 | 180 | 34.6 | 5.2
106 | Alfasolar | 180PQ6L A 195Wp | Alfasolar : 180PQ6L A 195Wp | -0.33 | 33.18 | 8.66 | 195 | 25.06 | 7.82
107 | Alfasolar | 180PQ6L A 200Wp | Alfasolar : 180PQ6L A 200Wp | -0.33 | 33.21 | 8.72 | 200 | 25.27 | 7.95
108 | Alfasolar | 180PQ6L A 205Wp | Alfasolar : 180PQ6L A 205Wp | -0.33 | 33.28 | 8.8 | 205 | 25.32 | 8.1
109 | Alfasolar | 180PQ6L A 210Wp | Alfasolar : 180PQ6L A 210Wp | -0.33 | 33.49 | 8.89 | 210 | 25.58 | 8.21
110 | Alfasolar | 180PQ6L A 215Wp | Alfasolar : 180PQ6L A 215Wp | -0.33 | 33.54 | 8.95 | 215 | 25.86 | 8.32
111 | Alfasolar | 210MQ6L | Alfasolar : 210MQ6L | -0.34 | 33.53 | 8.04 | 210 | 27.5 | 7.64
112 | Alfasolar | 215MQ6L | Alfasolar : 215MQ6L | -0.34 | 33.62 | 8.86 | 215 | 26 | 8.27
113 | Alfasolar | 55S | Alfasolar : 55S | -0.4 | 21.7 | 3.65 | 55 | 17.5 | 3.15
114 | Alliantz | APV 200 PE | Alliantz : APV 200 PE | -0.353 | 32.89 | 8.02 | 200 | 26.24 | 7.63
115 | Alliantz | APV 205 PE | Alliantz : APV 205 PE | -0.351 | 33.08 | 8.26 | 205 | 26.52 | 7.76
116 | Alliantz | APV 210 PE | Alliantz : APV 210 PE | -0.35 | 33.2 | 8.42 | 210 | 26.68 | 7.89
117 | AlpinSun | Prisma M60 230W | AlpinSun : Prisma M60 230W | -0.34435 | 36.3 | 8.3 | 230 | 28.9 | 8
118 | AlpinSun | Prisma M60 235W | AlpinSun : Prisma M60 235W | -0.34341 | 36.4 | 8.5 | 235 | 28.9 | 8.2
119 | AlpinSun | Prisma M60 240W | AlpinSun : Prisma M60 240W | -0.34153 | 36.6 | 8.6 | 240 | 29 | 8.3
120 | AlpinSun | Prisma M60 245W | AlpinSun : Prisma M60 245W | -0.33967 | 36.8 | 8.8 | 245 | 29.2 | 8.4
121 | AlpinSun | Prisma M60 250W | AlpinSun : Prisma M60 250W | -0.33784 | 37 | 8.8 | 250 | 29.4 | 8.5
122 | AlpinSun | Prisma M60 255W | AlpinSun : Prisma M60 255W | -0.33512 | 37.3 | 8.9 | 255 | 29.6 | 8.6
123 | Alwitra | Evalon®-Solar | Alwitra : Evalon®-Solar | -0.214 | 47.6 | 4.8 | 128 | 33 | 3.9
124 | Alwitra | Evalon®-Solar 3.36 | Alwitra : Evalon®-Solar 3.36 | -0.214 | 23.8 | 4.8 | 64 | 16.5 | 3.9
125 | Alwitra | Evalon®-Solar 6.0 | Alwitra : Evalon®-Solar 6.0 | -0.214 | 47.6 | 4.8 | 128 | 33 | 3.9
126 | Amerisolar | AS-5M (170W) | Amerisolar : AS-5M (170W) | -0.33 | 44.19 | 5.2 | 170 | 35.68 | 4.77
127 | Amerisolar | AS-5M (175W) | Amerisolar : AS-5M (175W) | -0.33 | 44.36 | 5.28 | 175 | 35.88 | 4.88
128 | Amerisolar | AS-5M (180W) | Amerisolar : AS-5M (180W) | -0.33 | 44.53 | 5.37 | 180 | 36.08 | 4
129 | Amerisolar | AS-5M (185W) | Amerisolar : AS-5M (185W) | -0.33 | 44.7 | 5.45 | 185 | 36.28 | 5.1
130 | Amerisolar | AS-5M (190W) | Amerisolar : AS-5M (190W) | -0.33 | 44.87 | 5.54 | 190 | 36.48 | 5.21
131 | Amerisolar | AS-5M (195W) | Amerisolar : AS-5M (195W) | -0.33 | 45.04 | 5.63 | 195 | 36.67 | 5.32
132 | Amerisolar | AS-6P30 (200W) | Amerisolar : AS-6P30 (200W) | -0.38 | 36 | 7.52 | 200 | 29.5 | 6.78
133 | Amerisolar | AS-6P30 (205W) | Amerisolar : AS-6P30 (205W) | -0.38 | 36.1 | 7.67 | 205 | 29.6 | 6.93
134 | Amerisolar | AS-6P30 (210W) | Amerisolar : AS-6P30 (210W) | -0.38 | 36.2 | 7.82 | 210 | 29.7 | 7.08
135 | Amerisolar | AS-6P30 (215W) | Amerisolar : AS-6P30 (215W) | -0.38 | 36.4 | 7.97 | 215 | 29.7 | 7.24
136 | Amerisolar | AS-6P30 (220W) | Amerisolar : AS-6P30 (220W) | -0.38 | 36.5 | 8.12 | 220 | 29.8 | 7.4
137 | Amerisolar | AS-6P30 (225W) | Amerisolar : AS-6P30 (225W) | -0.38 | 36.7 | 8.18 | 225 | 29.9 | 7.53
138 | Amerisolar | AS-6P30 (230W) | Amerisolar : AS-6P30 (230W) | -0.38 | 36.8 | 8.34 | 230 | 30 | 7.67
139 | Amerisolar | AS-6P30 (235W) | Amerisolar : AS-6P30 (235W) | -0.38 | 36.9 | 8.44 | 235 | 30.1 | 7.81
140 | Amerisolar | AS-6P30 (240W) | Amerisolar : AS-6P30 (240W) | -0.38 | 37 | 8.54 | 240 | 30.2 | 7.95
141 | AmpleSun | ASF-100 | AmpleSun : ASF-100 | -0.33 | 99 | 1.65 | 100 | 77 | 1.29
142 | AmpleSun | ASF-90 | AmpleSun : ASF-90 | -0.33 | 98 | 1.59 | 90 | 37 | 1.24
143 | ANDROMEDA | AR212 | ANDROMEDA : AR212 | -0.37 | 40 | 3.25 | 100 | 32 | 3.15
144 | Antec Solar | ATF 36 | Antec Solar : ATF 36 | -0.274 | 82 | 1.06 | 36 | 46 | 0.78
145 | Antec Solar | ATF 43 | Antec Solar : ATF 43 | -0.25 | 81 | 1.07 | 43 | 53 | 0.81
146 | Antec Solar | ATF 50 | Antec Solar : ATF 50 | -0.25 | 85 | 1.11 | 50 | 56 | 0.89
147 | APRISUN | PV TA 150 | APRISUN : PV TA 150 | -0.38 | 43.4 | 4.88 | 150 | 34.8 | 4.31
148 | APRISUN | PV TA 170 | APRISUN : PV TA 170 | -0.38 | 44.5 | 5.12 | 170 | 35.9 | 4.74
149 | APRISUN | PV TA 175 | APRISUN : PV TA 175 | -0.38 | 44.8 | 5.17 | 175 | 36 | 4.86
150 | ARINNA | Exklusiv 36 Glas-Glas 130Wp | ARINNA : Exklusiv 36 Glas-Glas 130Wp | -0.35 | 22.03 | 7.82 | 130 | 18 | 7.23
151 | ARINNA | Exklusiv 36 Glas-Glas 135Wp | ARINNA : Exklusiv 36 Glas-Glas 135Wp | -0.347 | 22.2 | 7.89 | 135 | 18.3 | 7.37
152 | ARINNA | Exklusiv 36 Glas-Glas 140Wp | ARINNA : Exklusiv 36 Glas-Glas 140Wp | -0.343 | 22.45 | 8.06 | 140 | 18.65 | 7.54
153 | ARINNA | Peakpower 60 220Wp | ARINNA : Peakpower 60 220Wp | -0.35 | 36.9 | 7.85 | 220 | 30.2 | 7.28
154 | ARINNA | Peakpower 60 225Wp | ARINNA : Peakpower 60 225Wp | -0.349 | 37 | 7.89 | 225 | 30.5 | 7.37
155 | ARINNA | Peakpower 60 230Wp | ARINNA : Peakpower 60 230Wp | -0.346 | 37.32 | 8 | 230 | 30.84 | 7.48
156 | ARINNA | Peakpower 60/A 200Wp | ARINNA : Peakpower 60/A 200Wp | -0.35 | 35.6 | 7.9 | 200 | 27.8 | 7.2
157 | ARINNA | Peakpower 60/A 205Wp | ARINNA : Peakpower 60/A 205Wp | -0.35 | 35.9 | 8 | 205 | 28.1 | 7.3
158 | ARINNA | Peakpower 60/A 210Wp | ARINNA : Peakpower 60/A 210Wp | -0.35 | 36.1 | 8.1 | 210 | 28.3 | 7.45
159 | ARINNA | Peakpower 60/A 215Wp | ARINNA : Peakpower 60/A 215Wp | -0.35 | 36.3 | 8.2 | 215 | 28.5 | 7.55
160 | ARINNA | Peakpower 60/A 220Wp | ARINNA : Peakpower 60/A 220Wp | -0.35 | 36.4 | 8.3 | 220 | 28.8 | 7.65
161 | ARINNA | Peakpower 60/A 225Wp | ARINNA : Peakpower 60/A 225Wp | -0.35 | 36.6 | 8.4 | 225 | 28.9 | 7.8
162 | ARINNA | Peakpower 60/A 230Wp | ARINNA : Peakpower 60/A 230Wp | -0.35 | 36.7 | 8.55 | 230 | 29 | 7.95
163 | ARINNA | Premium 48 175Wp | ARINNA : Premium 48 175Wp | -0.349 | 29.52 | 7.85 | 175 | 24.16 | 7.28
164 | ARINNA | Premium 48 180Wp | ARINNA : Premium 48 180Wp | -0.348 | 29.6 | 7.89 | 180 | 24.4 | 7.37
165 | ARINNA | Premium 48 185Wp | ARINNA : Premium 48 185Wp | -0.345 | 29.86 | 8 | 185 | 24.67 | 7.48
166 | ARINNA | Ventus 40 platin 145Wp | ARINNA : Ventus 40 platin 145Wp | -0.35 | 24.6 | 7.85 | 145 | 20.11 | 7.24
167 | ARINNA | Ventus 40 platin 150Wp | ARINNA : Ventus 40 platin 150Wp | -0.349 | 24.67 | 7.89 | 150 | 20.34 | 7.37
168 | ARINNA | Ventus 40 platin 155Wp | ARINNA : Ventus 40 platin 155Wp | -0.346 | 24.88 | 8 | 155 | 20.63 | 7.5
169 | Asola | 150W/40-156P | Asola : 150W/40-156P | -0.37 | 24.6 | 7.9 | 150 | 20 | 7.5
170 | Asola | 155W/40-156M | Asola : 155W/40-156M | -0.37 | 24.4 | 8.27 | 155 | 20 | 7.8
171 | Asola | 175W/48-156P | Asola : 175W/48-156P | -0.37 | 29.18 | 7.83 | 175 | 24.26 | 7.17
172 | Asola | 185W/48-156M | Asola : 185W/48-156M | -0.37 | 28.75 | 8.1 | 185 | 24.5 | 7.5
173 | Asola | 185W/48-156p/2 (180 Wp) | Asola : 185W/48-156p/2 (180 Wp) | -0.33 | 29,52 | 8.05 | 180 | 24 | 7.57
174 | Asola | 185W/48-156p/2 (185 Wp) | Asola : 185W/48-156p/2 (185 Wp) | -0.33 | 29,76 | 8,15 | 185 | 24 | 7,8
175 | Asola | 185W/48-156p/2 (190 Wp) | Asola : 185W/48-156p/2 (190 Wp) | -0.33 | 29,76 | 8.47 | 190 | 24 | 8.02
176 | Asola | 195W/48-156m/2 (190 Wp) | Asola : 195W/48-156m/2 (190 Wp) | -0.33 | 29.63 | 8.28 | 190 | 24.94 | 7.75
177 | Asola | 195W/48-156m/2 (195 Wp) | Asola : 195W/48-156m/2 (195 Wp) | -0.33 | 29.95 | 8.45 | 195 | 24.96 | 7.9
178 | Asola | 195W/48-156m/2 (200 Wp) | Asola : 195W/48-156m/2 (200 Wp) | -0.33 | 30.24 | 8.55 | 200 | 24.96 | 8.1
179 | Asola | 200W/54-156p (200 Wp) | Asola : 200W/54-156p (200 Wp) | -0.33 | 33.16 | 7.92 | 200 | 27 | 7.46
180 | Asola | 200W/54-156p (205 Wp) | Asola : 200W/54-156p (205 Wp) | -0.33 | 33.4 | 8.08 | 205 | 27 | 7.67
181 | Asola | 200W/54-156p (210 Wp) | Asola : 200W/54-156p (210 Wp) | -0.33 | 33.48 | 8.15 | 210 | 27 | 7.8
182 | Asola | 210W/54-156m (210Wp) | Asola : 210W/54-156m (210Wp) | -0.33 | 33.28 | 8.17 | 210 | 27.83 | 7.62
183 | Asola | 210W/54-156m (215 Wp) | Asola : 210W/54-156m (215 Wp) | -0.33 | 33.45 | 8.28 | 215 | 28.08 | 7.75
184 | Asola | 210W/54-156m (220 Wp) | Asola : 210W/54-156m (220 Wp) | -0.33 | 33.7 | 8.45 | 220 | 28.08 | 7.9
185 | Asola | 220W/60-156p/2 (220Wp) | Asola : 220W/60-156p/2 (220Wp) | -0.33 | 36,77 | 7,85 | 220 | 30 | 7,37
186 | Asola | 220W/60-156p/2 (225 Wp) | Asola : 220W/60-156p/2 (225 Wp) | -0.33 | 36,90 | 8,05 | 225 | 30 | 7,57
187 | Asola | 220W/60-156p/2 (230 Wp) | Asola : 220W/60-156p/2 (230 Wp) | -0.33 | 37,11 | 8,08 | 230 | 30 | 7,75
189 | Asola | 230W/60-156P | Asola : 230W/60-156P | -0.37 | 36.6 | 8.6 | 230 | 29 | 7.9
191 | Asola | 245W/60-156m/2 | Asola : 245W/60-156m/2 | -0.36 | 37.44 | 8.45 | 245 | 31.2 | 7.9
192 | Asola | 270W/72-156P | Asola : 270W/72-156P | -0.37 | 44.28 | 8.5 | 270 | 36.14 | 7.53
193 | Asola | 275W/72-156M | Asola : 275W/72-156M | -0.37 | 43.85 | 8.1 | 275 | 36.87 | 7.5
194 | Asola | 290W/72-156m (285Wp) | Asola : 290W/72-156m (285Wp) | -0.36 | 44.45 | 8.26 | 285 | 37.22 | 7.7
195 | Asola | 290W/72-156m (290Wp) | Asola : 290W/72-156m (290Wp) | -0.36 | 44.71 | 8.38 | 290 | 37.44 | 7.83
196 | Asola | 290W/72-156m (295Wp) | Asola : 290W/72-156m (295Wp) | -0.36 | 44.93 | 8.45 | 295 | 37.44 | 7.9
197 | Asola | 290W/72-156m (300Wp) | Asola : 290W/72-156m (300Wp) | -0.36 | 45.36 | 8.55 | 300 | 37.44 | 8.1
198 | AstroPower | AP-110 | AstroPower : AP-110 | -0.429 | 20.7 | 7.5 | 110 | 16.7 | 6.6
199 | AstroPower | AP-1106 | AstroPower : AP-1106 | -0.386 | 20.7 | 7.5 | 110 | 16.7 | 6.6
200 | AstroPower | AP-120 | AstroPower : AP-120 | -0.429 | 21 | 7.7 | 120 | 16.9 | 7.1
201 | AstroPower | AP-1206 | AstroPower : AP-1206 | -0.381 | 21 | 7.7 | 120 | 16.9 | 7.1
202 | AstroPower | AP-140 | AstroPower : AP-140 | -0.476 | 21 | 9.2 | 140 | 17.1 | 8.2
203 | AstroPower | AP-150 | AstroPower : AP-150 | -0.476 | 21 | 9.8 | 150 | 17.1 | 8.8
204 | AstroPower | AP-30 | AstroPower : AP-30 | -0.463 | 21.6 | 2.05 | 30 | 16.7 | 1.8
205 | AstroPower | AP-45 | AstroPower : AP-45 | -0.465 | 21.5 | 3 | 45 | 16.7 | 2.7
206 | AstroPower | AP-50 | AstroPower : AP-50 | -0.465 | 21.5 | 3.3 | 50 | 16.7 | 3
207 | AstroPower | AP-5106 | AstroPower : AP-5106 | -0.387 | 20.7 | 3.8 | 55 | 16.7 | 3.3
208 | AstroPower | AP-6105 | AstroPower : AP-6105 | -0.39 | 20.5 | 4.7 | 65 | 16.3 | 4
209 | AstroPower | AP-6106 | AstroPower : AP-6106 | -0.4 | 21.2 | 3.9 | 60 | 17 | 3.5
210 | AstroPower | AP-65 | AstroPower : AP-65 | -0.439 | 20.5 | 4.7 | 65 | 16.3 | 4
211 | AstroPower | AP-7105 | AstroPower : AP-7105 | -0.381 | 21 | 4.8 | 75 | 17 | 4.4
212 | AstroPower | AP-75 | AstroPower : AP-75 | -0.429 | 21 | 4.8 | 75 | 17 | 4.4
213 | AstroPower | APx-130 | AstroPower : APx-130 | -0.471 | 19.1 | 9.9 | 130 | 15.3 | 8.5
214 | AstroPower | APx-140 | AstroPower : APx-140 | -0.464 | 19.4 | 10.1 | 140 | 15.7 | 8.9
215 | AstroPower | APx-45 | AstroPower : APx-45 | -0.488 | 20.5 | 3.3 | 45 | 16.7 | 2.7
216 | AstroPower | APx-50 | AstroPower : APx-50 | -0.483 | 20.7 | 3.4 | 50 | 16.8 | 3
217 | AstroPower | APx-65 | AstroPower : APx-65 | -0.488 | 20.5 | 4.7 | 65 | 16.3 | 4
218 | AstroPower | APx-75 | AstroPower : APx-75 | -0.476 | 21 | 4.8 | 75 | 17 | 4.4
219 | AstroPower | APX-80 (AP 8225) | AstroPower : APX-80 (AP 8225) | -0.411 | 19.8 | 6.05 | 80 | 16 | 5
220 | AstroPower | APX-90 (AP 9225) | AstroPower : APX-90 (AP 9225) | -0.411 | 21.9 | 5.8 | 90 | 17.3 | 5.2
221 | Atersa | A-10 | Atersa : A-10 | -0.4 | 21 | 0.62 | 10 | 17 | 0.59
222 | Atersa | A-115 | Atersa : A-115 | -0.4 | 20.9 | 7.6 | 115 | 16.8 | 6.9
223 | Atersa | A-120 | Atersa : A-120 | -0.4 | 21 | 7.7 | 120 | 16.9 | 7.1
224 | Atersa | A-130 | Atersa : A-130 | -0.4 | 21.3 | 8.1 | 130 | 17.2 | 7.54
225 | Atersa | A-140 | Atersa : A-140 | -0.4 | 42.9 | 4.7 | 140 | 33.4 | 4.2
226 | Atersa | A-150 | Atersa : A-150 | -0.4 | 43.4 | 4.8 | 150 | 34 | 4.4
227 | Atersa | A-150 | Atersa : A-150 | -0.296 | 43 | 4.8 | 150 | 34 | 4.4
228 | Atersa | A-160 | Atersa : A-160 | -0.296 | 43.9 | 5 | 160 | 35.7 | 4.5
229 | Atersa | A-160/5 | Atersa : A-160/5 | -0.4 | 44.2 | 4.75 | 160 | 36 | 4.45
230 | Atersa | A-170 | Atersa : A-170 | -0.296 | 43.95 | 5.1 | 170 | 35.8 | 4.75
231 | Atersa | A-20 | Atersa : A-20 | -0.4 | 21 | 1.31 | 20 | 17 | 1.18
232 | Atersa | A-214P | Atersa : A-214P | -0.344 | 37 | 7.8 | 214 | 29.48 | 7.26
233 | Atersa | A-222P | Atersa : A-222P | -0.342 | 37.2 | 7.96 | 222 | 29.84 | 7.44
234 | Atersa | A-230P | Atersa : A-230P | -0.34 | 37.4 | 8.12 | 230 | 30.2 | 7.62
235 | Atersa | A-235P | Atersa : A-235P | -0.35 | 37.78 | 8.22 | 235 | 30.39 | 7.73
236 | Atersa | A-238P | Atersa : A-238P | -0.35 | 37.32 | 8.44 | 238 | 29.86 | 7.97
237 | Atersa | A-245M | Atersa : A-245M | -0.35 | 36.48 | 8.43 | 245 | 30.84 | 7.98
238 | Atersa | A-250M | Atersa : A-250M | -0.32 | 37.75 | 8.86 | 250 | 30.39 | 8.23
239 | Atersa | A-270P | Atersa : A-270P | -0.35 | 44.85 | 0.5 | 270 | 35.8 | 7.54
240 | Atersa | A-277P | Atersa : A-277P | -0.35 | 45.32 | 0.5 | 277 | 36.26 | 7.64
241 | Atersa | A-38 | Atersa : A-38 | -0.4 | 21.3 | 2.38 | 38 | 17.2 | 2.2
242 | Atersa | A-5 | Atersa : A-5 | -0.4 | 21 | 0.31 | 5 | 17 | 0.29
243 | Atersa | A-55 | Atersa : A-55 | -0.4 | 19.2 | 3.85 | 55 | 15.5 | 3.55
244 | Atersa | A-60 | Atersa : A-60 | -0.4 | 21 | 3.85 | 60 | 16.9 | 3.55
245 | Atersa | A-75 | Atersa : A-75 | -0.4 | 21 | 4.8 | 75 | 17 | 4.4
246 | Atersa | A-85 | Atersa : A-85 | -0.4 | 21.2 | 5.2 | 85 | 17.3 | 4.9
247 | Atersa | APX-45 | Atersa : APX-45 | -0.4 | 21.9 | 2.9 | 45 | 17.3 | 2.6
248 | Atersa | APX-90 | Atersa : APX-90 | -0.4 | 21.9 | 5.8 | 90 | 17.3 | 5.2
249 | Atlantis | Atlantis-Magog-Sunslates TM | Atlantis : Atlantis-Magog-Sunslates TM | -0.417 | 2.4 | 4.6 | 7.8 | 1.93 | 4.1
250 | Atlantis | Atlantis-Sunslates TM mono | Atlantis : Atlantis-Sunslates TM mono | -0.417 | 3.6 | 4.6 | 11.8 | 2.9 | 4.07
251 | Atlantis | Atlantis-Sunslates TM poly | Atlantis : Atlantis-Sunslates TM poly | -0.417 | 3.6 | 4.6 | 11.8 | 2.9 | 4.07
252 | Atlantis | Atlantis-Sunslates TM poly 13.3Wp | Atlantis : Atlantis-Sunslates TM poly 13.3Wp | -0.417 | 3.91 | 4.84 | 13.3 | 2.93 | 4.54
253 | Avancis | 100 | Avancis : 100 | -0.205 | 56 | 3.1 | 100 | 39.5 | 2.54
254 | Avancis | 110 | Avancis : 110 | -0.205 | 56.6 | 3.11 | 110 | 42.3 | 2.61
255 | Avancis | 120 | Avancis : 120 | -0.205 | 57.4 | 3.13 | 120 | 44.9 | 2.68
256 | Avancis | 130 | Avancis : 130 | -0.205 | 58.1 | 3.19 | 130 | 47.8 | 2.72
257 | Axitec | AC-127P | Axitec : AC-127P | -0.4 | 33.23 | 4.9 | 127 | 27.8 | 4.57
258 | Axitec | AC-150M/12 | Axitec : AC-150M/12 | -0.38 | 21 | 9.2 | 150 | 17 | 8.8
259 | Axitec | AC-150M/24 | Axitec : AC-150M/24 | -0.38 | 42 | 4.8 | 150 | 34 | 4.4
260 | Axitec | AC-160P | Axitec : AC-160P | -0.4 | 21.3 | 9.5 | 160 | 17.28 | 9.26
261 | Axitec | AC-167P/12 | Axitec : AC-167P/12 | -0.4 | 21.75 | 9.8 | 167 | 18.2 | 9.2
262 | Axitec | AC-167P/24 | Axitec : AC-167P/24 | -0.4 | 43.5 | 4.9 | 167 | 36.4 | 4.6
263 | Axitec | AC-172P (12V) | Axitec : AC-172P (12V) | -0.33 | 22.5 | 9.98 | 172 | 18.42 | 9.34
264 | Axitec | AC-172P (24V) | Axitec : AC-172P (24V) | -0.33 | 45 | 4.99 | 172 | 36.84 | 4.67
265 | Axitec | AC-185 | Axitec : AC-185 | -0.4 | 24.17 | 9.8 | 185 | 20.2 | 9.2
266 | Axitec | AC-190P (14V) | Axitec : AC-190P (14V) | -0.35 | 25 | 9.98 | 190 | 20.4 | 9.34
267 | Axitec | AC-190P (28V) | Axitec : AC-190P (28V) | -0.35 | 50 | 4.99 | 190 | 40.8 | 4.67
268 | Axitec | AC-217P 217Wp | Axitec : AC-217P 217Wp | -0.33 | 58.94 | 4.75 | 217 | 48 | 4.53
269 | Axitec | AC-222 P/32S 222Wp | Axitec : AC-222 P/32S 222Wp | -0.33 | 58.54 | 5.2 | 222 | 46.95 | 4.73
270 | Axitec | AC-222P 222Wp | Axitec : AC-222P 222Wp | -0.33 | 58.94 | 4.8 | 222 | 48.3 | 4.6
271 | Axitec | AC-227 P/32S 227Wp | Axitec : AC-227 P/32S 227Wp | -0.33 | 58.95 | 5.25 | 227 | 47 | 4.88
272 | Axitec | AC-232 P/32S 232Wp | Axitec : AC-232 P/32S 232Wp | -0.33 | 59.25 | 5.3 | 232 | 47.05 | 4.83
273 | Azur Solar | AZUR M 175 | Azur Solar : AZUR M 175 | -0.35 | 44.4 | 5.4 | 175 | 35.4 | 4.95
274 | Azur Solar | AZUR M 180 | Azur Solar : AZUR M 180 | -0.35 | 30 | 8.37 | 180 | 23.7 | 7.6
275 | Azur Solar | AZUR M 185 | Azur Solar : AZUR M 185 | -0.34 | 44.9 | 5.75 | 185 | 36.21 | 5.11
276 | Azur Solar | AZUR P 100 | Azur Solar : AZUR P 100 | -0.38 | 47 | 2.6 | 100 | 41 | 2.4
277 | Azur Solar | AZUR P 120 | Azur Solar : AZUR P 120 | -0.38 | 21.3 | 7.9 | 120 | 17.2 | 6.9
278 | Azur Solar | AZUR P 160 | Azur Solar : AZUR P 160 | -0.37 | 28.4 | 7.82 | 160 | 22.8 | 7.02
279 | Azur Solar | AZUR P 165 | Azur Solar : AZUR P 165 | -0.36 | 43.1 | 5.46 | 165 | 34.6 | 4.77
280 | Azur Solar | AZUR P 180/6+ | Azur Solar : AZUR P 180/6+ | -0.36 | 30.7 | 7.8 | 180 | 25.2 | 7.15
281 | Azur Solar | AZUR P 220/6+ | Azur Solar : AZUR P 220/6+ | -0.36 | 37.8 | 7.9 | 220 | 30.5 | 7.2
282 | Azur Solar | P 165U-3 | Azur Solar : P 165U-3 | -0.36 | 28.89 | 7.85 | 165 | 22.47 | 7.34
283 | Azur Solar | P 170U-3 | Azur Solar : P 170U-3 | -0.36 | 29 | 7.9 | 170 | 22.97 | 7.4
284 | Azur Solar | P 175U-3 | Azur Solar : P 175U-3 | -0.36 | 29.18 | 7.95 | 175 | 23.58 | 7.42
285 | Azur Solar | P 180U-3 | Azur Solar : P 180U-3 | -0.36 | 29.47 | 8 | 180 | 24.09 | 7.47
286 | Azur Solar | P160-3 | Azur Solar : P160-3 | -0.33 | 42.3 | 5.1 | 160 | 33.17 | 4.82
287 | Azur Solar | P165-3 | Azur Solar : P165-3 | -0.33 | 42.7 | 5.25 | 165 | 33.7 | 4.89
288 | Azur Solar | P170-3 | Azur Solar : P170-3 | -0.33 | 43.1 | 5.31 | 170 | 34.3 | 4.95
289 | Bangkok Solar | BS-40 | Bangkok Solar : BS-40 | -0.32 | 62.2 | 1.14 | 40 | 44.8 | 0.93
290 | Bangkok Solar | BS-42-A | Bangkok Solar : BS-42-A | -0.32 | 62.4 | 1.16 | 42 | 45.8 | 0.96
291 | Bangkok Solar | BS-44 | Bangkok Solar : BS-44 | -0.32 | 62.6 | 1.17 | 44 | 46.9 | 0.99
292 | Bangkok Solar | BS-44-B | Bangkok Solar : BS-44-B | -0.32 | 62.6 | 1.17 | 44 | 46.9 | 0.99
293 | Bangkok Solar | BS-46 | Bangkok Solar : BS-46 | -0.32 | 93 | 0.82 | 46 | 70.3 | 0.66
294 | Bangkok Solar | BS-50 | Bangkok Solar : BS-50 | -0.32 | 93.4 | 0.86 | 50 | 70.9 | 0.71
295 | Bangkok Solar | BS-52 | Bangkok Solar : BS-52 | -0.32 | 93.6 | 0.88 | 52 | 71.2 | 0.74
296 | Bangkok Solar | NPVT-42B 42,5Wp | Bangkok Solar : NPVT-42B 42,5Wp | -0.37 | 62.2 | 1.16 | 42.5 | 44.8 | 0.95
297 | Bharat | Mono Crystalline 10 W | Bharat : Mono Crystalline 10 W | -0.4 | 21.3 | 0.77 | 11 | 17 | 0.67
298 | Bharat | Mono Crystalline 37 W | Bharat : Mono Crystalline 37 W | -0.4 | 21.5 | 2.5 | 37 | 17 | 2.3
299 | Bharat | Mono Crystalline 72 W | Bharat : Mono Crystalline 72 W | -0.4 | 21.5 | 4.5 | 72 | 17 | 4.1
300 | BHEL | L1210 | BHEL : L1210 | -0.371 | 21 | 0.75 | 10 | 16.4 | 0.61
301 | BHEL | L1235 | BHEL : L1235 | -0.371 | 21 | 2.5 | 37 | 16.4 | 2.26
302 | BHEL | L1270 | BHEL : L1270 | -0.371 | 21 | 4.6 | 75 | 17 | 4.41
303 | BIC | GP 120 | BIC : GP 120 | -0.381 | 21 | 7.7 | 120 | 16.9 | 7.1
304 | BIC | GP 60 | BIC : GP 60 | -0.381 | 21 | 3.85 | 60 | 16.9 | 3.55
305 | BIC | GP 75 | BIC : GP 75 | -0.381 | 21 | 4.8 | 75 | 17 | 4.4
306 | Biosol | Uni Pro 124 | Biosol : Uni Pro 124 | -0.38 | 42 | 5.1 | 124 | 30 | 4.1
307 | Biosol | Uni Pro 127 | Biosol : Uni Pro 127 | -0.38 | 42.2 | 5.2 | 127 | 30.2 | 4.2
308 | BISOL | 210Wp | BISOL : 210Wp | -0.33 | 36.5 | 8.15 | 210 | 28.2 | 7.45
309 | BISOL | 215Wp | BISOL : 215Wp | -0.33 | 36.6 | 8.2 | 215 | 28.5 | 7.55
310 | BISOL | 218Wp | BISOL : 218Wp | -0.33 | 36.7 | 8.25 | 218 | 28.7 | 7.6
311 | BISOL | 221Wp | BISOL : 221Wp | -0.33 | 36.8 | 8.3 | 221 | 28.7 | 7.7
312 | BISOL | 224Wp | BISOL : 224Wp | -0.33 | 36.8 | 8.35 | 224 | 28.9 | 7.75
313 | Bisol | BMU-214 | Bisol : BMU-214 | -0.35 | 36.4 | 8.15 | 214 | 28.5 | 7.5
314 | BISOL | BMU-215-2/210 | BISOL : BMU-215-2/210 | -0.329 | 36.5 | 8.15 | 210 | 28.2 | 7.45
315 | BISOL | BMU-215-2/213 | BISOL : BMU-215-2/213 | -0.328 | 36.6 | 8.15 | 213 | 28.4 | 7.5
316 | BISOL | BMU-215-2/215 | BISOL : BMU-215-2/215 | -0.327 | 36.6 | 8.2 | 215 | 28.5 | 7.55
317 | BISOL | BMU-215-2/218 | BISOL : BMU-215-2/218 | -0.326 | 36.7 | 8.25 | 218 | 28.7 | 7.6
318 | BISOL | BMU-215-2/221 | BISOL : BMU-215-2/221 | -0.326 | 36.8 | 8.3 | 221 | 28.7 | 7.7
319 | BISOL | BMU-215-2/224 | BISOL : BMU-215-2/224 | -0.325 | 36.8 | 8.35 | 224 | 28.9 | 7.75
320 | BISOL | BMU-215-2/227 | BISOL : BMU-215-2/227 | -0.324 | 36.9 | 8.4 | 227 | 29.1 | 7.8
321 | BISOL | BMU-215-2/233 | BISOL : BMU-215-2/233 | -0.324 | 37 | 8.5 | 233 | 29.3 | 7.95
322 | Bisol | BMU-224 | Bisol : BMU-224 | -0.35 | 37 | 8.3 | 244 | 29 | 7.7
323 | Bisol | BMU-227 | Bisol : BMU-227 | -0.35 | 37.1 | 8.35 | 227 | 29.2 | 7.8
324 | Bisol | BMU-233 | Bisol : BMU-233 | -0.35 | 37.5 | 8.45 | 233 | 29.5 | 7.9
325 | Bisol | BMU-239 | Bisol : BMU-239 | -0.35 | 37.8 | 8.56 | 239 | 29.8 | 8
326 | Bisol | BMU-245 | Bisol : BMU-245 | -0.35 | 38.1 | 8.65 | 245 | 30.2 | 8.15
327 | BlueSun Systems | Blue Sun PT | BlueSun Systems : Blue Sun PT | -0.347 | 21.6 | 1.6 | 4.55 | 1.5 | 3.1
328 | BlueSun Systems | Extra Power 55 | BlueSun Systems : Extra Power 55 | -0.347 | 21.6 | 3.33 | 55 | 17.7 | 3.1
329 | BMC | clay 2000 tec | BMC : clay 2000 tec | -0.356 | 1.8 | 3.17 | 4.55 | 1.5 | 3.03
330 | Bosch Solar Energy | a-Si plus 75 | Bosch Solar Energy : a-Si plus 75 | -0.28 | 137 | 1.1 | 75 | 93 | 0.81
331 | Bosch Solar Energy | a-Si plus 80 | Bosch Solar Energy : a-Si plus 80 | -0.28 | 139 | 1.11 | 80 | 95 | 0.85
332 | Bosch Solar Energy | a-Si plus 85 | Bosch Solar Energy : a-Si plus 85 | -0.28 | 141 | 1.12 | 85 | 97 | 0.88
333 | Bosch Solar Energy | a-Si plus 90 | Bosch Solar Energy : a-Si plus 90 | -0.28 | 143 | 1.13 | 90 | 99 | 0.9
334 | Bosch Solar Energy | M220 3BB | Bosch Solar Energy : M220 3BB | -0.36 | 36 | 8.1 | 220 | 29.4 | 7.55
335 | Bosch Solar Energy | M225 3BB | Bosch Solar Energy : M225 3BB | -0.36 | 36.2 | 8.2 | 225 | 29.6 | 7.65
336 | Bosch Solar Energy | M230 3BB | Bosch Solar Energy : M230 3BB | -0.36 | 36.4 | 8.3 | 230 | 29.8 | 7.75
337 | Bosch Solar Energy | M235 3BB | Bosch Solar Energy : M235 3BB | -0.36 | 36.6 | 8.4 | 235 | 30 | 7.85
338 | Bosch Solar Energy | M240 3BB | Bosch Solar Energy : M240 3BB | -0.36 | 36.8 | 8.5 | 240 | 30.2 | 7.95
339 | Bosch Solar Energy | μm-Si 100 | Bosch Solar Energy : μm-Si 100 | -0.31 | 129 | 1.34 | 100 | 98 | 1.02
340 | Bosch Solar Energy | μm-Si 105 | Bosch Solar Energy : μm-Si 105 | -0.31 | 131 | 1.37 | 105 | 100 | 1.05
341 | Bosch Solar Energy | μm-Si 110 | Bosch Solar Energy : μm-Si 110 | -0.31 | 133 | 1.4 | 110 | 102 | 1.08
342 | Bosch Solar Energy | μm-Si 115 | Bosch Solar Energy : μm-Si 115 | -0.31 | 135 | 1.44 | 115 | 104 | 1.11
343 | BP Solar | 3160Q | BP Solar : 3160Q | -0.36 | 30.2 | 7.34 | 160 | 23.8 | 6.72
344 | BP Solar | 4180 T | BP Solar : 4180 T | -0.36 | 43.6 | 5.58 | 180 | 35.8 | 5.03
345 | BP Solar | BP 2140 L | BP Solar : BP 2140 L | -0.402 | 42.8 | 4.48 | 140 | 34 | 4.16
346 | BP Solar | BP 2140 S | BP Solar : BP 2140 S | -0.402 | 42.8 | 4.48 | 140 | 34 | 4.16
347 | BP Solar | BP 2150 L | BP Solar : BP 2150 L | -0.402 | 42.8 | 4.48 | 150 | 34 | 4.16
348 | BP Solar | BP 2150 S | BP Solar : BP 2150 S | -0.402 | 42.8 | 4.48 | 150 | 34 | 4.16
349 | BP Solar | BP 245/1 | BP Solar : BP 245/1 | -0.41 | 21 | 3 | 45 | 17 | 2.6
350 | BP Solar | BP 245/2 | BP Solar : BP 245/2 | -0.41 | 21 | 3 | 45 | 17 | 2.6
351 | BP Solar | BP 250/1 od, /2 | BP Solar : BP 250/1 od, /2 | -0.406 | 21.2 | 3.22 | 50 | 17.3 | 2.94
352 | BP Solar | BP 270 F | BP Solar : BP 270 F | -0.374 | 21.4 | 4.75 | 70 | 17 | 4.45
353 | BP Solar | BP 270 L | BP Solar : BP 270 L | -0.402 | 21.4 | 4.48 | 70 | 17 | 4.16
354 | BP Solar | BP 270 U | BP Solar : BP 270 U | -0.374 | 21.4 | 4.75 | 70 | 17 | 4.45
355 | BP Solar | BP 275 F | BP Solar : BP 275 F | -0.374 | 21.4 | 4.75 | 75 | 17 | 4.45
356 | BP Solar | BP 275 L | BP Solar : BP 275 L | -0.402 | 21.4 | 4.75 | 75 | 17 | 4.45
357 | BP Solar | BP 275 U | BP Solar : BP 275 U | -0.374 | 21.4 | 4.75 | 75 | 17 | 4.45
358 | BP Solar | BP 3150 L | BP Solar : BP 3150 L | -0.368 | 43.5 | 4.75 | 150 | 34.5 | 4.35
359 | BP Solar | BP 3150 S | BP Solar : BP 3150 S | -0.368 | 43.5 | 4.75 | 150 | 34.5 | 4.35
360 | BP Solar | BP 3160 L | BP Solar : BP 3160 L | -0.362 | 44.2 | 4.8 | 160 | 35.1 | 4.55
361 | BP Solar | BP 3160 S | BP Solar : BP 3160 S | -0.362 | 44.2 | 4.8 | 160 | 35.1 | 4.55
362 | BP Solar | BP 3160X L | BP Solar : BP 3160X L | -0.362 | 44.2 | 4.8 | 160 | 35.1 | 4.55
363 | BP Solar | BP 3160X S | BP Solar : BP 3160X S | -0.362 | 44.2 | 4.8 | 160 | 35.1 | 4.55
364 | BP Solar | BP 3165 165Wp | BP Solar : BP 3165 165Wp | -0.362 | 44.2 | 5.1 | 165 | 35.2 | 4.7
365 | BP Solar | BP 3170 | BP Solar : BP 3170 | -0.362 | 44.2 | 5.2 | 170 | 35.5 | 4.8
366 | BP Solar | BP 375 H | BP Solar : BP 375 H | -0.367 | 21.8 | 4.75 | 75 | 17.3 | 4.35
367 | BP Solar | BP 375 S | BP Solar : BP 375 S | -0.367 | 21.8 | 4.75 | 75 | 17.3 | 4.35
368 | BP Solar | BP 375 U | BP Solar : BP 375 U | -0.367 | 21.8 | 4.75 | 75 | 17.3 | 4.35
369 | BP Solar | BP 380 H | BP Solar : BP 380 H | -0.362 | 22.1 | 4.8 | 80 | 17.6 | 4.55
370 | BP Solar | BP 380 S | BP Solar : BP 380 S | -0.362 | 22.1 | 4.8 | 80 | 17.6 | 4.55
371 | BP Solar | BP 380 U | BP Solar : BP 380 U | -0.362 | 22.1 | 4.8 | 80 | 17.6 | 4.55
372 | BP Solar | BP 380X L | BP Solar : BP 380X L | -0.362 | 22.1 | 4.8 | 80 | 17.6 | 4.55
373 | BP Solar | BP 380X S,U | BP Solar : BP 380X S,U | -0.362 | 22.1 | 4.8 | 80 | 17.6 | 4.55
374 | BP Solar | BP 4150 L | BP Solar : BP 4150 L | -0.367 | 43.6 | 4.75 | 150 | 34.8 | 4.33
375 | BP Solar | BP 4150 S | BP Solar : BP 4150 S | -0.367 | 43.6 | 4.75 | 150 | 34.8 | 4.33
376 | BP Solar | BP 4160 L | BP Solar : BP 4160 L | -0.362 | 44.2 | 4.9 | 160 | 35.4 | 4.52
377 | BP Solar | BP 4160 S | BP Solar : BP 4160 S | -0.362 | 44.2 | 4.9 | 160 | 35.4 | 4.52
378 | BP Solar | BP 475 H | BP Solar : BP 475 H | -0.367 | 21.8 | 4.75 | 75 | 17.4 | 4.33
379 | BP Solar | BP 475 S | BP Solar : BP 475 S | -0.367 | 21.8 | 4.75 | 75 | 17.4 | 4.33
380 | BP Solar | BP 475 U | BP Solar : BP 475 U | -0.367 | 21.8 | 4.75 | 75 | 17.4 | 4.33
381 | BP Solar | BP 480 H | BP Solar : BP 480 H | -0.362 | 22.1 | 4.8 | 80 | 17.7 | 4.52
382 | BP Solar | BP 480 S | BP Solar : BP 480 S | -0.362 | 22.1 | 4.8 | 80 | 17.7 | 4.52
383 | BP Solar | BP 480 U | BP Solar : BP 480 U | -0.362 | 22.1 | 4.8 | 80 | 17.7 | 4.52
384 | BP Solar | BP 5130 F | BP Solar : BP 5130 F | -0.397 | 36 | 4.8 | 130 | 30 | 4.3
385 | BP Solar | BP 5130 L | BP Solar : BP 5130 L | -0.4 | 36.3 | 4.8 | 133 | 29.8 | 4.5
386 | BP Solar | BP 5140 F | BP Solar : BP 5140 F | -0.397 | 36 | 5 | 140 | 30 | 4.6
387 | BP Solar | BP 5140 L | BP Solar : BP 5140 L | -0.397 | 36 | 5 | 140 | 30 | 4.6
388 | BP Solar | BP 5160 L | BP Solar : BP 5160 L | -0.391 | 44 | 4.8 | 160 | 36 | 4.4
389 | BP Solar | BP 5160 S | BP Solar : BP 5160 S | -0.391 | 44 | 4.8 | 160 | 36 | 4.4
390 | BP Solar | BP 5170 L | BP Solar : BP 5170 L | -0.391 | 44 | 5 | 170 | 36 | 4.7
391 | BP Solar | BP 5170 S | BP Solar : BP 5170 S | -0.362 | 44 | 5 | 170 | 36 | 4.7
392 | BP Solar | BP 555/1 od, /2 | BP Solar : BP 555/1 od, /2 | -0.391 | 22 | 3.2 | 55 | 18 | 3
393 | BP Solar | BP 580 F | BP Solar : BP 580 F | -0.364 | 22 | 4.7 | 80 | 18 | 4.44
394 | BP Solar | BP 580 L | BP Solar : BP 580 L | -0.364 | 22 | 4.7 | 80 | 18 | 4.44
395 | BP Solar | BP 580 S | BP Solar : BP 580 S | -0.364 | 22 | 4.7 | 80 | 18 | 4.44
396 | BP Solar | BP 580 U | BP Solar : BP 580 U | -0.364 | 22 | 4.7 | 80 | 18 | 4.44
397 | BP Solar | BP 580 W | BP Solar : BP 580 W | -0.364 | 22 | 4.7 | 80 | 18 | 4.44
398 | BP Solar | BP 585 | BP Solar : BP 585 | -0.362 | 22.1 | 5 | 85 | 18 | 4.72
399 | BP Solar | BP 585 F | BP Solar : BP 585 F | -0.362 | 22.1 | 5 | 85 | 18 | 4.72
400 | BP Solar | BP 585 L | BP Solar : BP 585 L | -0.362 | 22.1 | 5 | 85 | 18 | 4.72
401 | BP Solar | BP 585 S | BP Solar : BP 585 S | -0.362 | 22.1 | 5 | 85 | 18 | 4.72
402 | BP Solar | BP 585 U | BP Solar : BP 585 U | -0.362 | 22.1 | 5 | 85 | 18 | 4.72
403 | BP Solar | BP 585 W | BP Solar : BP 585 W | -0.362 | 22.1 | 5 | 85 | 18 | 4.72
404 | BP Solar | BP 7185 185Wp | BP Solar : BP 7185 185Wp | -0.357 | 44.8 | 5.5 | 185 | 36.5 | 5.1
405 | BP Solar | BP 7190 | BP Solar : BP 7190 | -0.357 | 44.8 | 5.5 | 190 | 36.6 | 5.2
406 | BP Solar | BP Apollo 980 | BP Solar : BP Apollo 980 | -0.332 | 45.2 | 3 | 80 | 32.3 | 2.48
407 | BP Solar | GSX 116 U | BP Solar : GSX 116 U | -0.384 | 41.7 | 5.07 | 116 | 33.4 | 4.68
408 | BP Solar | GSX 156 U | BP Solar : GSX 156 U | -0.384 | 41.7 | 3.8 | 156 | 33.4 | 3.48
409 | BP Solar | Millenia MST 50 LV | BP Solar : Millenia MST 50 LV | -0.269 | 23.3 | 3.65 | 50 | 17.6 | 2.81
410 | BP Solar | Millenia MST 50 MV | BP Solar : Millenia MST 50 MV | -0.272 | 102 | 0.85 | 50 | 77 | 0.65
411 | BP Solar | Millenia MST 50 MV L | BP Solar : Millenia MST 50 MV L | -0.272 | 102 | 0.85 | 50 | 77 | 0.65
412 | BP Solar | Millenia MST 56 MV | BP Solar : Millenia MST 56 MV | -0.4 | 102 | 0.87 | 56 | 73 | 0.76
413 | BP Solar | Millenia MST-43-LV | BP Solar : Millenia MST-43-LV | -0.27 | 22.3 | 3.3 | 43 | 16.7 | 2.6
414 | BP Solar | Millenia MST-43-LV L | BP Solar : Millenia MST-43-LV L | -0.305 | 24.6 | 3.3 | 43 | 17.2 | 2.5
415 | BP Solar | Millenia MST-43-MV | BP Solar : Millenia MST-43-MV | -0.264 | 98 | 0.84 | 43 | 73 | 0.59
416 | BP Solar | Millenia MST-43-MV L | BP Solar : Millenia MST-43-MV L | -0.264 | 98 | 0.84 | 43 | 70.5 | 0.61
417 | BP Solar | MSX 120, 12 V | BP Solar : MSX 120, 12 V | -0.379 | 21.1 | 7.74 | 120 | 16.9 | 7.12
418 | BP Solar | MSX 120, 12 V Lam | BP Solar : MSX 120, 12 V Lam | -0.379 | 21.1 | 7.74 | 120 | 16.9 | 7.12
419 | BP Solar | MSX 120, 24 V | BP Solar : MSX 120, 24 V | -0.38 | 42.1 | 3.87 | 120 | 33.7 | 3.56
420 | BP Solar | MSX 120, 24 V Lam | BP Solar : MSX 120, 24 V Lam | -0.38 | 42.1 | 3.87 | 120 | 33.7 | 3.56
421 | BP Solar | MSX 240 | BP Solar : MSX 240 | -0.376 | 85.2 | 3.8 | 240 | 68.4 | 3.5
422 | BP Solar | MSX 56 | BP Solar : MSX 56 | -0.385 | 20.8 | 3.6 | 56 | 16.8 | 3.35
423 | BP Solar | MSX 60 | BP Solar : MSX 60 | -0.381 | 21 | 3.87 | 60 | 16.8 | 3.56
424 | BP Solar | MSX 60 U | BP Solar : MSX 60 U | -0.381 | 21 | 5.17 | 60 | 16.8 | 4.75
425 | BP Solar | MSX 64 | BP Solar : MSX 64 | -0.376 | 21.3 | 4 | 64 | 17.5 | 3.66
426 | BP Solar | MSX 77 | BP Solar : MSX 77 | -0.381 | 21 | 5 | 77 | 16.9 | 4.56
427 | BP Solar | MSX 80 | BP Solar : MSX 80 | -0.381 | 21 | 5 | 80 | 16.9 | 4.56
428 | BP Solar | MSX 83 | BP Solar : MSX 83 | -0.377 | 21.2 | 5.27 | 83 | 17.1 | 4.85
429 | BP Solar | Poly3 serie- BP 3230N | BP Solar : Poly3 serie- BP 3230N | -0.36 | 36.4 | 8.7 | 230 | 29.2 | 7.9
430 | BP Solar | SX 110 S, 12 v | BP Solar : SX 110 S, 12 v | -0.38 | 42.1 | 3.87 | 120 | 16.8 | 3.56
431 | BP Solar | SX 110 U, 24v | BP Solar : SX 110 U, 24v | -0.38 | 42.1 | 3.87 | 120 | 32.8 | 3.56
432 | BP Solar | SX 120 S, 12 v | BP Solar : SX 120 S, 12 v | -0.38 | 42.1 | 3.87 | 120 | 16.8 | 3.56
433 | BP Solar | SX 120 U, 24v | BP Solar : SX 120 U, 24v | -0.38 | 42.1 | 3.87 | 120 | 32.8 | 3.56
434 | BP Solar | SX 140 L | BP Solar : SX 140 L | -0.374 | 42.8 | 4.5 | 140 | 34 | 4.11
435 | BP Solar | SX 140 S | BP Solar : SX 140 S | -0.374 | 42.8 | 4.5 | 140 | 34 | 4.11
436 | BP Solar | SX 150 L | BP Solar : SX 150 L | -0.368 | 43.5 | 4.75 | 150 | 34.5 | 4.35
437 | BP Solar | SX 150 S | BP Solar : SX 150 S | -0.368 | 43.5 | 4.75 | 150 | 34.5 | 4.35
438 | BP Solar | SX 40 M | BP Solar : SX 40 M | -0.381 | 21 | 2.58 | 40 | 16.8 | 2.37
439 | BP Solar | SX 40 U | BP Solar : SX 40 U | -0.381 | 21 | 2.58 | 40 | 16.8 | 2.37
440 | BP Solar | SX 50 M | BP Solar : SX 50 M | -0.381 | 21 | 3.23 | 50 | 16.8 | 2.97
441 | BP Solar | SX 50 U | BP Solar : SX 50 U | -0.381 | 21 | 3.23 | 50 | 16.8 | 2.97
442 | BP Solar | SX 55 U | BP Solar : SX 55 U | -0.381 | 21 | 5.17 | 55 | 16.8 | 4.75
443 | BP Solar | SX 60 U | BP Solar : SX 60 U | -0.381 | 21 | 5.17 | 60 | 16.8 | 4.75
444 | BP Solar | SX 65 U | BP Solar : SX 65 U | -0.372 | 21.5 | 4.06 | 65 | 17.2 | 3.77
445 | BP Solar | SX 70T U | BP Solar : SX 70T U | -0.374 | 21.4 | 4.5 | 70 | 17 | 4.11
446 | BP Solar | SX 75 U | BP Solar : SX 75 U | -0.381 | 21 | 5.17 | 75 | 16.8 | 4.75
447 | BP Solar | SX 75T U | BP Solar : SX 75T U | -0.367 | 21.8 | 4.75 | 75 | 17.3 | 4.35
448 | BP Solar | SX 80 U | BP Solar : SX 80 U | -0.381 | 21 | 5.17 | 80 | 16.8 | 4.75
449 | BP Solar | SX 85 U | BP Solar : SX 85 U | -0.376 | 21.3 | 5.3 | 85 | 17.1 | 4.97
450 | BP Solar | VLX-53 | BP Solar : VLX-53 | -0.343 | 21.3 | 3.33 | 53 | 17.2 | 3.08
451 | Braas | SRT 35 | Braas : SRT 35 | -0.355 | 10.7 | 4.5 | 35 | 8.5 | 4.15
452 | Braas | SRT 80 | Braas : SRT 80 | -0.355 | 22.1 | 4.8 | 80 | 17.6 | 4.55
453 | Buderus | Logasol PV 250 | Buderus : Logasol PV 250 | -0.33 | 77.5 | 4.46 | 260 | 64 | 4.1
454 | Canadian Solar | 190M | Canadian Solar : 190M | -0.35 | 44.8 | 5.52 | 190 | 36.6 | 5.19
455 | Canadian Solar | CS5A-160 | Canadian Solar : CS5A-160 | -0.35 | 43.6 | 4.97 | 160 | 34.9 | 4.58
456 | Canadian Solar | CS5A-170 | Canadian Solar : CS5A-170 | -0.35 | 44.1 | 5.19 | 170 | 35.5 | 4.79
457 | Canadian Solar | CS5A-180 | Canadian Solar : CS5A-180 | -0.35 | 44.5 | 5.4 | 180 | 36.1 | 4.99
458 | Canadian Solar | CS5B-145 | Canadian Solar : CS5B-145 | -0.364 | 42 | 4.7 | 140.1 | 33.6 | 4.32
459 | Canadian Solar | CS5B-150 | Canadian Solar : CS5B-150 | -0.364 | 42 | 4.95 | 145 | 33.6 | 4.47
460 | Canadian Solar | CS5B-155 | Canadian Solar : CS5B-155 | -0.364 | 42 | 5.11 | 150.1 | 33.6 | 4.61
461 | Canadian Solar | CS5B-160 | Canadian Solar : CS5B-160 | -0.364 | 42 | 5.27 | 155.1 | 33.6 | 4.77
462 | Canadian Solar | CS5B-165 | Canadian Solar : CS5B-165 | -0.364 | 42 | 5.34 | 160.1 | 33.6 | 4.92
463 | Canadian Solar | CS5B-170 | Canadian Solar : CS5B-170 | -0.364 | 42 | 5.5 | 165.1 | 33.6 | 5.06
464 | Canadian Solar | CS5P-200 | Canadian Solar : CS5P-200 | -0.35 | 57.4 | 4.78 | 200 | 46.4 | 4.31
465 | Canadian Solar | CS5P-210 | Canadian Solar : CS5P-210 | -0.35 | 57.9 | 4.94 | 210 | 46.6 | 4.51
466 | Canadian Solar | CS5P-220 | Canadian Solar : CS5P-220 | -0.35 | 58.4 | 5.1 | 220 | 46.9 | 4.69
467 | Canadian Solar | CS5P-230 | Canadian Solar : CS5P-230 | -0.35 | 58.8 | 5.25 | 230 | 47.5 | 4.84
468 | Canadian Solar | CS5P-240 | Canadian Solar : CS5P-240 | -0.35 | 59.3 | 5.4 | 240 | 48.1 | 4.99
469 | Canadian Solar | CS6A-150 | Canadian Solar : CS6A-150 | -0.35 | 28.8 | 7.12 | 150 | 23.1 | 6.5
470 | Canadian Solar | CS6A-160 | Canadian Solar : CS6A-160 | -0.35 | 28.9 | 7.51 | 160 | 23.1 | 6.92
471 | Canadian Solar | CS6A-170 | Canadian Solar : CS6A-170 | -0.35 | 29.2 | 7.85 | 170 | 23.2 | 7.33
472 | Canadian Solar | CS6A-180 | Canadian Solar : CS6A-180 | -0.35 | 29.4 | 8.2 | 180 | 23.6 | 7.62
473 | Canadian Solar | CS6P-170 | Canadian Solar : CS6P-170 | -0.35 | 35.8 | 6.62 | 170 | 28.7 | 5.93
474 | Canadian Solar | CS6P-180 | Canadian Solar : CS6P-180 | -0.35 | 35.9 | 6.98 | 180 | 28.7 | 6.26
475 | Canadian Solar | CS6P-190 | Canadian Solar : CS6P-190 | -0.35 | 36 | 7.33 | 190 | 28.8 | 6.6
476 | Canadian Solar | CS6P-200 | Canadian Solar : CS6P-200 | -0.35 | 36.2 | 7.68 | 200 | 28.9 | 6.93
477 | Canadian Solar | CS6P-210 | Canadian Solar : CS6P-210 | -0.35 | 36.4 | 7.91 | 210 | 28.9 | 7.26
478 | Canadian Solar | CS6P-220 | Canadian Solar : CS6P-220 | -0.35 | 36.6 | 8.09 | 220 | 29.3 | 7.52
479 | Canadian Solar | CS6P-225 | Canadian Solar : CS6P-225 | -0.34 | 37 | 8.07 | 225 | 29.7 | 7.58
480 | Canadian Solar | CS6P-230 | Canadian Solar : CS6P-230 | -0.35 | 36.8 | 8.34 | 230 | 29.8 | 7.71
481 | Canadian Solar | CS6P-235 | Canadian Solar : CS6P-235 | -0.34 | 37.2 | 8.34 | 235 | 30.1 | 7.82
482 | Canadian Solar | CS6P-240 | Canadian Solar : CS6P-240 | -0.35 | 37 | 8.61 | 240 | 30.4 | 7.91
483 | Canadian Solar | CS6P-245 | Canadian Solar : CS6P-245 | -0.34 | 37.4 | 8.61 | 245 | 30.3 | 8.09
484 | Canadian Solar | CS6P-250 | Canadian Solar : CS6P-250 | -0.34 | 37.5 | 8.74 | 250 | 30.4 | 8.22
485 | CellSolar | CS 110 M | CellSolar : CS 110 M | -0.39 | 42 | 3.4 | 110 | 35.2 | 3.25
486 | CellSolar | CS 160 P | CellSolar : CS 160 P | -0.39 | 44 | 5 | 160 | 35.5 | 4.5
487 | CellSolar | CS 165 P | CellSolar : CS 165 P | -0.39 | 44 | 5 | 165 | 35.5 | 4.65
488 | CellSolar | CS 170P | CellSolar : CS 170P | -0.39 | 44 | 5 | 170 | 35.5 | 4.8
489 | Centennial Solar | CS125 | Centennial Solar : CS125 | -0.33 | 22 | 7.6 | 125 | 17.4 | 7.18
490 | Centennial Solar | CS125D | Centennial Solar : CS125D | -0.33 | 44 | 7.6 | 250 | 34.8 | 7.18
491 | Centennial Solar | CS130 | Centennial Solar : CS130 | -0.33 | 22 | 8 | 130 | 17.6 | 7.39
492 | Centennial Solar | CS130D | Centennial Solar : CS130D | -0.33 | 44 | 8 | 260 | 35.2 | 7.39
493 | Centennial Solar | CS135 | Centennial Solar : CS135 | -0.33 | 22 | 8.1 | 135 | 17.9 | 7.54
494 | Centennial Solar | CS135D | Centennial Solar : CS135D | -0.33 | 44 | 8.1 | 270 | 35.8 | 7.54
495 | Centennial Solar | CS140 | Centennial Solar : CS140 | -0.33 | 22 | 8.4 | 140 | 17.9 | 7.82
496 | Centennial Solar | CS230 | Centennial Solar : CS230 | -0.33 | 22 | 13.97 | 230 | 17.4 | 13.2
497 | Centennial Solar | CS240 | Centennial Solar : CS240 | -0.33 | 22 | 14.7 | 240 | 17.6 | 13.6
498 | Centennial Solar | CS250 | Centennial Solar : CS250 | -0.33 | 22 | 15 | 250 | 17.9 | 14
499 | Centennial Solar | CS40T | Centennial Solar : CS40T | -0.26 | 22.8 | 2.5 | 40 | 16.8 | 1.92
500 | Centennial Solar | OPAK-3-L | Centennial Solar : OPAK-3-L | -0.26 | 98 | 2.09 | 114 | 72 | 1.59
501 | Centennial Solar | Thin Film 117Wp | Centennial Solar : Thin Film 117Wp | -0.26 | 98 | 1.8 | 117 | 72 | 1.33
502 | Centennial Solar | THRU-4x | Centennial Solar : THRU-4x | -0.26 | 98 | 1.8 | 96 | 72 | 1.33
503 | Centro Solar | TFM288RG Proff | Centro Solar : TFM288RG Proff | -0.3 | 46.2 | 5.3 | 144 | 33 | 4.36
504 | CentroSolar | S 205M54 Excellent | CentroSolar : S 205M54 Excellent | -0.36 | 32.67 | 8.49 | 205 | 26.38 | 7.77
505 | CentroSolar | S 210M54 Excellent | CentroSolar : S 210M54 Excellent | -0.36 | 32.78 | 8.66 | 210 | 26.45 | 7.94
506 | CentroSolar | S 215M54 Excellent | CentroSolar : S 215M54 Excellent | -0.36 | 32.83 | 8.71 | 215 | 26.88 | 8
507 | CentroSolar | S 220M54 Excellent | CentroSolar : S 220M54 Excellent | -0.36 | 32.89 | 8.78 | 220 | 27.26 | 8.07
508 | CentroSolar | S 225M54 Excellent | CentroSolar : S 225M54 Excellent | -0.36 | 32.94 | 8.94 | 225 | 27.61 | 8.15
509 | CentroSolar | S-Excellent S-185P50 | CentroSolar : S-Excellent S-185P50 | -0.36 | 30.65 | 8.09 | 185 | 24.1 | 7.68
510 | CentroSolar | S-Excellent S-185P50 | CentroSolar : S-Excellent S-185P50 | -0.36 | 30.65 | 8.09 | 185 | 24.1 | 7.68
511 | CentroSolar | S-Excellent S-190M50 | CentroSolar : S-Excellent S-190M50 | -0.36 | 30.5 | 8.33 | 190 | 24.15 | 7.87
512 | CentroSolar | S-Excellent S-190P50 | CentroSolar : S-Excellent S-190P50 | -0.36 | 30.75 | 8.27 | 190 | 24.15 | 7.87
513 | CentroSolar | S-Excellent S-190P50 | CentroSolar : S-Excellent S-190P50 | -0.36 | 30.75 | 8.27 | 190 | 24.15 | 7.87
514 | CentroSolar | S-Excellent S-195M50 | CentroSolar : S-Excellent S-195M50 | -0.36 | 30.6 | 8.51 | 195 | 24.2 | 8.06
515 | CentroSolar | S-Excellent S-195P50 | CentroSolar : S-Excellent S-195P50 | -0.36 | 30.85 | 8.45 | 195 | 24.2 | 8.06
516 | CentroSolar | S-Excellent S-195P50 | CentroSolar : S-Excellent S-195P50 | -0.36 | 30.85 | 8.45 | 195 | 24.2 | 8.06
517 | CentroSolar | S-Excellent S-200M50 | CentroSolar : S-Excellent S-200M50 | -0.36 | 30.7 | 8.69 | 200 | 24.25 | 8.25
518 | CentroSolar | S-Excellent S-200P50 | CentroSolar : S-Excellent S-200P50 | -0.36 | 30.95 | 8.66 | 200 | 24.25 | 8.25
519 | CentroSolar | S-Excellent S-205M50 | CentroSolar : S-Excellent S-205M50 | -0.36 | 30.8 | 8.8 | 205 | 24.3 | 8.44
520 | CentroSolar | S-Professional S-220M60 | CentroSolar : S-Professional S-220M60 | -0.35 | 36.25 | 8.26 | 220 | 28.55 | 7.69
521 | CentroSolar | S-Professional S-220P60 | CentroSolar : S-Professional S-220P60 | -0.35 | 36.25 | 8.26 | 220 | 28.55 | 7.69
522 | CentroSolar | S-Professional S-225M60 | CentroSolar : S-Professional S-225M60 | -0.35 | 36.32 | 8.37 | 225 | 28.6 | 7.87
523 | CentroSolar | S-Professional S-225P60 | CentroSolar : S-Professional S-225P60 | -0.35 | 36.32 | 8.37 | 225 | 28.6 | 7.87
524 | CentroSolar | S-Professional S-230M60 | CentroSolar : S-Professional S-230M60 | -0.35 | 36.39 | 8.48 | 230 | 28.65 | 8.03
525 | CentroSolar | S-Professional S-230P60 | CentroSolar : S-Professional S-230P60 | -0.35 | 36.39 | 8.48 | 230 | 28.65 | 8.03
526 | CentroSolar | S-Professional S-235M60 | CentroSolar : S-Professional S-235M60 | -0.35 | 36.46 | 8.59 | 235 | 28.7 | 8.19
527 | CentroSolar | S-Professional S-235P60 | CentroSolar : S-Professional S-235P60 | -0.35 | 36.46 | 8.59 | 235 | 28.7 | 8.19
528 | CentroSolar | S-Professional S-240M60 | CentroSolar : S-Professional S-240M60 | -0.35 | 36.53 | 8.7 | 240 | 28.75 | 8.35
529 | CentroSolar | S-Professional S-240P60 | CentroSolar : S-Professional S-240P60 | -0.35 | 36.53 | 8.7 | 240 | 28.75 | 8.35
530 | CentroSolar | S-Ultra S-185P50 | CentroSolar : S-Ultra S-185P50 | -0.36 | 30.65 | 8.09 | 185 | 24.1 | 7.68
531 | CentroSolar | S-Ultra S-190M50 | CentroSolar : S-Ultra S-190M50 | -0.36 | 30.5 | 8.33 | 190 | 24.15 | 7.87
532 | CentroSolar | S-Ultra S-190P50 | CentroSolar : S-Ultra S-190P50 | -0.36 | 30.75 | 8.27 | 190 | 24.15 | 7.87
533 | CentroSolar | S-Ultra S-195M50 | CentroSolar : S-Ultra S-195M50 | -0.36 | 30.6 | 8.51 | 195 | 24.2 | 8.06
534 | CentroSolar | S-Ultra S-195P50 | CentroSolar : S-Ultra S-195P50 | -0.36 | 30.85 | 8.45 | 195 | 24.2 | 8.06
535 | CentroSolar | S-Ultra S-200M50 | CentroSolar : S-Ultra S-200M50 | -0.36 | 30.7 | 8.69 | 200 | 24.25 | 8.25
536 | CentroSolar | S-Ultra S-200P50 | CentroSolar : S-Ultra S-200P50 | -0.36 | 30.95 | 8.66 | 200 | 24.25 | 8.25
537 | CentroSolar | S-Ultra S-205M50 | CentroSolar : S-Ultra S-205M50 | -0.36 | 30.8 | 8.8 | 205 | 24.3 | 8.44
538 | Chaori Solar, Shanghai | CRM155W125s 155Wp | Chaori Solar, Shanghai : CRM155W125s 155Wp | -0.34 | 43 | 4.8 | 155 | 35 | 4.42
539 | Chaori Solar, Shanghai | CRM160W125s 160Wp | Chaori Solar, Shanghai : CRM160W125s 160Wp | -0.34 | 43 | 4.96 | 160 | 35 | 4.57
540 | Chaori Solar, Shanghai | CRM165W125s 165Wp | Chaori Solar, Shanghai : CRM165W125s 165Wp | -0.34 | 43 | 5.11 | 165 | 35 | 4.71
541 | Chaori Solar, Shanghai | CRM170W125s 170Wp | Chaori Solar, Shanghai : CRM170W125s 170Wp | -0.34 | 43 | 5.27 | 170 | 35 | 4.86
542 | Chaori Solar, Shanghai | CRM175W125s 175Wp | Chaori Solar, Shanghai : CRM175W125s 175Wp | -0.34 | 43 | 5.42 | 175 | 35 | 5
543 | Chaori Solar, Shanghai | CRM180W125s 180Wp | Chaori Solar, Shanghai : CRM180W125s 180Wp | -0.34 | 43 | 5.58 | 180 | 35 | 5.15
544 | Chinaland Solar Energy | CHN-150-72M | Chinaland Solar Energy : CHN-150-72M | -0.35 | 43.9 | 4.77 | 150 | 35.3 | 4.27
545 | Chinaland Solar Energy | CHN-160-72M | Chinaland Solar Energy : CHN-160-72M | -0.35 | 44.6 | 4.95 | 160 | 36 | 4.48
546 | Chinaland Solar Energy | CHN-170-72M | Chinaland Solar Energy : CHN-170-72M | -0.35 | 44.6 | 5.11 | 170 | 36.7 | 4.67
547 | Chinaland Solar Energy | CHN-180-72M | Chinaland Solar Energy : CHN-180-72M | -0.35 | 44.6 | 5.23 | 180 | 38.2 | 4.74
548 | Chinaland Solar Energy | CHN-185-72M | Chinaland Solar Energy : CHN-185-72M | -0.35 | 44.2 | 5.44 | 185 | 37 | 5.01
549 | Chinaland Solar Energy | CHN-190-72M | Chinaland Solar Energy : CHN-190-72M | -0.35 | 44.3 | 5.6 | 190 | 37.1 | 5.12
550 | Ching Han Tech | CSSS-100A | Ching Han Tech : CSSS-100A | -0.32 | 100 | 1.65 | 100 | 76 | 1.32
551 | CNBM | Solar Mono 160 | CNBM : Solar Mono 160 | -0.33 | 43.8 | 5.07 | 160 | 35 | 4.58
552 | CNBM | Solar Mono 165 | CNBM : Solar Mono 165 | -0.33 | 43.9 | 5.14 | 165 | 35.7 | 4.62
553 | CNBM | Solar Mono 170 | CNBM : Solar Mono 170 | -0.33 | 44.1 | 5.22 | 170 | 36 | 4.72
554 | CNBM | Solar Mono 175 | CNBM : Solar Mono 175 | -0.33 | 44.2 | 5.22 | 175 | 36.4 | 4.81
555 | CNBM | Solar Mono 180 | CNBM : Solar Mono 180 | -0.33 | 44.6 | 5.3 | 180 | 36.8 | 4.89
556 | CNBM | Solar Mono 185 | CNBM : Solar Mono 185 | -0.33 | 44.6 | 5.46 | 185 | 36.8 | 5.03
557 | CNBM | Solar Poly 200 | CNBM : Solar Poly 200 | -0.35 | 36 | 7.75 | 200 | 28.7 | 6.97
558 | CNBM | Solar Poly 210 | CNBM : Solar Poly 210 | -0.35 | 36.4 | 7.86 | 210 | 29.2 | 7.19
559 | CNBM | Solar Poly 220 | CNBM : Solar Poly 220 | -0.35 | 36.8 | 8 | 220 | 29.8 | 7.39
560 | CNBM | Solar Poly 230 | CNBM : Solar Poly 230 | -0.35 | 37 | 8.18 | 230 | 30 | 7.66
561 | CNBM | Solar Poly 240 | CNBM : Solar Poly 240 | -0.35 | 37.5 | 8.38 | 240 | 30.6 | 7.84
562 | CNPV Power | 175M | CNPV Power : 175M | -0.35 | 44.2 | 5.3 | 175 | 36.6 | 4.8
563 | CNPV Power | 180M | CNPV Power : 180M | -0.35 | 44.6 | 5.35 | 180 | 37.2 | 4.85
564 | CNPV Power | 185M | CNPV Power : 185M | -0.35 | 45 | 5.4 | 185 | 37.8 | 4.9
565 | CNPV Power | 190M | CNPV Power : 190M | -0.35 | 45.1 | 5.55 | 190 | 37.8 | 5.05
566 | CNPV Power | 195M | CNPV Power : 195M | -0.35 | 45.2 | 5.6 | 195 | 37.9 | 5.15
567 | CNPV Power | 200M | CNPV Power : 200M | -0.35 | 45.3 | 5.65 | 200 | 38 | 5.25
568 | CNPV Power | 220P | CNPV Power : 220P | -0.35 | 36.8 | 8 | 220 | 29.8 | 7.4
569 | CNPV Power | 225P | CNPV Power : 225P | -0.35 | 37 | 8.1 | 225 | 30 | 7.5
570 | CNPV Power | 230P | CNPV Power : 230P | -0.35 | 37.2 | 8.2 | 230 | 30.3 | 7.6
571 | CNPV Power | 235P | CNPV Power : 235P | -0.35 | 37.3 | 8.3 | 235 | 30.5 | 7.7
572 | CNPV Power | 240P | CNPV Power : 240P | -0.35 | 37.4 | 8.4 | 240 | 30.8 | 7.8
573 | CNPV Power | 245P | CNPV Power : 245P | -0.35 | 37.5 | 8.5 | 245 | 31 | 7.9
574 | Conergy | A 165P | Conergy : A 165P | -0.366 | 43.2 | 5.1 | 165 | 34.4 | 4.8
575 | Conergy | C 160P | Conergy : C 160P | -0.34 | 28.4 | 8.04 | 160 | 22.8 | 7.02
576 | Conergy | C 175M | Conergy : C 175M | -0.324 | 44.4 | 5.4 | 175 | 35.4 | 4.95
577 | Conergy | P 170 | Conergy : P 170 | -0.36 | 31.2 | 7.7 | 172 | 24.3 | 7.1
578 | Conergy | P 170 M | Conergy : P 170 M | -0.38 | 44.5 | 5.12 | 170 | 35.9 | 4.74
579 | Conergy | P 175 M | Conergy : P 175 M | -0.38 | 44.8 | 5.17 | 175 | 36 | 4.86
580 | Conergy | P 180 M | Conergy : P 180 M | -0.35 | 45 | 5.2 | 180 | 36 | 5
581 | Conergy | PowerPlus 200Wp | Conergy : PowerPlus 200Wp | -0.34 | 35.29 | 7.72 | 200 | 28.52 | 7.09
582 | Conergy | PowerPlus 205Wp | Conergy : PowerPlus 205Wp | -0.34 | 35.53 | 7.83 | 205 | 28.56 | 7.26
583 | Conergy | PowerPlus 210Wp | Conergy : PowerPlus 210Wp | -0.34 | 35.77 | 7.94 | 210 | 28.65 | 7.41
584 | Conergy | PowerPlus 215Wp | Conergy : PowerPlus 215Wp | -0.34 | 36 | 8.04 | 215 | 28.8 | 7.54
585 | Conergy | PowerPlus 220Wp | Conergy : PowerPlus 220Wp | -0.34 | 36.23 | 8.15 | 220 | 29.01 | 7.65
586 | Conergy | PowerPlus 225Wp | Conergy : PowerPlus 225Wp | -0.34 | 36.43 | 8.24 | 225 | 29.23 | 7.74
587 | Conergy | PowerPlus 230Wp | Conergy : PowerPlus 230Wp | -0.34 | 36.66 | 8.34 | 230 | 29.54 | 7.82
588 | Conergy | S 170 M | Conergy : S 170 M | -0.35 | 43.8 | 5.14 | 170 | 35.2 | 4.83
589 | Conergy | S 175 M | Conergy : S 175 M | -0.35 | 44.2 | 5.2 | 175 | 35.2 | 4.95
590 | Conergy | S 190 P | Conergy : S 190 P | -0.354 | 32.8 | 7.82 | 190 | 26.2 | 7.25
591 | Conergy | S 200 P | Conergy : S 200 P | -0.354 | 32.8 | 8 | 200 | 26.2 | 7.63
592 | CONSOLAR | Voltus 180 | CONSOLAR : Voltus 180 | -0.35 | 44.3 | 5.2 | 180 | 36.73 | 4.9
593 | CP-Solar | 185M36 Black-laminated | CP-Solar : 185M36 Black-laminated | -0.38 | 44.5 | 5.31 | 185 | 36.9 | 5.02
594 | CP-Solar | 185M36 Ultra | CP-Solar : 185M36 Ultra | -0.38 | 44.5 | 5.31 | 185 | 36.9 | 5.02
595 | CP-Solar | 185M36 Ultra-Laminated | CP-Solar : 185M36 Ultra-Laminated | -0.38 | 44.5 | 5.31 | 185 | 36.9 | 5.02
596 | CP-Solar | 190M36 Laminated | CP-Solar : 190M36 Laminated | -0.38 | 44.5 | 5.48 | 190 | 37.3 | 5.1
597 | CP-Solar | 195M36 | CP-Solar : 195M36 | -0.38 | 45.5 | 5.6 | 195 | 37.3 | 5.23
598 | CP-Solar | 230M30 | CP-Solar : 230M30 | -0.38 | 36.1 | 8.35 | 230 | 29.9 | 7.7
599 | CP-Solar | 235P30 | CP-Solar : 235P30 | -0.38 | 36 | 8.77 | 235 | 30 | 7.84
600 | CP-Solar | 240M48 | CP-Solar : 240M48 | -0.38 | 58.5 | 5.38 | 240 | 48.6 | 4.94
601 | CP-Solar | 240P30 | CP-Solar : 240P30 | -0.38 | 37.2 | 8.52 | 240 | 30.6 | 7.85
602 | CP-Solar | 240P36 | CP-Solar : 240P36 | -0.38 | 42.91 | 7.75 | 240 | 34.92 | 6.88
603 | CP-Solar | 245M30 | CP-Solar : 245M30 | -0.38 | 37.2 | 8.66 | 245 | 30.3 | 8.09
604 | CP-Solar | 250P36 | CP-Solar : 250P36 | -0.38 | 43.2 | 7.71 | 250 | 35.3 | 7.09
605 | CP-Solar | 260P36 | CP-Solar : 260P36 | -0.38 | 43.8 | 7.98 | 260 | 35.6 | 7.31
606 | CP-Solar | 270P36 | CP-Solar : 270P36 | -0.38 | 44.2 | 8.06 | 270 | 36 | 7.5
607 | CP-Solar | 280P36 | CP-Solar : 280P36 | -0.38 | 44.4 | 8.23 | 280 | 36 | 7.78
608 | CP-Solar | 290P36 | CP-Solar : 290P36 | -0.38 | 44.6 | 8.4 | 290 | 36 | 8.06
609 | CP-Solar | CPS 185Wp | CP-Solar : CPS 185Wp | -0.4 | 44.5 | 5.31 | 185 | 36.9 | 5.01
610 | CP-Solar | CPS120M24 | CP-Solar : CPS120M24 | -0.33 | 29.3 | 5.47 | 120 | 23.9 | 5.03
611 | CP-Solar | CPS125M24 | CP-Solar : CPS125M24 | -0.33 | 29.7 | 5.4 | 125 | 24.9 | 5.02
612 | CP-Solar | CPS130P18 | CP-Solar : CPS130P18 | -0.33 | 21.9 | 7.98 | 130 | 17.8 | 7.3
613 | CP-Solar | CPS135M27(frameless) | CP-Solar : CPS135M27(frameless) | -0.33 | 32.9 | 5.31 | 135 | 27.8 | 4.86
614 | CP-Solar | CPS135M27(with frame) | CP-Solar : CPS135M27(with frame) | -0.33 | 32.9 | 5.31 | 135 | 27.8 | 4.86
615 | CP-Solar | CPS135P18(frameless) | CP-Solar : CPS135P18(frameless) | -0.33 | 22.1 | 8.06 | 135 | 18 | 7.5
616 | CP-Solar | CPS135P18(with frame) | CP-Solar : CPS135P18(with frame) | -0.33 | 22.1 | 8.06 | 135 | 18 | 7.5
617 | CP-Solar | CPS140P18 | CP-Solar : CPS140P18 | -0.33 | 22.2 | 8.23 | 140 | 18 | 7.78
618 | CP-Solar | CPS150M30 | CP-Solar : CPS150M30 | -0.33 | 37.6 | 5.18 | 150 | 31.2 | 4.81
619 | CP-Solar | CPS155M30 | CP-Solar : CPS155M30 | -0.33 | 37.7 | 5.39 | 155 | 31.1 | 4.98
620 | CP-Solar | CPS160M30 | CP-Solar : CPS160M30 | -0.33 | 37.7 | 5.13 | 160 | 31.2 | 5.13
621 | CP-Solar | CPS165P24 | CP-Solar : CPS165P24 | -0.33 | 28.6 | 7.84 | 165 | 23.5 | 7.02
622 | CP-Solar | CPS170M36 | CP-Solar : CPS170M36 | -0.33 | 44.1 | 5.09 | 170 | 36.5 | 4.66
623 | CP-Solar | CPS170P24 | CP-Solar : CPS170P24 | -0.33 | 28.6 | 8.08 | 170 | 23.5 | 7.23
624 | CP-Solar | CPS175M36 | CP-Solar : CPS175M36 | -0.33 | 44.1 | 5.22 | 175 | 36.5 | 4.79
625 | CP-Solar | CPS175P24 | CP-Solar : CPS175P24 | -0.33 | 29.2 | 8.06 | 175 | 23.8 | 7.35
626 | CP-Solar | CPS180M36 | CP-Solar : CPS180M36 | -0.33 | 44.6 | 5.22 | 180 | 36.8 | 4.89
627 | CP-Solar | CPS180P24 | CP-Solar : CPS180P24 | -0.33 | 29.5 | 8.05 | 180 | 24 | 7.5
628 | CP-Solar | CPS185M36 | CP-Solar : CPS185M36 | -0.33 | 44.5 | 5.31 | 185 | 36.9 | 5.31
629 | CP-Solar | CPS185P24 | CP-Solar : CPS185P24 | -0.33 | 29.6 | 8.17 | 185 | 24 | 7.71
630 | CP-Solar | CPS190M36 | CP-Solar : CPS190M36 | -0.33 | 44.5 | 5.48 | 190 | 37.3 | 5.09
631 | CP-Solar | CPS190P27 | CP-Solar : CPS190P27 | -0.33 | 32.6 | 7.92 | 190 | 26.5 | 7.17
632 | CP-Solar | CPS200P27 | CP-Solar : CPS200P27 | -0.33 | 33.2 | 7.95 | 200 | 27 | 7.41
633 | CP-Solar | CPS205P27 | CP-Solar : CPS205P27 | -0.33 | 33.3 | 8.04 | 205 | 27 | 7.59
634 | CP-Solar | CPS210P27 | CP-Solar : CPS210P27 | -0.33 | 33.4 | 8.12 | 210 | 27 | 7.78
635 | CP-Solar | CPS210P30 | CP-Solar : CPS210P30 | -0.33 | 36.1 | 8.02 | 210 | 29.1 | 7.22
636 | CP-Solar | CPS215P30 | CP-Solar : CPS215P30 | -0.33 | 36.2 | 8.15 | 215 | 29.3 | 7.34
637 | CP-Solar | CPS220P30 | CP-Solar : CPS220P30 | -0.33 | 36.3 | 8.25 | 220 | 29.6 | 7.43
638 | CP-Solar | CPS225P30 | CP-Solar : CPS225P30 | -0.33 | 36.3 | 8.35 | 225 | 30 | 7.5
639 | CP-Solar | CPS230M30 | CP-Solar : CPS230M30 | -0.33 | 36.1 | 8.35 | 230 | 29.9 | 7.69
640 | CP-Solar | CPS230P30 | CP-Solar : CPS230P30 | -0.33 | 36.3 | 8.48 | 230 | 30.1 | 7.64
641 | CP-Solar | CPS240M48 | CP-Solar : CPS240M48 | -0.33 | 58.5 | 5.38 | 240 | 48.6 | 4.94
642 | CP-Solar | CPS240P30 | CP-Solar : CPS240P30 | -0.33 | 37.2 | 8.52 | 240 | 30.6 | 7.84
643 | CP-Solar | CPS250P36 | CP-Solar : CPS250P36 | -0.33 | 43.2 | 7.71 | 250 | 35.3 | 7.08
644 | CP-Solar | CPS260P36 | CP-Solar : CPS260P36 | -0.33 | 43.8 | 7.98 | 260 | 35.6 | 7.3
645 | CP-Solar | CPS270P36 | CP-Solar : CPS270P36 | -0.33 | 44.2 | 8.06 | 270 | 36 | 7.5
646 | CP-Solar | CPS60M12 | CP-Solar : CPS60M12 | -0.33 | 14.6 | 5.1 | 60 | 11.9 | 5.09
647 | CP-Solar | CPS65P18 | CP-Solar : CPS65P18 | -0.33 | 21.9 | 3.99 | 65 | 17.8 | 3.65
648 | CP-Solar | CPS70P18 | CP-Solar : CPS70P18 | -0.33 | 22.2 | 4.12 | 70 | 18 | 3.89
649 | CP-Solar | CPS85P12 | CP-Solar : CPS85P12 | -0.33 | 14.6 | 7.83 | 85 | 11.88 | 7.15
650 | CP-Solar | CPS90M18 | CP-Solar : CPS90M18 | -0.33 | 22.4 | 5.22 | 90 | 18.8 | 4.78
651 | CP-Solar | CPS90P12 | CP-Solar : CPS90P12 | -0.33 | 14.7 | 8.08 | 90 | 12 | 7.5
652 | CP-Solar | CP-Solar_CPS120M24 | CP-Solar : CP-Solar_CPS120M24 | -0.3 | 29.3 | 5.47 | 120 | 23.9 | 5.03
653 | CP-Solar | CP-Solar_CPS125M24 | CP-Solar : CP-Solar_CPS125M24 | -0.3 | 29.7 | 5.4 | 125 | 24.9 | 5.03
654 | CP-Solar | CP-Solar_CPS130P18 | CP-Solar : CP-Solar_CPS130P18 | -0.3 | 21.9 | 7.98 | 130 | 17.8 | 7.31
655 | CP-Solar | CP-Solar_CPS135M27(frameless) | CP-Solar : CP-Solar_CPS135M27(frameless) | -0.3 | 32.9 | 5.31 | 135 | 27.8 | 4.86
656 | CP-Solar | CP-Solar_CPS135M27(with frame) | CP-Solar : CP-Solar_CPS135M27(with frame) | -0.3 | 32.9 | 5.31 | 135 | 27.8 | 4.86
657 | CP-Solar | CP-Solar_CPS135P18(frameless) | CP-Solar : CP-Solar_CPS135P18(frameless) | -0.3 | 22.1 | 8.06 | 135 | 18 | 7.5
658 | CP-Solar | CP-Solar_CPS135P18(with frame) | CP-Solar : CP-Solar_CPS135P18(with frame) | -0.3 | 22.1 | 8.06 | 135 | 18 | 7.5
659 | CP-Solar | CP-Solar_CPS140P18 | CP-Solar : CP-Solar_CPS140P18 | -0.3 | 22.2 | 8.23 | 140 | 18 | 7.78
660 | CP-Solar | CP-Solar_CPS150M30 | CP-Solar : CP-Solar_CPS150M30 | -0.3 | 37.6 | 5.18 | 150 | 31.2 | 4.81
661 | CP-Solar | CP-Solar_CPS155M30 | CP-Solar : CP-Solar_CPS155M30 | -0.3 | 37.7 | 5.39 | 155 | 31.1 | 4.99
662 | CP-Solar | CP-Solar_CPS160M30 | CP-Solar : CP-Solar_CPS160M30 | -0.3 | 37.7 | 5.13 | 160 | 31.2 | 5.13
663 | CP-Solar | CP-Solar_CPS165P24 | CP-Solar : CP-Solar_CPS165P24 | -0.3 | 28.6 | 7.84 | 165 | 23.5 | 7.03
664 | CP-Solar | CP-Solar_CPS170M36 | CP-Solar : CP-Solar_CPS170M36 | -0.3 | 44.1 | 5.09 | 170 | 36.5 | 4.66
665 | CP-Solar | CP-Solar_CPS170P24 | CP-Solar : CP-Solar_CPS170P24 | -0.3 | 28.6 | 8.08 | 170 | 23.5 | 7.24
666 | CP-Solar | CP-Solar_CPS175M36 | CP-Solar : CP-Solar_CPS175M36 | -0.3 | 44.1 | 5.22 | 175 | 36.5 | 4.8
667 | CP-Solar | CP-Solar_CPS175M36 transparent | CP-Solar : CP-Solar_CPS175M36 transparent | -0.3 | 44.1 | 5.22 | 175 | 36.5 | 4.8
668 | CP-Solar | CP-Solar_CPS175P24 | CP-Solar : CP-Solar_CPS175P24 | -0.3 | 29.2 | 8.06 | 175 | 23.8 | 7.36
669 | CP-Solar | CP-Solar_CPS180M36 | CP-Solar : CP-Solar_CPS180M36 | -0.3 | 44.6 | 5.22 | 180 | 36.8 | 4.9
670 | CP-Solar | CP-Solar_CPS180P24 | CP-Solar : CP-Solar_CPS180P24 | -0.3 | 29.5 | 8.05 | 180 | 24 | 7.5
671 | CP-Solar | CP-Solar_CPS185M36 black | CP-Solar : CP-Solar_CPS185M36 black | -0.3 | 44.5 | 5.31 | 185 | 36.9 | 5.02
672 | CP-Solar | CP-Solar_CPS185M36 black | CP-Solar : CP-Solar_CPS185M36 black | -0.3 | 44.5 | 5.31 | 185 | 36.9 | 5.02
673 | CP-Solar | CP-Solar_CPS185M36 Laminate | CP-Solar : CP-Solar_CPS185M36 Laminate | -0.3 | 44.5 | 5.31 | 185 | 36.9 | 5.02
674 | CP-Solar | CP-Solar_CPS185M36 transparent | CP-Solar : CP-Solar_CPS185M36 transparent | -0.3 | 44.5 | 5.31 | 185 | 36.9 | 5.02
675 | CP-Solar | CP-Solar_CPS185M36(with frame) | CP-Solar : CP-Solar_CPS185M36(with frame) | -0.3 | 44.5 | 5.31 | 185 | 36.9 | 5.02
676 | CP-Solar | CP-Solar_CPS185M36(with frame) | CP-Solar : CP-Solar_CPS185M36(with frame) | -0.3 | 44.5 | 5.31 | 185 | 36.9 | 5.02
677 | CP-Solar | CP-Solar_CPS185P24 | CP-Solar : CP-Solar_CPS185P24 | -0.3 | 29.6 | 8.17 | 185 | 24 | 7.71
678 | CP-Solar | CP-Solar_CPS190M36 | CP-Solar : CP-Solar_CPS190M36 | -0.3 | 44.5 | 5.48 | 190 | 37.3 | 5.1
679 | CP-Solar | CP-Solar_CPS190M36 transparent | CP-Solar : CP-Solar_CPS190M36 transparent | -0.3 | 44.5 | 5.48 | 190 | 37.3 | 5.1
680 | CP-Solar | CP-Solar_CPS190P27 | CP-Solar : CP-Solar_CPS190P27 | -0.3 | 32.6 | 7.92 | 190 | 26.5 | 7.17
681 | CP-Solar | CP-Solar_CPS205P27 | CP-Solar : CP-Solar_CPS205P27 | -0.3 | 33.2 | 7.95 | 200 | 27 | 7.6
682 | CP-Solar | CP-Solar_CPS20P18 | CP-Solar : CP-Solar_CPS20P18 | -0.3 | 21.5 | 1.29 | 20 | 17.5 | 1.15
683 | CP-Solar | CP-Solar_CPS210P27 | CP-Solar : CP-Solar_CPS210P27 | -0.3 | 33.3 | 8.04 | 205 | 27 | 7.6
684 | CP-Solar | CP-Solar_CPS210P27 | CP-Solar : CP-Solar_CPS210P27 | -0.3 | 33.4 | 8.12 | 210 | 27 | 7.78
685 | CP-Solar | CP-Solar_CPS210P30 | CP-Solar : CP-Solar_CPS210P30 | -0.3 | 36.1 | 8.02 | 210 | 29.1 | 7.22
686 | CP-Solar | CP-Solar_CPS215P30 | CP-Solar : CP-Solar_CPS215P30 | -0.3 | 36.2 | 8.15 | 215 | 29.3 | 7.34
687 | CP-Solar | CP-Solar_CPS220P30 | CP-Solar : CP-Solar_CPS220P30 | -0.3 | 36.3 | 8.25 | 220 | 29.6 | 7.44
688 | CP-Solar | CP-Solar_CPS225P30 | CP-Solar : CP-Solar_CPS225P30 | -0.3 | 36.3 | 8.35 | 225 | 30 | 7.5
689 | CP-Solar | CP-Solar_CPS230M30 | CP-Solar : CP-Solar_CPS230M30 | -0.3 | 36.1 | 8.35 | 230 | 29.9 | 7.7
690 | CP-Solar | CP-Solar_CPS230P30 | CP-Solar : CP-Solar_CPS230P30 | -0.3 | 36.3 | 8.48 | 230 | 30.1 | 7.65
691 | CP-Solar | CP-Solar_CPS240M48 | CP-Solar : CP-Solar_CPS240M48 | -0.3 | 58.5 | 5.38 | 240 | 48.6 | 4.94
692 | CP-Solar | CP-Solar_CPS240P30 | CP-Solar : CP-Solar_CPS240P30 | -0.3 | 37.2 | 8.52 | 240 | 30.6 | 7.85
693 | CP-Solar | CP-Solar_CPS24M4.5 | CP-Solar : CP-Solar_CPS24M4.5 | -0.3 | 5.54 | 5.61 | 24 | 4.64 | 5.18
694 | CP-Solar | CP-Solar_CPS250P36 | CP-Solar : CP-Solar_CPS250P36 | -0.3 | 43.2 | 7.71 | 250 | 35.3 | 7.09
695 | CP-Solar | CP-Solar_CPS260P36 | CP-Solar : CP-Solar_CPS260P36 | -0.3 | 43.8 | 7.98 | 260 | 35.6 | 7.31
696 | CP-Solar | CP-Solar_CPS270P36 | CP-Solar : CP-Solar_CPS270P36 | -0.3 | 44.2 | 8.06 | 270 | 36 | 7.5
697 | CP-Solar | CP-Solar_CPS60M12 | CP-Solar : CP-Solar_CPS60M12 | -0.3 | 14.6 | 5.1 | 60 | 11.9 | 5.09
698 | CP-Solar | CP-Solar_CPS65P18 | CP-Solar : CP-Solar_CPS65P18 | -0.3 | 21.9 | 3.99 | 65 | 17.8 | 3.66
699 | CP-Solar | CP-Solar_CPS70P18 | CP-Solar : CP-Solar_CPS70P18 | -0.3 | 22.2 | 4.12 | 70 | 18 | 3.89
700 | CP-Solar | CP-Solar_CPS85P12 | CP-Solar : CP-Solar_CPS85P12 | -0.3 | 14.6 | 7.83 | 85 | 11.88 | 7.16
701 | CP-Solar | CP-Solar_CPS90M18 | CP-Solar : CP-Solar_CPS90M18 | -0.3 | 22.4 | 5.22 | 90 | 18.8 | 4.79
702 | CP-Solar | CP-Solar_CPS90P12 | CP-Solar : CP-Solar_CPS90P12 | -0.3 | 14.7 | 8.08 | 90 | 12 | 7.5
703 | CP-Solar | CP-Solar_CPS-Red170M36 | CP-Solar : CP-Solar_CPS-Red170M36 | -0.3 | 44.1 | 5.09 | 170 | 36.5 | 4.66
704 | CP-Solar | CP-Solar_CPS-Red230P3 | CP-Solar : CP-Solar_CPS-Red230P3 | -0.3 | 36.3 | 8.48 | 230 | 30.1 | 7.65
705 | CP-Solar | CPS-Red 170M36 | CP-Solar : CPS-Red 170M36 | -0.33 | 44.1 | 5.09 | 170 | 36.5 | 4.66
706 | CP-Solar | CPS-Red 230P30 | CP-Solar : CPS-Red 230P30 | -0.33 | 36.3 | 8.48 | 230 | 30.1 | 7.64
707 | Creaton | CREASOL | Creaton : CREASOL | -0.3 | 31.7 | 3.35 | 83.5 | 26.6 | 3.14
708 | Dasol | DS-A4-185 | Dasol : DS-A4-185 | -0.38 | 35.1 | 7.3 | 185 | 28.2 | 6.56
709 | Dasol | DS-A4-185(m) | Dasol : DS-A4-185(m) | -0.38 | 35.1 | 7.3 | 185 | 28.2 | 6.56
710 | Dasol | DS-A4-190 | Dasol : DS-A4-190 | -0.38 | 35.3 | 7.5 | 190 | 28.4 | 6.69
711 | Dasol | DS-A4-190(m | Dasol : DS-A4-190(m | -0.38 | 35.3 | 7.5 | 190 | 28.4 | 6.69
712 | Dasol | DS-A4-195 | Dasol : DS-A4-195 | -0.38 | 35.5 | 7.6 | 195 | 28.6 | 6.82
713 | Dasol | DS-A4-195(m) | Dasol : DS-A4-195(m) | -0.38 | 35.5 | 7.6 | 195 | 28.6 | 6.82
714 | Dasol | DS-A4-200 | Dasol : DS-A4-200 | -0.38 | 35.7 | 7.8 | 200 | 28.8 | 6.94
715 | Dasol | DS-A4-200(m) | Dasol : DS-A4-200(m) | -0.38 | 35.7 | 7.8 | 200 | 28.8 | 6.94
716 | Dasol | DS-A4-205 | Dasol : DS-A4-205 | -0.38 | 35.9 | 7.8 | 205 | 29 | 7.07
717 | Dasol | DS-A4-205(m) | Dasol : DS-A4-205(m) | -0.38 | 35.9 | 7.8 | 205 | 29 | 7.07
718 | Dasol | DS-A4-210 | Dasol : DS-A4-210 | -0.38 | 36.1 | 8 | 210 | 29.2 | 7.19
719 | Dasol | DS-A4-210(m) | Dasol : DS-A4-210(m) | -0.38 | 36.1 | 8 | 210 | 29.2 | 7.19
720 | Dasol | DS-A4-215 | Dasol : DS-A4-215 | -0.38 | 36.3 | 8 | 215 | 29.4 | 7.31
721 | Dasol | DS-A4-215(m) | Dasol : DS-A4-215(m) | -0.38 | 36.3 | 8 | 215 | 29.4 | 7.31
722 | Dasol | DS-A4-220 | Dasol : DS-A4-220 | -0.38 | 36.5 | 8.1 | 220 | 29.6 | 7.44
723 | Dasol | DS-A4-220(m) | Dasol : DS-A4-220(m) | -0.38 | 36.5 | 8.1 | 220 | 29.6 | 7.44
724 | Dasol | DS-A4-225 | Dasol : DS-A4-225 | -0.38 | 36.7 | 8.2 | 225 | 29.8 | 7.55
725 | Dasol | DS-A4-225(m) | Dasol : DS-A4-225(m) | -0.38 | 36.7 | 8.2 | 225 | 29.8 | 7.55
726 | Dasol | DS-A4-230 | Dasol : DS-A4-230 | -0.38 | 36.9 | 8.3 | 230 | 30 | 7.67
727 | Dasol | DS-A4-230(m) | Dasol : DS-A4-230(m) | -0.38 | 36.9 | 8.3 | 230 | 30 | 7.67
728 | Dasol | DS-A4-230(m) | Dasol : DS-A4-230(m) | -0.38 | 36.9 | 8.3 | 230 | 30 | 7.67
729 | Dasol | DS-A4-235 | Dasol : DS-A4-235 | -0.38 | 37.1 | 8.4 | 235 | 30.2 | 7.79
730 | Dasol | DS-A4-235(m) | Dasol : DS-A4-235(m) | -0.38 | 37.1 | 8.4 | 235 | 30.2 | 7.79
731 | Dasol | DS-A4-235(m) | Dasol : DS-A4-235(m) | -0.38 | 37.1 | 8.4 | 235 | 30.2 | 7.79
732 | Dasol | DS-A4-240 | Dasol : DS-A4-240 | -0.38 | 37.3 | 8.6 | 240 | 30.4 | 7.9
733 | Dasol | DS-A4-240(m) | Dasol : DS-A4-240(m) | -0.38 | 37.3 | 8.6 | 240 | 30.4 | 7.9
734 | Dasol | DS-A4-240(m) | Dasol : DS-A4-240(m) | -0.38 | 37.3 | 8.6 | 240 | 30.4 | 7.9
735 | Dasol | DS-A4-245 | Dasol : DS-A4-245 | -0.38 | 37.5 | 8.7 | 245 | 30.6 | 8.01
736 | Dasol | DS-A4-245(m) | Dasol : DS-A4-245(m) | -0.38 | 37.5 | 8.7 | 245 | 30.6 | 8.01
737 | Dasol | DS-A4-245(m) | Dasol : DS-A4-245(m) | -0.38 | 37.5 | 8.7 | 245 | 30.6 | 8.01
738 | Derbysolar | PVL-136 | Derbysolar : PVL-136 | -0.38 | 46.2 | 5.1 | 136 | 33 | 4.1
739 | Derbysolar | PVL-144 | Derbysolar : PVL-144 | -0.38 | 46.2 | 5.3 | 144 | 33 | 4.36
740 | Derbysolar | PVL-68 | Derbysolar : PVL-68 | -0.38 | 23.1 | 5.1 | 68 | 16.5 | 4.1
741 | DOPT | DM 160 | DOPT : DM 160 | -0.366 | 43.24 | 4.9 | 160 | 35.35 | 4.52
742 | DOPT | DM 170 | DOPT : DM 170 | -0.353 | 44.86 | 5.1 | 170 | 35.64 | 4.77
743 | DOPT | DM 175 | DOPT : DM 175 | -0.352 | 45.06 | 5.21 | 175 | 35.64 | 4.91
744 | DOPT | DM 180 | DOPT : DM 180 | -0.351 | 45.1 | 5.23 | 180 | 35.64 | 5.05
745 | DROBen | CG200 215Wp | DROBen : CG200 215Wp | -0.332 | 36.1 | 8 | 215 | 29.4 | 7.3
746 | Dunasolar | DS 10-12 | Dunasolar : DS 10-12 | -0.4 | 21.8 | 0.72 | 10 | 16.1 | 0.58
747 | Dunasolar | DS 20 | Dunasolar : DS 20 | -0.4 | 62.2 | 0.55 | 20 | 44.8 | 0.45
748 | Dunasolar | DS 40 | Dunasolar : DS 40 | -0.2 | 62.4 | 1.15 | 40 | 44.8 | 0.9
749 | Dunasolar | DS 40-12 | Dunasolar : DS 40-12 | -0.4 | 22.4 | 3.05 | 40 | 16 | 2.35
750 | Dunasolar | DS 40-24 | Dunasolar : DS 40-24 | -0.4 | 44.9 | 1.6 | 40 | 32 | 1.25
751 | Dunasolar | DS 45 | Dunasolar : DS 45 | -0.4 | 62.5 | 1.18 | 45 | 48 | 0.95
752 | Ebara Solar | 25Wp | Ebara Solar : 25Wp | -0.132 | 22 | 4.8 | 25 | 17 | 4.4
753 | Eclipse Italia | SOL 225M | Eclipse Italia : SOL 225M | -0.41 | 36.9 | 8.3 | 225 | 29.7 | 7.58
754 | Eclipse Italia | SOL 230M | Eclipse Italia : SOL 230M | -0.41 | 37 | 8.44 | 230 | 29.8 | 7.72
755 | Eclipse Italia | SOL 235M | Eclipse Italia : SOL 235M | -0.41 | 37.1 | 8.58 | 235 | 29.9 | 7.86
756 | Eclipse Italia | SOL 240M | Eclipse Italia : SOL 240M | -0.41 | 37.2 | 8.72 | 240 | 30 | 8
757 | Eclipse Italia | SOL 245M | Eclipse Italia : SOL 245M | -0.41 | 37.3 | 8.86 | 245 | 30.1 | 8.14
758 | Eco Power | EP210 P60 | Eco Power : EP210 P60 | -0.35 | 36.3 | 7.76 | 210 | 30.12 | 7.03
759 | Eco Power | EP220 P60 | Eco Power : EP220 P60 | -0.35 | 36.66 | 7.91 | 220 | 30.48 | 7.3
760 | Eco Power | EP230 P60 | Eco Power : EP230 P60 | -0.35 | 36.9 | 8.01 | 230 | 30.72 | 7.48
761 | Ecoxtra | EcoMono 160/Ac | Ecoxtra : EcoMono 160/Ac | -0.34 | 43.1 | 5.1 | 160 | 34.7 | 4.6
762 | Ecoxtra | EcoMono 170/Ac | Ecoxtra : EcoMono 170/Ac | -0.34 | 43.6 | 5.1 | 170 | 36.17 | 4.7
763 | Ecoxtra | EcoMono 170/Ac | Ecoxtra : EcoMono 170/Ac | -0.339 | 43.7 | 5.13 | 180 | 37.02 | 4.86
764 | EGing | BD GRID-170 | EGing : BD GRID-170 | -0.25 | 44 | 5.15 | 170 | 35 | 4.86
765 | EGing | BD GRID-175 | EGing : BD GRID-175 | -0.25 | 44.2 | 5.25 | 175 | 35.2 | 4.97
766 | EGing | BD GRID-180 | EGing : BD GRID-180 | -0.25 | 44.4 | 5.35 | 180 | 35.4 | 5.08
767 | EGing | EGM36-70 | EGing : EGM36-70 | -0.37 | 22 | 4.2 | 70 | 17.5 | 4
768 | EGing | EGM36-75 | EGing : EGM36-75 | -0.37 | 22 | 4.5 | 75 | 17.5 | 4.29
769 | EGing | EGM36-80 | EGing : EGM36-80 | -0.37 | 22 | 4.8 | 80 | 17.5 | 4.57
770 | EGing | EGM48-170 | EGing : EGM48-170 | -0.37 | 29.2 | 8.08 | 170 | 23 | 7.39
771 | EGing | EGM48-175 | EGing : EGM48-175 | -0.37 | 29.3 | 8.29 | 175 | 23 | 7.6
772 | EGing | EGM48-180 | EGing : EGM48-180 | -0.37 | 29.4 | 8.38 | 180 | 23.2 | 7.76
773 | EGing | EGM60-210 | EGing : EGM60-210 | -0.37 | 35.8 | 8.38 | 210 | 28.8 | 7.29
774 | EGing | EGM60-230 | EGing : EGM60-230 | -0.37 | 36.2 | 8.82 | 230 | 29.1 | 7.9
775 | EGing | EGM60-250 | EGing : EGM60-250 | -0.37 | 36.3 | 9.18 | 250 | 29.4 | 8.5
776 | EGing | EGM72-170 | EGing : EGM72-170 | -0.37 | 44 | 5.15 | 170 | 35 | 35
777 | EGing | EGM72-175 | EGing : EGM72-175 | -0.37 | 44.2 | 5.25 | 175 | 35.2 | 35.2
778 | EGing | EGM72-180 | EGing : EGM72-180 | -0.37 | 44.4 | 5.35 | 180 | 35.4 | 35.4
779 | EKARAT Solar | 120Wp Poly | EKARAT Solar : 120Wp Poly | -0.353 | 21.5 | 7.45 | 120 | 16.9 | 7.1
780 | EKARAT Solar | 125Wp Poly | EKARAT Solar : 125Wp Poly | -0.353 | 21.5 | 7.64 | 125 | 17 | 7.36
781 | EKARAT Solar | 180Wp Poly | EKARAT Solar : 180Wp Poly | -0.236 | 32.25 | 7.45 | 180 | 25.35 | 7.11
782 | ENE | PSP 90000/12+ | ENE : PSP 90000/12+ | -0.4 | 20.4 | 6 | 90 | 15.95 | 5.64
783 | ENE | SHE058 | ENE : SHE058 | -0.4 | 20.9 | 3.35 | 58 | 17.8 | 3.2
784 | ENE | SHE060 | ENE : SHE060 | -0.4 | 20.9 | 3.42 | 60 | 17.8 | 3.35
785 | ENE | SHE062 | ENE : SHE062 | -0.4 | 20.9 | 3.62 | 62 | 17.8 | 3.45
786 | Energetica | E - 110/24 | Energetica : E - 110/24 | -0.35 | 43.26 | 3.4 | 110 | 34.6 | 3.18
787 | Energetica | E - 130 | Energetica : E - 130 | -0.34 | 24.3 | 7.43 | 130 | 19.4 | 6.91
788 | Energie Bau | ebk 105-R | Energie Bau : ebk 105-R | -0.33 | 43.9 | 3.28 | 105 | 36 | 2.92
789 | Energie Bau | ebk 110-R | Energie Bau : ebk 110-R | -0.33 | 44.1 | 3.31 | 110 | 36 | 3.06
790 | Energy Solutions | ES(L)636 / QP 120Wp | Energy Solutions : ES(L)636 / QP 120Wp | -0.35 | 21.9 | 8.08 | 120 | 16.5 | 7.49
791 | Energy Solutions | ES(L)636 / QP 125Wp | Energy Solutions : ES(L)636 / QP 125Wp | -0.35 | 21.8 | 8.11 | 125 | 16.6 | 7.55
792 | Energy Solutions | ES(L)636 / QP 130Wp | Energy Solutions : ES(L)636 / QP 130Wp | -0.35 | 21.8 | 8.35 | 130 | 16.6 | 7.79
793 | Energy Solutions | ES(L)636 / QP 135Wp | Energy Solutions : ES(L)636 / QP 135Wp | -0.35 | 21.9 | 8.52 | 135 | 16.9 | 8
794 | Energy Solutions | ES(L)660 / QP 200Wp | Energy Solutions : ES(L)660 / QP 200Wp | -0.35 | 35.6 | 7.88 | 200 | 27.3 | 7.35
795 | Energy Solutions | ES(L)660 / QP 205Wp | Energy Solutions : ES(L)660 / QP 205Wp | -0.35 | 36.1 | 8 | 205 | 27.4 | 7.49
796 | Energy Solutions | ES(L)660 / QP 210Wp | Energy Solutions : ES(L)660 / QP 210Wp | -0.35 | 36.1 | 8.27 | 210 | 27.4 | 7.71
797 | Energy Solutions | ES(L)660 / QP 215Wp | Energy Solutions : ES(L)660 / QP 215Wp | -0.35 | 36.1 | 8.4 | 215 | 28 | 7.8
798 | Energy Solutions | ES(L)660 / QP 220Wp | Energy Solutions : ES(L)660 / QP 220Wp | -0.35 | 36.4 | 8.4 | 220 | 28 | 7.9
799 | Energy Solutions | ES(L)660 / QP 225Wp | Energy Solutions : ES(L)660 / QP 225Wp | -0.35 | 36.4 | 8.55 | 225 | 28 | 8.03
800 | Energy Solutions | ES(L)660 / QP 230Wp | Energy Solutions : ES(L)660 / QP 230Wp | -0.35 | 36.4 | 7.79 | 230 | 28.2 | 8.22
801 | EPV | SolarCompany EPV 40 | EPV : SolarCompany EPV 40 | -0.28 | 59 | 1.17 | 40 | 44 | 0.92
802 | EQ Solar Wuxi | EQS175D-24 | EQ Solar Wuxi : EQS175D-24 | -0.38 | 44.5 | 5.41 | 175 | 35.4 | 4.94
803 | EQ Solar Wuxi | EQS240D-24 | EQ Solar Wuxi : EQS240D-24 | -0.38 | 43.2 | 7.7 | 240 | 34.3 | 7
804 | EQ Solar Wuxi | EQS250D-24 | EQ Solar Wuxi : EQS250D-24 | -0.38 | 43.2 | 7.82 | 250 | 34.4 | 7.27
805 | EQ Solar Wuxi | EQS260D-24 | EQ Solar Wuxi : EQS260D-24 | -0.38 | 43.6 | 7.9 | 260 | 34.9 | 7.45
806 | EQ Solar Wuxi | EQS270D-24 | EQ Solar Wuxi : EQS270D-24 | -0.38 | 43.8 | 8.1 | 270 | 35.3 | 7.65
807 | EQ Solar Wuxi | EQS280D-24 | EQ Solar Wuxi : EQS280D-24 | -0.38 | 44.1 | 8.31 | 280 | 35.3 | 7.39
808 | EQ Solar Wuxi | EQS280P-24 240Wp | EQ Solar Wuxi : EQS280P-24 240Wp | -0.38 | 43.2 | 7.7 | 240 | 34.2 | 7.02
809 | EQ Solar Wuxi | EQS280P-24 250Wp | EQ Solar Wuxi : EQS280P-24 250Wp | -0.38 | 43.2 | 7.82 | 250 | 34.3 | 7.29
810 | EQ Solar Wuxi | EQS280P-24 260Wp | EQ Solar Wuxi : EQS280P-24 260Wp | -0.38 | 43.6 | 7.9 | 260 | 34.8 | 7.47
811 | EQ Solar Wuxi | EQS280P-24 270Wp | EQ Solar Wuxi : EQS280P-24 270Wp | -0.38 | 43.8 | 8.1 | 270 | 35.2 | 7.67
812 | EQ Solar Wuxi | EQS280P-24 280Wp | EQ Solar Wuxi : EQS280P-24 280Wp | -0.38 | 44.1 | 8.31 | 280 | 35.2 | 7.95
813 | ErSol | 160 A/24V | ErSol : 160 A/24V | -0.4 | 44.2 | 4.79 | 160 | 36.2 | 4.42
814 | ErSol | 160 B/24V | ErSol : 160 B/24V | -0.4 | 44.2 | 4.79 | 160 | 36.2 | 4.42
815 | ErSol | Blue Power 150 A | ErSol : Blue Power 150 A | -0.35 | 29.75 | 7.05 | 150 | 24.15 | 6.25
816 | ErSol | Blue Power 155 A | ErSol : Blue Power 155 A | -0.35 | 30.15 | 7.2 | 155 | 24.22 | 6.44
817 | ErSol | Blue Power 160 A | ErSol : Blue Power 160 A | -0.35 | 29.85 | 7.51 | 160 | 24.15 | 6.65
818 | ErSol | Blue Power 165 A | ErSol : Blue Power 165 A | -0.35 | 30.2 | 7.65 | 165 | 24.2 | 6.85
819 | ErSol | Blue Power 170 A | ErSol : Blue Power 170 A | -0.35 | 30.25 | 7.85 | 170 | 24.25 | 7.05
820 | ErSol | Blue Power 175 A | ErSol : Blue Power 175 A | -0.35 | 30.35 | 8 | 175 | 24.36 | 7.2
821 | ErSol | Blue Power 180 A | ErSol : Blue Power 180 A | -0.35 | 30.55 | 8.2 | 180 | 24.43 | 7.4
822 | ERSOL | Ganymed-M 2 busbar 220Wp | ERSOL : Ganymed-M 2 busbar 220Wp | -0.37 | 35.9 | 8.45 | 220 | 28.25 | 7.85
823 | ERSOL | Ganymed-M 2 busbar 225Wp | ERSOL : Ganymed-M 2 busbar 225Wp | -0.37 | 36 | 8.5 | 225 | 28.5 | 7.95
824 | ERSOL | Ganymed-M 2 busbar 230Wp | ERSOL : Ganymed-M 2 busbar 230Wp | -0.37 | 36.1 | 8.55 | 230 | 28.75 | 8.05
825 | ERSOL | Ganymed-M 2 busbar 235Wp | ERSOL : Ganymed-M 2 busbar 235Wp | -0.37 | 36.2 | 8.6 | 235 | 29 | 8.15
826 | ERSOL | Ganymed-M 3 busbar 220Wp | ERSOL : Ganymed-M 3 busbar 220Wp | -0.37 | 36 | 8.1 | 220 | 29.4 | 7.55
827 | ERSOL | Ganymed-M 3 busbar 225Wp | ERSOL : Ganymed-M 3 busbar 225Wp | -0.37 | 36.2 | 8.2 | 225 | 29.6 | 7.65
828 | ERSOL | Ganymed-M 3 busbar 230Wp | ERSOL : Ganymed-M 3 busbar 230Wp | -0.37 | 36.4 | 8.3 | 230 | 29.8 | 7.75
829 | ERSOL | Ganymed-M 3 busbar 235Wp | ERSOL : Ganymed-M 3 busbar 235Wp | -0.37 | 36.6 | 8.4 | 235 | 30 | 7.85
830 | ERSOL | Ganymed-M 3 busbar 240Wp | ERSOL : Ganymed-M 3 busbar 240Wp | -0.37 | 36.8 | 8.5 | 240 | 30.2 | 7.95
831 | ERSOL | Ganymed-P 195Wp | ERSOL : Ganymed-P 195Wp | -0.32 | 36.1 | 7.4 | 195 | 28.8 | 6.8
832 | ERSOL | Ganymed-P 200Wp | ERSOL : Ganymed-P 200Wp | -0.32 | 36.3 | 7.5 | 200 | 28.9 | 6.95
833 | ERSOL | Ganymed-P 205Wp | ERSOL : Ganymed-P 205Wp | -0.32 | 36.5 | 7.6 | 205 | 29 | 7.1
834 | ERSOL | Ganymed-P 210Wp | ERSOL : Ganymed-P 210Wp | -0.32 | 36.7 | 7.7 | 210 | 29.1 | 7.25
835 | ERSOL | Ganymed-P 215Wp | ERSOL : Ganymed-P 215Wp | -0.32 | 36.9 | 7.8 | 215 | 29.2 | 7.4
836 | ERSOL | Ganymed-P 220Wp | ERSOL : Ganymed-P 220Wp | -0.32 | 37.1 | 7.9 | 220 | 29.3 | 7.55
837 | ERSOL | Io-M 180Wp | ERSOL : Io-M 180Wp | -0.37 | 28.9 | 8.4 | 180 | 23.4 | 7.8
838 | ERSOL | Io-M 185Wp | ERSOL : Io-M 185Wp | -0.37 | 29.1 | 8.45 | 185 | 23.7 | 7.85
839 | ERSOL | Io-M 190Wp | ERSOL : Io-M 190Wp | -0.37 | 29.3 | 8.5 | 190 | 24.1 | 7.9
840 | ERSOL | Io-M 195Wp | ERSOL : Io-M 195Wp | -0.37 | 29.5 | 8.55 | 195 | 24.6 | 7.95
841 | ERSOL | Io-P 145Wp | ERSOL : Io-P 145Wp | -0.32 | 28.95 | 7.6 | 145 | 23.3 | 6.3
842 | ERSOL | Io-P 150Wp | ERSOL : Io-P 150Wp | -0.32 | 29.1 | 7.65 | 150 | 23.4 | 6.45
843 | ERSOL | Io-P 155Wp | ERSOL : Io-P 155Wp | -0.32 | 29.15 | 7.7 | 155 | 23.5 | 6.6
844 | ERSOL | Io-P 160Wp | ERSOL : Io-P 160Wp | -0.32 | 29.2 | 7.8 | 160 | 23.6 | 6.85
845 | ERSOL | Io-P 165Wp | ERSOL : Io-P 165Wp | -0.32 | 29.3 | 7.85 | 165 | 23.7 | 7
846 | ERSOL | Io-P 170Wp | ERSOL : Io-P 170Wp | -0.32 | 29.45 | 7.9 | 170 | 23.8 | 7.15
847 | ERSOL | Io-P 175Wp | ERSOL : Io-P 175Wp | -0.32 | 29.6 | 7.95 | 175 | 23.9 | 7.35
848 | ERSOL | Io-P 180Wp | ERSOL : Io-P 180Wp | -0.32 | 29.8 | 8 | 180 | 24 | 7.5
849 | ERSOL | Nova-T 75Wp | ERSOL : Nova-T 75Wp | -0.28 | 135 | 1.1 | 75 | 93 | 0.81
850 | ERSOL | Nova-T 80Wp | ERSOL : Nova-T 80Wp | -0.28 | 137 | 1.11 | 80 | 95 | 0.85
851 | ERSOL | Nova-T 85Wp | ERSOL : Nova-T 85Wp | -0.28 | 139 | 1.12 | 85 | 97 | 0.88
852 | ERSOL | Nova-T 90Wp | ERSOL : Nova-T 90Wp | -0.28 | 141 | 1.13 | 90 | 99 | 0.9
853 | Ersol | P-190 | Ersol : P-190 | -0.32 | 35.2 | 7.85 | 190 | 26.75 | 7.1
854 | Ersol | P-195 | Ersol : P-195 | -0.32 | 35.6 | 7.93 | 195 | 27.25 | 7.15
855 | Ersol | P-200 | Ersol : P-200 | -0.32 | 36 | 8 | 200 | 27.5 | 7.27
856 | Ersol | P-205 | Ersol : P-205 | -0.32 | 36.4 | 8.07 | 205 | 27.75 | 7.38
857 | Ersol | P-210 | Ersol : P-210 | -0.32 | 36.8 | 8.15 | 210 | 28 | 7.5
858 | ET Solar | ET-M572150 150Wp | ET Solar : ET-M572150 150Wp | -0.34 | 43.3 | 4.79 | 150 | 34.5 | 4.35
859 | ET Solar | ET-M572155 155Wp | ET Solar : ET-M572155 155Wp | -0.34 | 43.3 | 7.98 | 155 | 35.2 | 4.4
860 | ET Solar | ET-M572160 160Wp | ET Solar : ET-M572160 160Wp | -0.34 | 43.9 | 5.07 | 160 | 35.62 | 4.49
861 | ET Solar | ET-M572165 165Wp | ET Solar : ET-M572165 165Wp | -0.34 | 44.12 | 5.19 | 165 | 35.8 | 4.6
862 | ET Solar | ET-M572170 170Wp | ET Solar : ET-M572170 170Wp | -0.34 | 44.16 | 5.3 | 170 | 36.13 | 4.71
863 | ET Solar | ET-M572175 175Wp | ET Solar : ET-M572175 175Wp | -0.34 | 44.25 | 5.5 | 175 | 36.24 | 4.83
864 | ET Solar | ET-M572180 180Wp | ET Solar : ET-M572180 180Wp | -0.34 | 43.92 | 5.33 | 180 | 36.58 | 4.91
865 | ET Solar | ET-M572185 185Wp | ET Solar : ET-M572185 185Wp | -0.34 | 44.06 | 5.46 | 185 | 36.72 | 5.04
866 | ET Solar | ET-M572190 190Wp | ET Solar : ET-M572190 190Wp | -0.336 | 44.85 | 5.48 | 190 | 37.23 | 5.1
867 | ET Solar | ET-M572195 195Wp | ET Solar : ET-M572195 195Wp | -0.336 | 45.2 | 5.75 | 195 | 37.65 | 5.18
868 | ET Solar | ET-P636115 115Wp | ET Solar : ET-P636115 115Wp | -0.346 | 21.75 | 7.55 | 115 | 17.2 | 6.68
869 | ET Solar | ET-P636120 120Wp | ET Solar : ET-P636120 120Wp | -0.346 | 21.75 | 7.63 | 120 | 17.4 | 6.89
870 | ET Solar | ET-P636125 125Wp | ET Solar : ET-P636125 125Wp | -0.346 | 21.75 | 7.8 | 125 | 17.4 | 7.18
871 | ET Solar | ET-P636130 130Wp | ET Solar : ET-P636130 130Wp | -0.346 | 21.75 | 8.1 | 130 | 17.41 | 7.47
872 | ET Solar | ET-P636135 135Wp | ET Solar : ET-P636135 135Wp | -0.346 | 21.96 | 8.41 | 135 | 17.6 | 7.76
873 | ET Solar | ET-P636140 140Wp | ET Solar : ET-P636140 140Wp | -0.346 | 21.96 | 8.41 | 140 | 17.6 | 7.95
874 | ET Solar | ET-P636145 145Wp | ET Solar : ET-P636145 145Wp | -0.346 | 21.96 | 8.5 | 145 | 17.8 | 8.15
875 | ET Solar | ET-P648155 155Wp | ET Solar : ET-P648155 155Wp | -0.346 | 29 | 7.6 | 155 | 23 | 6.73
876 | ET Solar | ET-P648160 160Wp | ET Solar : ET-P648160 160Wp | -0.346 | 29 | 7.8 | 160 | 23 | 6.95
877 | ET Solar | ET-P648165 165Wp | ET Solar : ET-P648165 165Wp | -0.346 | 29 | 7.9 | 165 | 23 | 7.17
878 | ET Solar | ET-P648170 170Wp | ET Solar : ET-P648170 170Wp | -0.346 | 29 | 8.1 | 170 | 23 | 7.39
879 | ET Solar | ET-P648175 175Wp | ET Solar : ET-P648175 175Wp | -0.346 | 29.04 | 8.1 | 175 | 23.2 | 7.54
880 | ET Solar | ET-P648180 180Wp | ET Solar : ET-P648180 180Wp | -0.346 | 29.04 | 8.1 | 180 | 23.5 | 7.66
881 | ET Solar | ET-P648185 185Wp | ET Solar : ET-P648185 185Wp | -0.346 | 29.04 | 8.41 | 185 | 23.5 | 7.87
882 | ET Solar | ET-P648190 190Wp | ET Solar : ET-P648190 190Wp | -0.346 | 29.2 | 8.41 | 190 | 23.5 | 8.08
883 | ET Solar | ET-P648195 195Wp | ET Solar : ET-P648195 195Wp | -0.346 | 29.2 | 8.5 | 195 | 23.5 | 8.29
884 | ET Solar | ET-P654180 180Wp | ET Solar : ET-P654180 180Wp | -0.34 | 32.35 | 7.6 | 180 | 26.45 | 6.81
885 | ET Solar | ET-P654185 185Wp | ET Solar : ET-P654185 185Wp | -0.34 | 32.35 | 7.7 | 185 | 26.45 | 6.99
886 | ET Solar | ET-P654190 190Wp | ET Solar : ET-P654190 190Wp | -0.34 | 32.5 | 7.72 | 190 | 26.78 | 7.1
887 | ET Solar | ET-P654195 195Wp | ET Solar : ET-P654195 195Wp | -0.346 | 32.75 | 7.98 | 195 | 27 | 7.22
888 | ET Solar | ET-P654200 200Wp | ET Solar : ET-P654200 200Wp | -0.34 | 32.72 | 7.86 | 200 | 27.21 | 7.36
889 | ET Solar | ET-P654205 205Wp | ET Solar : ET-P654205 205Wp | -0.346 | 32.8 | 8.1 | 205 | 27.3 | 7.5
890 | ET Solar | ET-P654210 210Wp | ET Solar : ET-P654210 210Wp | -0.346 | 32.93 | 8.3 | 210 | 27.45 | 7.63
891 | ET Solar | ET-P654215 215Wp | ET Solar : ET-P654215 215Wp | -0.346 | 33.2 | 8.5 | 215 | 27.54 | 7.81
892 | ET Solar | ET-P660200 200Wp | ET Solar : ET-P660200 200Wp | -0.346 | 36 | 7.71 | 200 | 28.75 | 6.95
893 | ET Solar | ET-P660205 205Wp | ET Solar : ET-P660205 205Wp | -0.346 | 36 | 7.8 | 205 | 28.75 | 7.13
894 | ET Solar | ET-P660210 210Wp | ET Solar : ET-P660210 210Wp | -0.346 | 36 | 7.99 | 210 | 28.75 | 7.3
895 | ET Solar | ET-P660215 215Wp | ET Solar : ET-P660215 215Wp | -0.346 | 36 | 8.1 | 215 | 29 | 7.41
896 | ET Solar | ET-P660220 220Wp | ET Solar : ET-P660220 220Wp | -0.346 | 36.3 | 8.1 | 220 | 29 | 7.58
897 | ET Solar | ET-P660225 225Wp | ET Solar : ET-P660225 225Wp | -0.346 | 36.3 | 8.1 | 225 | 29 | 7.75
898 | ET Solar | ET-P660230 230Wp | ET Solar : ET-P660230 230Wp | -0.346 | 36.5 | 8.3 | 230 | 29.4 | 7.82
899 | ET Solar | ET-P660235 235Wp | ET Solar : ET-P660235 235Wp | -0.346 | 36.5 | 8.3 | 235 | 29.4 | 7.99
900 | ET Solar | ET-P660240 240Wp | ET Solar : ET-P660240 240Wp | -0.346 | 36.5 | 8.5 | 240 | 29.4 | 8.16
901 | ET Solar | ET-P672155 155Wp | ET Solar : ET-P672155 155Wp | -0.397 | 43.3 | 4.98 | 155 | 35.2 | 4.4
902 | ET Solar | ET-P672180 180Wp | ET Solar : ET-P672180 180Wp | -0.397 | 44.6 | 5.61 | 180 | 36.3 | 4.95
903 | ET Solar | ET-P672185 185Wp | ET Solar : ET-P672185 185Wp | -0.397 | 44.6 | 5.8 | 185 | 36.3 | 5.09
904 | ET Solar | ET-P672240 240Wp | ET Solar : ET-P672240 240Wp | -0.346 | 43.85 | 7.63 | 240 | 34.95 | 6.88
905 | ET Solar | ET-P672245 245Wp | ET Solar : ET-P672245 245Wp | -0.346 | 43.85 | 7.7 | 245 | 34.95 | 7.01
906 | ET Solar | ET-P672250 250Wp | ET Solar : ET-P672250 250Wp | -0.346 | 43.88 | 7.81 | 250 | 35.2 | 7.12
907 | ET Solar | ET-P672255 255Wp | ET Solar : ET-P672255 255Wp | -0.346 | 43.88 | 7.85 | 255 | 35.2 | 7.23
908 | ET Solar | ET-P672260 260Wp | ET Solar : ET-P672260 260Wp | -0.34 | 43.49 | 7.79 | 260 | 36 | 7.23
909 | ET Solar | ET-P672265 265Wp | ET Solar : ET-P672265 265Wp | -0.346 | 43.63 | 7.9 | 265 | 36.4 | 7.28
910 | ET Solar | ET-P672270 270Wp | ET Solar : ET-P672270 270Wp | -0.346 | 43.63 | 7.9 | 270 | 36.4 | 7.42
911 | ET Solar | ET-P672275 275Wp | ET Solar : ET-P672275 275Wp | -0.346 | 43.78 | 7.96 | 275 | 36.72 | 7.49
912 | ET Solar | ET-P672280 280Wp | ET Solar : ET-P672280 280Wp | -0.346 | 43.78 | 7.97 | 280 | 36.72 | 7.63
913 | Eurener | MEPV 220 | Eurener : MEPV 220 | -0.38 | 36.81 | 8.35 | 220 | 29.1 | 7.61
914 | Eurener | MEPV 230 | Eurener : MEPV 230 | -0.38 | 36.83 | 8.45 | 230 | 29.23 | 7.75
915 | Eurener | PEPV 190 | Eurener : PEPV 190 | -0.38 | 35.75 | 7.29 | 190 | 28.25 | 6.66
916 | Eurener | PEPV 200 | Eurener : PEPV 200 | -0.38 | 36.11 | 7.32 | 200 | 28.71 | 6.78
917 | Eurener | PEPV 210 | Eurener : PEPV 210 | -0.38 | 36.72 | 7.65 | 210 | 28.93 | 7.6
918 | Eurosolare | M 200 | Eurosolare : M 200 | -0.363 | 21.2 | 1.6 | 24 | 17.5 | 1.43
919 | Eurosolare | M 500 A | Eurosolare : M 500 A | -0.349 | 21.8 | 3.41 | 52.5 | 17.5 | 3.15
920 | Eurosolare | M 510 A | Eurosolare : M 510 A | -0.355 | 21.4 | 3.25 | 48 | 17 | 2.95
921 | Eurosolare | MM 250/A | Eurosolare : MM 250/A | -0.362 | 21.3 | 1.6 | 25 | 17.2 | 1.45
922 | Eurosolare | P 500 A | Eurosolare : P 500 A | -0.365 | 21.1 | 3.2 | 47 | 17.2 | 2.9
923 | Eurosolare | P 500 D | Eurosolare : P 500 D | -0.367 | 21 | 6.4 | 90 | 17 | 5.6
924 | Eurosolare | P 510 A | Eurosolare : P 510 A | -0.367 | 21 | 3.15 | 42 | 16.9 | 2.65
925 | Eurosolare | PL 120 | Eurosolare : PL 120 | -0.365 | 37.5 | 4.5 | 115 | 30.4 | 4
926 | Eurosolare | PL 120 B | Eurosolare : PL 120 B | -0.368 | 37.2 | 4.4 | 115 | 29.6 | 3.88
927 | Eurosolare | PL 160 | Eurosolare : PL 160 | -0.376 | 42.5 | 4.55 | 138 | 35 | 4.14
928 | Eurosolare | PL 800 | Eurosolare : PL 800 | -0.363 | 21.2 | 4.5 | 70 | 17.2 | 4.2
929 | Eurosolare | PL 800 D | Eurosolare : PL 800 D | -0.365 | 21.1 | 9 | 134 | 17 | 8.25
930 | Eurosolare | PL 810 | Eurosolare : PL 810 | -0.367 | 21 | 4.4 | 64 | 16.9 | 4
931 | Ever Step | # 892 TGM 750 - 12 V | Ever Step : # 892 TGM 750 - 12 V | -0.4 | 18.2 | 0.75 | 13 | 17.5 | 0.67
932 | Ever Step | # 893 TGM 1000 - 12 V | Ever Step : # 893 TGM 1000 - 12 V | -0.4 | 18.2 | 1 | 17 | 17.5 | 0.9
933 | Ever Step | # 893 TGM 500 - 24 (72) | Ever Step : # 893 TGM 500 - 24 (72) | -0.4 | 36 | 0.5 | 18 | 33.1 | 0.4
934 | Ever Step | # 894 TGM 1500 - 12 V | Ever Step : # 894 TGM 1500 - 12 V | -0.4 | 18.2 | 1.5 | 25 | 17.5 | 1.4
935 | Ever Step | # 894 TGM 780 - 24 V (72) | Ever Step : # 894 TGM 780 - 24 V (72) | -0.4 | 36 | 0.75 | 30 | 33.7 | 0.67
936 | Evergreen solar | Cedar Line EC-110-GL | Evergreen solar : Cedar Line EC-110-GL | -0.41 | 21.3 | 7.48 | 110 | 17 | 6.47
937 | Evergreen solar | Cedar Line EC-115-GL | Evergreen solar : Cedar Line EC-115-GL | -0.41 | 21.3 | 7.62 | 115 | 17.1 | 6.73
938 | Evergreen solar | Cedar Line EC-120-GL | Evergreen solar : Cedar Line EC-120-GL | -0.41 | 21.5 | 7.68 | 120 | 17.6 | 6.82
939 | Evergreen Solar | E-28 | Evergreen Solar : E-28 | -0.4 | 20 | 2.16 | 28 | 15.6 | 1.8
940 | Evergreen Solar | E-30 | Evergreen Solar : E-30 | -0.265 | 20 | 2.19 | 30 | 16.1 | 1.87
941 | Evergreen Solar | E-32 | Evergreen Solar : E-32 | -0.265 | 20 | 2.38 | 32 | 15.9 | 2.02
942 | Evergreen Solar | E-56 (12V) | Evergreen Solar : E-56 (12V) | -0.4 | 20 | 4.32 | 56 | 15.6 | 3.6
943 | Evergreen Solar | E-56 (24V) | Evergreen Solar : E-56 (24V) | -0.4 | 40 | 2.16 | 56 | 31.1 | 1.8
944 | Evergreen Solar | E-60 (12V) | Evergreen Solar : E-60 (12V) | -0.265 | 20 | 4.38 | 60 | 16.1 | 3.74
945 | Evergreen Solar | E-60 (24V) | Evergreen Solar : E-60 (24V) | -0.265 | 40 | 2.19 | 60 | 32.1 | 1.87
946 | Evergreen Solar | E-64 (12 V) | Evergreen Solar : E-64 (12 V) | -0.265 | 20 | 4.75 | 64 | 15.9 | 4.03
947 | Evergreen Solar | E-64 (24 V) | Evergreen Solar : E-64 (24 V) | -0.265 | 20 | 2.38 | 64 | 31.7 | 2.02
948 | Evergreen Solar | EC-102 (12V) | Evergreen Solar : EC-102 (12V) | -0.41 | 20 | 7.45 | 102 | 15.6 | 6.57
949 | Evergreen Solar | EC-102 (24V) | Evergreen Solar : EC-102 (24V) | -0.41 | 40 | 3.73 | 102 | 31.2 | 3.28
950 | Evergreen Solar | EC-110 (12 V) | Evergreen Solar : EC-110 (12 V) | -0.4 | 20 | 7.8 | 110 | 16.9 | 6.84
951 | Evergreen Solar | EC-110 (24V) | Evergreen Solar : EC-110 (24V) | -0.41 | 40 | 3.84 | 110 | 32.7 | 3.36
952 | Evergreen Solar | EC-115 (12V) | Evergreen Solar : EC-115 (12V) | -0.41 | 20 | 7.71 | 115 | 16.5 | 6.97
953 | Evergreen Solar | EC-115 (24V) | Evergreen Solar : EC-115 (24V) | -0.41 | 40 | 3.86 | 115 | 33 | 3.48
954 | Evergreen Solar | EC-47 | Evergreen Solar : EC-47 | -0.4 | 20 | 3.65 | 47 | 15.5 | 3.04
955 | Evergreen Solar | EC-51 | Evergreen Solar : EC-51 | -0.4 | 20 | 3.73 | 51 | 15.6 | 3.28
956 | Evergreen Solar | EC-55 | Evergreen Solar : EC-55 | -0.4 | 20 | 3.9 | 55 | 16.1 | 3.42
957 | Evergreen Solar | EC-94 (12 V) | Evergreen Solar : EC-94 (12 V) | -0.4 | 20 | 7.29 | 94 | 15.5 | 6.08
958 | Evergreen Solar | ES-A-190-fa2 | Evergreen Solar : ES-A-190-fa2 | -0.32 | 22 | 11.8 | 190 | 17.4 | 10.92
959 | Evergreen Solar | ES-A-195-fa2 | Evergreen Solar : ES-A-195-fa2 | -0.32 | 22.3 | 11.9 | 195 | 17.8 | 10.96
960 | Evergreen solar | ES-A-200 | Evergreen solar : ES-A-200 | -0.34 | 22.4 | 12 | 200 | 18.1 | 11.05
961 | Evergreen Solar | ES-A-200-fa2 | Evergreen Solar : ES-A-200-fa2 | -0.32 | 22.5 | 12 | 200 | 18.1 | 11.05
962 | Evergreen Solar | ES-A-200-fa3 | Evergreen Solar : ES-A-200-fa3 | -0.31 | 22.6 | 11.8 | 200 | 18.1 | 11.05
963 | Evergreen solar | ES-A-205 | Evergreen solar : ES-A-205 | -0.34 | 22.8 | 12.05 | 205 | 18.4 | 11.15
964 | Evergreen Solar | ES-A-205-fa2 | Evergreen Solar : ES-A-205-fa2 | -0.32 | 22.8 | 12.1 | 205 | 18.4 | 11.15
965 | Evergreen Solar | ES-A-205-fa3 | Evergreen Solar : ES-A-205-fa3 | -0.31 | 22.7 | 11.93 | 205 | 18.2 | 11.27
966 | Evergreen solar | ES-A-210 | Evergreen solar : ES-A-210 | -0.34 | 23.1 | 12.1 | 210 | 18.7 | 11.2
967 | Evergreen Solar | ES-A-210-fa2 | Evergreen Solar : ES-A-210-fa2 | -0.32 | 23.1 | 12.2 | 210 | 18.7 | 11.23
968 | Evergreen Solar | ES-A-210-fa3 | Evergreen Solar : ES-A-210-fa3 | -0.31 | 22.8 | 12.11 | 210 | 18.3 | 11.48
969 | Evergreen solar | ES-E-210 | Evergreen solar : ES-E-210 | -0.31 | 35.4 | 8.01 | 210 | 28.7 | 7.32
970 | Evergreen solar | ES-E-215 | Evergreen solar : ES-E-215 | -0.31 | 35.6 | 8.12 | 215 | 29 | 7.43
971 | Evergreen solar | ES-E-220 | Evergreen solar : ES-E-220 | -0.31 | 35.9 | 8.22 | 220 | 29.2 | 7.54
972 | Evergreen solar | Spuce Line ES-170-RL | Evergreen solar : Spuce Line ES-170-RL | -0.34 | 32.4 | 7.55 | 170 | 25.3 | 6.72
973 | Evergreen solar | Spuce Line ES-180-RL | Evergreen solar : Spuce Line ES-180-RL | -0.34 | 32.6 | 7.78 | 180 | 25.9 | 6.95
974 | Evergreen solar | Spuce Line ES-190-RL | Evergreen solar : Spuce Line ES-190-RL | -0.34 | 32.8 | 8.05 | 190 | 26.7 | 7.12
975 | Evergreen solar | Spuce Line ES-195-RL | Evergreen solar : Spuce Line ES-195-RL | -0.34 | 32.9 | 8.15 | 195 | 27.1 | 7.2
976 | First Solar | FS-265 | First Solar : FS-265 | -0.25 | 87 | 1.17 | 65 | 63.7 | 1.02
977 | First Solar | FS-267 | First Solar : FS-267 | -0.25 | 87 | 1.18 | 67.5 | 64.6 | 1.05
978 | First Solar | FS-270 | First Solar : FS-270 | -0.25 | 89 | 1.19 | 70 | 67.1 | 1.04
979 | First Solar | FS-272 | First Solar : FS-272 | -0.25 | 90 | 1.19 | 72.5 | 67.9 | 1.07
980 | First Solar | FS-275 | First Solar : FS-275 | -0.25 | 82 | 1.2 | 75 | 69.4 | 1.08
981 | First Solar | FS-277 | First Solar : FS-277 | -0.25 | 90.5 | 1.22 | 77.5 | 69.9 | 1.11
982 | First Solar | FS-280 | First Solar : FS-280 | -0.25 | 91.5 | 1.22 | 80 | 71.2 | 1.12
983 | First Solar | FS-370 | First Solar : FS-370 | -0.27 | 60.6 | 1.74 | 70 | 48.1 | 1.46
984 | First Solar | FS-372 | First Solar : FS-372 | -0.27 | 61.4 | 1.75 | 72.5 | 49.5 | 1.46
985 | First Solar | FS-375 | First Solar : FS-375 | -0.27 | 61.6 | 1.76 | 75 | 49.8 | 1.51
986 | First Solar | FS-377 | First Solar : FS-377 | -0.27 | 61.7 | 1.75 | 77.5 | 50.4 | 1.54
987 | First Solar | FS-380 | First Solar : FS-380 | -0.27 | 61.7 | 1.76 | 80 | 50.7 | 1.58
988 | First Solar | FS-50 | First Solar : FS-50 | -0.29 | 85 | 1.08 | 50 | 85 | 0.87
989 | First Solar | FS-55 | First Solar : FS-55 | -0.29 | 88 | 1.13 | 55 | 61 | 0.9
990 | First Solar | FS-57 | First Solar : FS-57 | -0.29 | 89 | 1.13 | 57.5 | 62 | 0.93
991 | First Solar | FS-60 | First Solar : FS-60 | -0.29 | 90 | 1.14 | 60 | 64 | 0.94
992 | First Solar | FS-62 | First Solar : FS-62 | -0.29 | 91 | 1.14 | 62.5 | 64 | 0.98
993 | First Solar | FS-65 | First Solar : FS-65 | -0.29 | 91 | 1.15 | 65 | 65 | 1
994 | Flabeg | Multisol 150 (140 W) | Flabeg : Multisol 150 (140 W) | -0.349 | 41.8 | 4.65 | 140 | 34.2 | 4.09
995 | Flabeg | Multisol 150 (145 W) | Flabeg : Multisol 150 (145 W) | -0.335 | 43.6 | 4.45 | 145 | 36 | 4.02
996 | Flabeg | Multisol 150 (150 W) | Flabeg : Multisol 150 (150 W) | -0.335 | 43.6 | 4.49 | 150 | 36.4 | 4.13
997 | Flabeg | Optisol SFM128Be | Flabeg : Optisol SFM128Be | -0.608 | 37.8 | 9.4 | 230 | 30.1 | 8.3
998 | Flabeg | Optisol SFM128Be 2000 | Flabeg : Optisol SFM128Be 2000 | -0.446 | 37.8 | 9.4 | 250 | 30.1 | 8.3
999 | Flabeg | Optisol SFM144Ha EFG | Flabeg : Optisol SFM144Ha EFG | -0.4 | 41.8 | 6.33 | 180 | 33.5 | 5.53
1000 | Flabeg | Optisol SFM144Ha poly | Flabeg : Optisol SFM144Ha poly | -0.4 | 42.6 | 5.64 | 184 | 34.2 | 5.4
1001 | Flabeg | Optisol SFM144Hx | Flabeg : Optisol SFM144Hx | -0.226 | 84.2 | 3.9 | 230 | 71.4 | 3.5
1002 | Flabeg | Optisol SFM144Hx 2000 | Flabeg : Optisol SFM144Hx 2000 | -0.446 | 84.2 | 3.9 | 250 | 71.4 | 3.5
1003 | Flabeg | Optisol SFM36He | Flabeg : Optisol SFM36He | -0.446 | 21.1 | 4.6 | 70 | 17.1 | 4.1
1004 | Flabeg | Optisol SFM72Bx | Flabeg : Optisol SFM72Bx | -0.4 | 42.2 | 4.6 | 144 | 34.2 | 4.2
1005 | Flabeg | Optisol SFM72Ha | Flabeg : Optisol SFM72Ha | -0.446 | 42.6 | 2.82 | 94 | 34.2 | 2.75
1006 | Flabeg | Optisol SFM72Hx | Flabeg : Optisol SFM72Hx | -0.475 | 42.1 | 3.9 | 125 | 35.7 | 3.5
1007 | Flabeg | Optisol SFM72Qa | Flabeg : Optisol SFM72Qa | -0.446 | 42.6 | 2.82 | 94 | 34.2 | 2.75
1008 | Flexcell | FLX-MO100 101Wp | Flexcell : FLX-MO100 101Wp | -0.237 | 64.1 | 3 | 101 | 45.4 | 2.23
1009 | Flexcell | FLX-TO200 200Wp | Flexcell : FLX-TO200 200Wp | -0.237 | 96 | 4 | 200 | 68 | 2.95
1010 | Fluitecnik | FTS-200P | Fluitecnik : FTS-200P | -0.33 | 36.05 | 7.85 | 200 | 27.78 | 7.2
1011 | Fluitecnik | FTS-210P | Fluitecnik : FTS-210P | -0.33 | 36.5 | 8.09 | 210 | 28.23 | 7.44
1012 | Fluitecnik | FTS-220P | Fluitecnik : FTS-220P | -0.33 | 36.77 | 8.37 | 220 | 28.5 | 7.72
1013 | Fluitecnik | FTS-230P | Fluitecnik : FTS-230P | -0.33 | 37.1 | 8.63 | 230 | 28.83 | 7.98
1014 | Formaro | FM130m | Formaro : FM130m | -0.34 | 21.8 | 8.06 | 130 | 17.3 | 7.52
1015 | Formaro | FM130m | Formaro : FM130m | -0.34 | 22.2 | 8.36 | 140 | 18.03 | 7.77
1016 | Formaro | FM130p | Formaro : FM130p | -0.33 | 21.8 | 8.06 | 130 | 17.3 | 7.52
1017 | Formaro | FM130p | Formaro : FM130p | -0.33 | 22.2 | 8.36 | 140 | 18.03 | 7.77
1018 | Formaro | FM150m | Formaro : FM150m | -0.33 | 25.36 | 8.02 | 150 | 20.06 | 7.49
1019 | Formaro | FM150m | Formaro : FM150m | -0.33 | 25.76 | 8.27 | 160 | 20.79 | 7.7
1020 | Formaro | FM150p | Formaro : FM150p | -0.33 | 25.36 | 8.02 | 150 | 20.06 | 7.49
1021 | Formaro | FM150p | Formaro : FM150p | -0.33 | 25.76 | 8.27 | 160 | 20.79 | 7.7
1022 | Formaro | FM170m | Formaro : FM170m | -0.34 | 28.93 | 7.99 | 170 | 22.82 | 7.46
1023 | Formaro | FM170m | Formaro : FM170m | -0.34 | 29.33 | 8.21 | 180 | 23.55 | 7.65
1024 | Formaro | FM170p | Formaro : FM170p | -0.34 | 28.93 | 7.99 | 170 | 22.82 | 7.46
1025 | Formaro | FM170p | Formaro : FM170p | -0.34 | 29.33 | 8.21 | 180 | 23.55 | 7.65
1026 | Formaro | FM210m | Formaro : FM210m | -0.34 | 32.5 | 7.96 | 190 | 25.58 | 7.44
1027 | Formaro | FM210m | Formaro : FM210m | -0.34 | 32.89 | 8.16 | 200 | 26.31 | 7.6
1028 | Formaro | FM210m | Formaro : FM210m | -0.34 | 33.29 | 8.36 | 210 | 27.05 | 7.77
1029 | Formaro | FM210p | Formaro : FM210p | -0.34 | 32.5 | 7.96 | 190 | 25.58 | 7.44
1030 | Formaro | FM210p | Formaro : FM210p | -0.34 | 32.89 | 8.16 | 200 | 26.31 | 7.6
1031 | Formaro | FM210p | Formaro : FM210p | -0.34 | 33.29 | 8.36 | 210 | 27.05 | 7.77
1032 | Formaro | FM230m | Formaro : FM230m | -0.34 | 36.46 | 8.12 | 220 | 29.07 | 7.57
1033 | Formaro | FM230m | Formaro : FM230m | -0.34 | 36.86 | 8.3 | 230 | 29.81 | 7.72
1034 | Formaro | FM230m | Formaro : FM230m | -0.34 | 37.41 | 8.48 | 240 | 29.92 | 8.02
1035 | Formaro | FM230p | Formaro : FM230p | -0.34 | 36.46 | 8.12 | 220 | 29.07 | 7.57
1036 | Formaro | FM230p | Formaro : FM230p | -0.34 | 36.86 | 8.3 | 230 | 29.81 | 7.72
1037 | Formaro | FM230p | Formaro : FM230p | -0.34 | 37.26 | 8.48 | 240 | 30.54 | 7.87
1038 | Formaro | FM-BIPV 100m | Formaro : FM-BIPV 100m | -0.34 | 17.94 | 7.58 | 100 | 14.02 | 7.13
1039 | Formaro | FM-BIPV 100m | Formaro : FM-BIPV 100m | -0.34 | 18.45 | 8.02 | 110 | 14.56 | 7.55
1040 | Formaro | FM-BIPV 100p | Formaro : FM-BIPV 100p | -0.34 | 17.97 | 7.57 | 100 | 14.17 | 7.06
1041 | Formaro | FM-BIPV 100p | Formaro : FM-BIPV 100p | -0.34 | 18.53 | 7.99 | 110 | 14.59 | 7.54
1042 | Formaro | FM-BIPV 120m | Formaro : FM-BIPV 120m | -0.34 | 21.7 | 7.65 | 120 | 16.7 | 7.19
1043 | Formaro | FM-BIPV 120m | Formaro : FM-BIPV 120m | -0.34 | 22.1 | 7.92 | 130 | 17.55 | 7.41
1044 | Formaro | FM-BIPV 120p | Formaro : FM-BIPV 120p | -0.34 | 21.57 | 7.57 | 120 | 17 | 7.06
1045 | Formaro | FM-BIPV 120p | Formaro : FM-BIPV 120p | -0.34 | 22.1 | 7.92 | 130 | 17.55 | 7.41
1046 | Formaro | FM-BIPV 140m | Formaro : FM-BIPV 140m | -0.34 | 25.12 | 7.58 | 140 | 19.62 | 7.13
1047 | Formaro | FM-BIPV 140m | Formaro : FM-BIPV 140m | -0.34 | 25.66 | 7.9 | 150 | 20.31 | 7.39
1048 | Formaro | FM-BIPV 140p | Formaro : FM-BIPV 140p | -0.34 | 25.16 | 7.57 | 140 | 19.84 | 7.06
1049 | Formaro | FM-BIPV 140p | Formaro : FM-BIPV 140p | -0.34 | 25.66 | 7.9 | 150 | 20.31 | 7.39
1050 | Formaro | FM-BIPV 160m | Formaro : FM-BIPV 160m | -0.34 | 28.75 | 7.57 | 160 | 22.67 | 7.06
1051 | Formaro | FM-BIPV 160m | Formaro : FM-BIPV 160m | -0.34 | 29.32 | 7.84 | 170 | 23.22 | 7.32
1052 | Formaro | FM-BIPV 160p | Formaro : FM-BIPV 160p | -0.34 | 28.75 | 7.57 | 160 | 22.67 | 7.06
1053 | Formaro | FM-BIPV 160p | Formaro : FM-BIPV 160p | -0.34 | 29.32 | 7.84 | 170 | 23.22 | 7.32
1054 | Formaro | FM-BIPV 180m | Formaro : FM-BIPV 180m | -0.34 | 32.35 | 7.57 | 180 | 25.51 | 7.06
1055 | Formaro | FM-BIPV 180m | Formaro : FM-BIPV 180m | -0.34 | 32.77 | 7.8 | 190 | 26.07 | 7.29
1056 | Formaro | FM-BIPV 180p | Formaro : FM-BIPV 180p | -0.34 | 32.35 | 7.57 | 180 | 25.51 | 7.06
1057 | Formaro | FM-BIPV 180p | Formaro : FM-BIPV 180p | -0.34 | 32.77 | 7.8 | 190 | 26.07 | 7.29
1058 | Formaro | FM-BIPV 200m | Formaro : FM-BIPV 200m | -0.34 | 35.94 | 7.61 | 200 | 28.34 | 7.08
1059 | Formaro | FM-BIPV 200m | Formaro : FM-BIPV 200m | -0.34 | 36.65 | 7.71 | 210 | 29.02 | 7.24
1060 | Formaro | FM-BIPV 200m | Formaro : FM-BIPV 200m | -0.34 | 37.11 | 7.96 | 220 | 30.05 | 7.32
1061 | Formaro | FM-BIPV 200p | Formaro : FM-BIPV 200p | -0.34 | 35.94 | 7.61 | 200 | 28.34 | 7.08
1062 | Formaro | FM-BIPV 200p | Formaro : FM-BIPV 200p | -0.34 | 36.65 | 7.71 | 210 | 29.02 | 7.24
1063 | Formaro | FM-BIPV 200p | Formaro : FM-BIPV 200p | -0.34 | 37.11 | 7.96 | 220 | 30.05 | 7.32
1064 | Free Energy Europe | A11P | Free Energy Europe : A11P | -0.209 | 22 | 0.3 | 4 | 16 | 0.25
1065 | Free Energy Europe | A1206P | Free Energy Europe : A1206P | -0.209 | 22 | 0.13 | 1.8 | 16 | 0.11
1066 | Free Energy Europe | A13P | Free Energy Europe : A13P | -0.209 | 22 | 0.9 | 12 | 16 | 0.75
1067 | Free Energy Europe | FEE-14-12 | Free Energy Europe : FEE-14-12 | -0.209 | 22.8 | 0.9 | 12 | 16 | 0.75
1068 | Free Energy Europe | FEE-20-12 | Free Energy Europe : FEE-20-12 | -0.29 | 22.8 | 1.22 | 16 | 16 | 0.99
1069 | French Energy | FE 110-TF-3E | French Energy : FE 110-TF-3E | -0.37 | 130 | 1.42 | 110 | 102.7 | 1.07
1070 | FVG Energy | 160 M - MC | FVG Energy : 160 M - MC | -0.35 | 42.8 | 5.15 | 160 | 34.9 | 4.6
1071 | FVG Energy | 165 M - MC | FVG Energy : 165 M - MC | -0.347 | 43.2 | 5.2 | 165 | 35.6 | 4.65
1072 | FVG Energy | 170 M - MC | FVG Energy : 170 M - MC | -0.344 | 43.6 | 5.25 | 170 | 35.8 | 4.76
1073 | FVG Energy | 175 M - MC | FVG Energy : 175 M - MC | -0.342 | 43.9 | 5.3 | 175 | 36.2 | 4.85
1074 | FVG Energy | 180 M - MC | FVG Energy : 180 M - MC | -0.339 | 44.2 | 5.35 | 180 | 36.8 | 4.9
1075 | FVG Energy | 185 M - MC | FVG Energy : 185 M - MC | -0.337 | 44.5 | 5.4 | 185 | 37.5 | 4.95
1076 | FVG Energy | FVG 205P | FVG Energy : FVG 205P | -0.35 | 36.5 | 7.78 | 205 | 29.18 | 7.05
1077 | FVG Energy | FVG 210P | FVG Energy : FVG 210P | -0.35 | 36.9 | 7.9 | 210 | 29.5 | 7.12
1078 | FVG Energy | FVG 220P | FVG Energy : FVG 220P | -0.35 | 37.5 | 8.15 | 220 | 30 | 7.34
1079 | FVG Energy | FVG 230P | FVG Energy : FVG 230P | -0.35 | 37.5 | 8.51 | 230 | 30 | 7.66
1080 | FVG Energy | Mono 160M- MC | FVG Energy : Mono 160M- MC | -0.35 | 42.8 | 5.15 | 160 | 34.9 | 4.6
1081 | FVG Energy | Mono 165M- MC | FVG Energy : Mono 165M- MC | -0.35 | 43.2 | 5.2 | 165 | 35.6 | 4.65
1082 | FVG Energy | Mono 170M- MC | FVG Energy : Mono 170M- MC | -0.35 | 43.6 | 5.25 | 170 | 35.8 | 4.76
1083 | FVG Energy | Mono 175M- MC | FVG Energy : Mono 175M- MC | -0.35 | 43.9 | 5.3 | 175 | 36.2 | 4.85
1084 | FVG Energy | Mono 180M- MC | FVG Energy : Mono 180M- MC | -0.35 | 44.2 | 5.35 | 180 | 36.8 | 4.9
1085 | FVG Energy | Mono 185M- MC | FVG Energy : Mono 185M- MC | -0.35 | 44.5 | 5.4 | 185 | 37.5 | 4.95
1086 | FVG Energy | Mono 210M- MC | FVG Energy : Mono 210M- MC | -0.35 | 36.4 | 7.86 | 210 | 29.2 | 7.2
1087 | FVG Energy | Mono 215M- MC | FVG Energy : Mono 215M- MC | -0.35 | 36.6 | 7.91 | 215 | 29.5 | 7.29
1088 | FVG Energy | Mono 220M- MC | FVG Energy : Mono 220M- MC | -0.35 | 36.8 | 8 | 220 | 29.8 | 7.39
1089 | FVG Energy | Mono 225M- MC | FVG Energy : Mono 225M- MC | -0.35 | 36.9 | 8.09 | 225 | 29.9 | 7.55
1090 | FVG Energy | Mono 230M- MC | FVG Energy : Mono 230M- MC | -0.35 | 37 | 8.18 | 230 | 30 | 7.67
1091 | FVG Energy | Mono 235M- MC | FVG Energy : Mono 235M- MC | -0.35 | 37.25 | 8.28 | 235 | 30.3 | 7.77
1092 | FVG Energy | Mono 240M- MC | FVG Energy : Mono 240M- MC | -0.35 | 37.5 | 8.38 | 240 | 30.6 | 7.85
1093 | FVG Energy | Mono 245M- MC | FVG Energy : Mono 245M- MC | -0.35 | 37.75 | 8.48 | 245 | 30.8 | 7.97
1094 | FVG Energy | Mono 250M- MC | FVG Energy : Mono 250M- MC | -0.35 | 37.95 | 8.58 | 250 | 30.95 | 8.1
1095 | FVG Energy | Mono 80M- MC | FVG Energy : Mono 80M- MC | -0.33 | 22.1 | 4.87 | 80 | 18.2 | 4.4
1096 | FVG Energy | Mono 85M- MC | FVG Energy : Mono 85M- MC | -0.33 | 22.2 | 5.13 | 85 | 18.5 | 4.59
1097 | FVG Energy | Mono 90M- MC | FVG Energy : Mono 90M- MC | -0.33 | 22.3 | 5.37 | 90 | 18.5 | 4.86
1098 | FVG Energy | Poly 200P- MC | FVG Energy : Poly 200P- MC | -0.35 | 36 | 7.75 | 200 | 28.7 | 6.97
1099 | FVG Energy | Poly 205P- MC | FVG Energy : Poly 205P- MC | -0.35 | 36.2 | 7.81 | 205 | 29.2 | 7.05
1100 | FVG Energy | Poly 215P- MC | FVG Energy : Poly 215P- MC | -0.35 | 36.6 | 7.93 | 215 | 29.75 | 7.25
1101 | FVG Energy | Poly 220P- MC | FVG Energy : Poly 220P- MC | -0.35 | 36.8 | 8 | 220 | 29.8 | 7.39
1102 | FVG Energy | Poly 225P- MC | FVG Energy : Poly 225P- MC | -0.35 | 37 | 8.07 | 225 | 30 | 7.5
1103 | FVG Energy | Poly 230P- MC | FVG Energy : Poly 230P- MC | -0.35 | 37.2 | 8.14 | 230 | 30.3 | 7.6
1104 | FVG Energy | Poly 235P- MC | FVG Energy : Poly 235P- MC | -0.35 | 37.4 | 8.21 | 235 | 30.4 | 7.75
1105 | FVG Energy | Poly 240P- MC | FVG Energy : Poly 240P- MC | -0.35 | 37.6 | 8.28 | 240 | 30.5 | 7.88
1106 | FVG Energy | Poly210P- MC | FVG Energy : Poly210P- MC | -0.35 | 36.4 | 7.86 | 210 | 29.7 | 7.1
1107 | Gaia Solar A/S | GS 52 p | Gaia Solar A/S : GS 52 p | -0.379 | 20.6 | 3.7 | 52 | 16 | 3.25
1108 | Gaia Solar A/S | GS 56 p | Gaia Solar A/S : GS 56 p | -0.375 | 20.8 | 3.7 | 56 | 16.2 | 3.45
1109 | Gaia Solar A/S | GS 60 p | Gaia Solar A/S : GS 60 p | -0.371 | 21 | 4 | 60 | 16.4 | 3.65
1110 | Gaia Solar A/S | GS 64 p | Gaia Solar A/S : GS 64 p | -0.368 | 21.2 | 4.3 | 64 | 16.6 | 3.85
1111 | Gaia Solar A/S | GS 68 p | Gaia Solar A/S : GS 68 p | -0.364 | 21.4 | 4.5 | 68 | 16.8 | 4.05
1112 | Gaia Solar A/S | GS 71 p | Gaia Solar A/S : GS 71 p | -0.361 | 21.6 | 4.8 | 71 | 17 | 4.2
1113 | Gebr. Laumans | Solar-Dachziegel Rheinland | Gebr. Laumans : Solar-Dachziegel Rheinland | -0.349 | 1.82 | 3.17 | 4.55 | 1.5 | 3.03
1114 | Gebr. Laumans | Solar-Dachziegel Tiefa-XL | Gebr. Laumans : Solar-Dachziegel Tiefa-XL | -0.349 | 1.82 | 3.17 | 4.55 | 1.5 | 3.03
1115 | GESolar | GES-M150 | GESolar : GES-M150 | -0.35 | 43.2 | 4.95 | 150 | 34.2 | 4.39
1116 | GESolar | GES-M160 | GESolar : GES-M160 | -0.35 | 43.6 | 5.05 | 160 | 34.6 | 4.62
1117 | GESolar | GES-M165 | GESolar : GES-M165 | -0.35 | 43.8 | 5.1 | 165 | 34.8 | 4.74
1118 | GESolar | GES-M170 | GESolar : GES-M170 | -0.35 | 44 | 5.15 | 170 | 35 | 4.86
1119 | GESolar | GES-M175 | GESolar : GES-M175 | -0.35 | 44.2 | 5.25 | 175 | 35.2 | 4.97
1120 | GESolar | GES-M180 | GESolar : GES-M180 | -0.35 | 44.4 | 5.35 | 180 | 35.4 | 5.08
1121 | GESolar | GES-P220 | GESolar : GES-P220 | -0.34 | 37 | 8.1 | 220 | 29.5 | 7.45
1122 | GESolar | GES-P225 | GESolar : GES-P225 | -0.34 | 37 | 8.16 | 225 | 29.7 | 7.59
1123 | GESolar | GES-P230 | GESolar : GES-P230 | -0.34 | 37 | 8.22 | 230 | 29.8 | 7.73
1124 | GESolar | GES-P235 | GESolar : GES-P235 | -0.34 | 37.1 | 8.28 | 235 | 30 | 7.84
1125 | GESolar | GES-P240 | GESolar : GES-P240 | -0.34 | 37.2 | 8.33 | 240 | 30.2 | 7.95
1126 | GH-Solar | GH135M125 | GH-Solar : GH135M125 | -0.3 | 33.53 | 5.21 | 135 | 28.18 | 4.86
1127 | GH-Solar | GH165M125 | GH-Solar : GH165M125 | -0.3 | 40.98 | 5.21 | 165 | 34.54 | 4.86
1128 | GH-Solar | GH175M125 | GH-Solar : GH175M125 | -0.3 | 44.64 | 5.17 | 175 | 37.36 | 4.83
1129 | GH-Solar | GH180M125 | GH-Solar : GH180M125 | -0.3 | 44.71 | 5.21 | 180 | 37.58 | 4.86
1130 | GH-Solar | GH185M125 | GH-Solar : GH185M125 | -0.3 | 44.71 | 5.53 | 185 | 36.79 | 5.01
1131 | GH-Solar | GH186P156 | GH-Solar : GH186P156 | -0.35 | 29.66 | 8.3 | 185 | 24.76 | 7.77
1132 | GH-Solar | GH190M156 | GH-Solar : GH190M156 | -0.3 | 29.85 | 8.36 | 190 | 24.48 | 7.82
1133 | GH-Solar | GH200M125 | GH-Solar : GH200M125 | -0.3 | 49.68 | 5.21 | 200 | 41.76 | 4.86
1134 | GH-Solar | GH200P156 | GH-Solar : GH200P156 | -0.35 | 32.83 | 8.03 | 200 | 27 | 7.47
1135 | GH-Solar | GH210P156 | GH-Solar : GH210P156 | -0.35 | 36.24 | 7.7 | 210 | 29.53 | 7.11
1136 | GH-Solar | GH210P156 | GH-Solar : GH210P156 | -0.3 | 33.58 | 8.36 | 215 | 27.54 | 7.82
1137 | GH-Solar | GH220M125 | GH-Solar : GH220M125 | -0.3 | 54.64 | 5.21 | 220 | 45.93 | 4.86
1138 | GH-Solar | GH220P156 | GH-Solar : GH220P156 | -0.35 | 36.48 | 7.93 | 220 | 30 | 7.33
1139 | GH-Solar | GH235M125 | GH-Solar : GH235M125 | -0.3 | 59.52 | 5.17 | 235 | 49.82 | 4.83
1140 | GH-Solar | GH235P156 | GH-Solar : GH235P156 | -0.35 | 37.08 | 8.3 | 235 | 30.96 | 7.77
1141 | GH-Solar | GH235P156 | GH-Solar : GH235P156 | -0.35 | 37.08 | 8.3 | 235 | 30.96 | 7.77
1142 | GH-Solar | GH240M125 | GH-Solar : GH240M125 | -0.3 | 59.61 | 5.21 | 240 | 50.11 | 4.86
1143 | GH-Solar | GH240M156 | GH-Solar : GH240M156 | -0.3 | 37.32 | 8.36 | 240 | 30.6 | 7.82
1144 | GH-Solar | GH285M156 | GH-Solar : GH285M156 | -0.3 | 44.78 | 8.36 | 290 | 36.72 | 7.82
1145 | GH-Solar | GH45M125 | GH-Solar : GH45M125 | -0.3 | 22.03 | 2.66 | 45 | 18.36 | 2.42
1146 | GH-Solar | GH90M125 | GH-Solar : GH90M125 | -0.3 | 22.35 | 5.21 | 90 | 18.79 | 4.86
1147 | GiraSolar | G5-72 165Wp | GiraSolar : G5-72 165Wp | -0.355 | 44.4 | 5.1 | 165 | 35.2 | 4.7
1148 | GiraSolar | G5-72 175Wp | GiraSolar : G5-72 175Wp | -0.354 | 44.6 | 5.3 | 175 | 35.4 | 4.95
1149 | GLORIA SOLAR | GSS5-170A-E | GLORIA SOLAR : GSS5-170A-E | -0.31 | 44.6 | 5.3 | 170 | 35.5 | 4.79
1150 | GLORIA SOLAR | GSS5-175A-E | GLORIA SOLAR : GSS5-175A-E | -0.309 | 44.8 | 5.32 | 175 | 35.7 | 4.9
1151 | GLORIA SOLAR | GSS5-180A-E | GLORIA SOLAR : GSS5-180A-E | -0.308 | 45 | 5.33 | 180 | 36 | 5
1152 | GLORIA SOLAR | GSS5-185A-E1 | GLORIA SOLAR : GSS5-185A-E1 | -0.304 | 45.64 | 5.38 | 185 | 36.27 | 5.1
1153 | GLORIA SOLAR | SS165 | GLORIA SOLAR : SS165 | -0.31 | 44.3 | 5.2 | 165 | 35.2 | 4.73
1154 | Göbel | GS 1155 F | Göbel : GS 1155 F | -0.4 | 30.6 | 4.7 | 115 | 25.8 | 4.44
1155 | GPV AB | GPV 102 P | GPV AB : GPV 102 P | -0.39 | 21.5 | 6.4 | 102 | 17 | 6
1156 | GPV AB | GPV 102-W 12V | GPV AB : GPV 102-W 12V | -0.4 | 21.5 | 6.4 | 102 | 17 | 6
1157 | GPV AB | GPV 102-W 24V | GPV AB : GPV 102-W 24V | -0.4 | 43 | 3.2 | 102 | 34 | 3
1158 | GPV AB | GPV 155-M, C 12V | GPV AB : GPV 155-M, C 12V | -0.4 | 21.6 | 9.4 | 155 | 17.5 | 8.8
1159 | GPV AB | GPV 155-M, C 24V | GPV AB : GPV 155-M, C 24V | -0.4 | 43.2 | 4.7 | 155 | 35 | 4.4
1160 | GPV AB | GPV 165-M, C 12V | GPV AB : GPV 165-M, C 12V | -0.4 | 21.62 | 10.2 | 165 | 17.68 | 9.34
1161 | GPV AB | GPV 165-M, C 24V | GPV AB : GPV 165-M, C 24V | -0.4 | 43.24 | 5.1 | 165 | 35.36 | 4.67
1162 | GPV AB | GPV 85-M, C | GPV AB : GPV 85-M, C | -0.4 | 21.5 | 5.18 | 85 | 17.5 | 4.86
1163 | GPV AB | GPV102PT-12 | GPV AB : GPV102PT-12 | -0.4 | 21.5 | 6.4 | 102 | 17 | 6
1164 | GPV AB | GPV110ME | GPV AB : GPV110ME | -0.4 | 42.7 | 3.64 | 110 | 35.1 | 3.15
1165 | GPV AB | GPV110ME 1998 | GPV AB : GPV110ME 1998 | -0.416 | 43.3 | 3.73 | 110 | 34.2 | 3.21
1166 | GPV AB | GPV120P-12 | GPV AB : GPV120P-12 | -0.4 | 20.9 | 8.08 | 120 | 16.7 | 7.2
1167 | GPV AB | GPV120PXE12 | GPV AB : GPV120PXE12 | -0.4 | 20.8 | 8.08 | 120 | 16.7 | 7.2
1168 | GPV AB | GPV150P-12 | GPV AB : GPV150P-12 | -0.4 | 21.5 | 9.4 | 150 | 17 | 8.8
1169 | GPV AB | GPV150PCR80XII | GPV AB : GPV150PCR80XII | -0.4 | 43 | 4.7 | 150 | 34 | 4.4
1170 | GPV AB | GPV160M-12 | GPV AB : GPV160M-12 | -0.4 | 21.6 | 9.8 | 160 | 17.7 | 9.04
1171 | GPV AB | GPV160M-R-12 | GPV AB : GPV160M-R-12 | -0.4 | 21.6 | 9.8 | 160 | 17.7 | 9.04
1172 | GPV AB | GPV160PCR80XII | GPV AB : GPV160PCR80XII | -0.4 | 43.2 | 4.9 | 160 | 35.3 | 4.52
1173 | GPV AB | GPV165M-12 | GPV AB : GPV165M-12 | -0.4 | 21.6 | 9.8 | 165 | 17.7 | 9.34
1174 | GPV AB | GPV51PT | GPV AB : GPV51PT | -0.4 | 21.5 | 3.2 | 51 | 17 | 3
1175 | GPV AB | GPV55M | GPV AB : GPV55M | -0.35 | 21.4 | 3.65 | 55 | 17.5 | 3.15
1176 | GPV AB | GPV55ME | GPV AB : GPV55ME | -0.415 | 21.7 | 3.65 | 55 | 17.5 | 3.15
1177 | GPV AB | GPV60P | GPV AB : GPV60P | -0.385 | 20.8 | 4.04 | 60 | 16.7 | 3.6
1178 | GPV AB | GPV60PXE-MP1 | GPV AB : GPV60PXE-MP1 | -0.4 | 20.8 | 4.04 | 60 | 16.7 | 3.6
1179 | GPV AB | GPV75M-PCR80 | GPV AB : GPV75M-PCR80 | -0.4 | 21.6 | 4.84 | 75 | 17.7 | 4.34
1180 | GPV AB | GPV75PX | GPV AB : GPV75PX | -0.4 | 21.5 | 4.7 | 75 | 17 | 4.4
1181 | Granit | Solar Freestyle 128 | Granit : Solar Freestyle 128 | -0.4 | 23.8 | 4.8 | 128 | 33 | 3.9
1182 | Granit | Solar Freestyle 128 d | Granit : Solar Freestyle 128 d | -0.4 | 23.8 | 4.8 | 128 | 33 | 3.9
1183 | Granit | Solar Freestyle 256 | Granit : Solar Freestyle 256 | -0.4 | 23.8 | 4.8 | 256 | 66 | 3.9
1184 | Granit | Solar Freestyle 64 | Granit : Solar Freestyle 64 | -0.4 | 23.8 | 4.8 | 64 | 16.5 | 3.9
1185 | GSS | GSS-PV-162 | GSS : GSS-PV-162 | -0.558 | 43.9 | 5.4 | 162 | 34.6 | 4.7
1186 | GSS | GSS-PV-216 | GSS : GSS-PV-216 | -0.557 | 58.5 | 5.4 | 216 | 46.1 | 4.7
1187 | GSS | GSS-PV-293 | GSS : GSS-PV-293 | -0.557 | 79.3 | 5.4 | 293 | 62.4 | 4.7
1188 | GSS | ZRE 140GEF-36M-6(+)Z *3 | GSS : ZRE 140GEF-36M-6(+)Z *3 | -0.37 | 21.8 | 8.28 | 140 | 18.25 | 7.68
1189 | GSS | ZRE 144GEF-36M-6(+)Z *3 | GSS : ZRE 144GEF-36M-6(+)Z *3 | -0.37 | 21.9 | 8.45 | 144 | 18.4 | 7.85
1190 | GSS | ZRE 148GEF-36M-6(+)Z *3 | GSS : ZRE 148GEF-36M-6(+)Z *3 | -0.37 | 22.1 | 8.6 | 148 | 18.54 | 8
1191 | GSS | ZRE 170GEF-50P-6(+)Z | GSS : ZRE 170GEF-50P-6(+)Z | -0.38 | 30.6 | 7.5 | 170 | 24.94 | 6.82
1192 | GSS | ZRE 173GEF-50P-6(+)Z | GSS : ZRE 173GEF-50P-6(+)Z | -0.38 | 30.65 | 7.52 | 173 | 25.04 | 6.91
1193 | GSS | ZRE 175GEF-50P-6(+)Z | GSS : ZRE 175GEF-50P-6(+)Z | -0.38 | 30.75 | 7.54 | 175 | 25.16 | 6.96
1194 | GSS | ZRE 183GEF-50P-6(+)Z | GSS : ZRE 183GEF-50P-6(+)Z | -0.38 | 31 | 7.76 | 183 | 25.44 | 7.19
1195 | GSS | ZRE 185GEF-50P-6(+)Z | GSS : ZRE 185GEF-50P-6(+)Z | -0.38 | 31.1 | 7.81 | 185 | 25.58 | 7.23
1196 | GSS | ZRE 185GEF-50P-6(+)Z | GSS : ZRE 185GEF-50P-6(+)Z | -0.36 | 30.4 | 7.89 | 185 | 24.2 | 7.64
1197 | GSS | ZRE 187GEF-72M-5Z | GSS : ZRE 187GEF-72M-5Z | -0.34 | 44.87 | 5.45 | 187 | 36.72 | 5.09
1198 | GSS | ZRE 188GEF-50P-6(+)Z | GSS : ZRE 188GEF-50P-6(+)Z | -0.38 | 31.2 | 7.9 | 188 | 25.72 | 7.31
1199 | GSS | ZRE 190GEF-50M-6(+)Z | GSS : ZRE 190GEF-50M-6(+)Z | -0.37 | 30.4 | 8.55 | 190 | 24.28 | 7.83
1200 | GSS | ZRE 190GEF-50P-6(+)Z | GSS : ZRE 190GEF-50P-6(+)Z | -0.36 | 30.65 | 8.25 | 190 | 24.3 | 7.81
1201 | GSS | ZRE 193GEF-50M-6(+)Z | GSS : ZRE 193GEF-50M-6(+)Z | -0.37 | 30.45 | 8.58 | 193 | 24.49 | 7.88
1202 | GSS | ZRE 195GEF-50M-6(+)Z | GSS : ZRE 195GEF-50M-6(+)Z | -0.37 | 30.5 | 8.62 | 195 | 24.64 | 7.92
1203 | GSS | ZRE 195GEF-50P-6(+)Z | GSS : ZRE 195GEF-50P-6(+)Z | -0.36 | 30.8 | 8.36 | 195 | 24.8 | 7.86
1204 | GSS | ZRE 197GEF-50M-6(+)Z | GSS : ZRE 197GEF-50M-6(+)Z | -0.37 | 30.65 | 8.66 | 197 | 24.73 | 7.97
1205 | GSS | ZRE 198GEF-50M-6(+)Z *2 | GSS : ZRE 198GEF-50M-6(+)Z *2 | -0.37 | 30.45 | 8.68 | 198 | 24.85 | 7.97
1206 | GSS | ZRE 198GEF-50M-6(+)Z *3 | GSS : ZRE 198GEF-50M-6(+)Z *3 | -0.37 | 30.37 | 8.42 | 198 | 25.4 | 7.8
1207 | GSS | ZRE 200GEF-50M-6(+)Z | GSS : ZRE 200GEF-50M-6(+)Z | -0.37 | 30.85 | 8.69 | 200 | 24.88 | 8.04
1208 | GSS | ZRE 202GEF-60P-6(+)Z | GSS : ZRE 202GEF-60P-6(+)Z | -0.38 | 36.66 | 7.48 | 202 | 29.85 | 6.77
1209 | GSS | ZRE 203GEF-50M-6(+)Z *2 | GSS : ZRE 203GEF-50M-6(+)Z *2 | -0.37 | 30.55 | 8.72 | 203 | 25.22 | 8.05
1210 | GSS | ZRE 203GEF-50M-6(+)Z *3 | GSS : ZRE 203GEF-50M-6(+)Z *3 | -0.37 | 30.41 | 8.52 | 203 | 25.6 | 7.9
1211 | GSS | ZRE 205GEF-60P-6(+)Z | GSS : ZRE 205GEF-60P-6(+)Z | -0.38 | 36.72 | 7.5 | 205 | 29.93 | 6.85
1212 | GSS | ZRE 207GEF-60P-6(+)Z | GSS : ZRE 207GEF-60P-6(+)Z | -0.38 | 36.78 | 7.52 | 207 | 30.05 | 6.89
1213 | GSS | ZRE 208GEF-50M-6(+)Z *2 | GSS : ZRE 208GEF-50M-6(+)Z *2 | -0.37 | 30.82 | 8.87 | 208 | 25.55 | 8.14
1214 | GSS | ZRE 208GEF-50M-6(+)Z *3 | GSS : ZRE 208GEF-50M-6(+)Z *3 | -0.37 | 30.75 | 8.6 | 208 | 25.6 | 8.02
1215 | GSS | ZRE 213GEF-60P-6(+)Z | GSS : ZRE 213GEF-60P-6(+)Z | -0.38 | 37.02 | 7.64 | 213 | 30.32 | 7.02
1216 | GSS | ZRE 216GEF-60P-6(+)Z | GSS : ZRE 216GEF-60P-6(+)Z | -0.38 | 37.14 | 7.69 | 216 | 30.37 | 7.11
1217 | GSS | ZRE 219GEF-60P-6(+)Z | GSS : ZRE 219GEF-60P-6(+)Z | -0.38 | 37.2 | 7.76 | 219 | 30.53 | 7.17
1218 | GSS | ZRE 222GEF-60P-6(+)Z | GSS : ZRE 222GEF-60P-6(+)Z | -0.38 | 37.32 | 7.81 | 222 | 30.7 | 7.23
1219 | GSS | ZRE 222GEF-60P-6(+)Z *3 | GSS : ZRE 222GEF-60P-6(+)Z *3 | -0.36 | 36.48 | 7.89 | 222 | 29.04 | 7.65
1220 | GSS | ZRE 225GEF-60P-6(+)Z | GSS : ZRE 225GEF-60P-6(+)Z | -0.38 | 37.44 | 7.9 | 225 | 30.87 | 7.29
1221 | GSS | ZRE 228GEF-60M-6(+)Z | GSS : ZRE 228GEF-60M-6(+)Z | -0.37 | 36.48 | 8.55 | 228 | 29.14 | 7.83
1222 | GSS | ZRE 228GEF-60P-6(+)Z *3 | GSS : ZRE 228GEF-60P-6(+)Z *3 | -0.36 | 36.78 | 8.25 | 228 | 29.16 | 7.82
1223 | GSS | ZRE 231GEF-60M-6(+)Z | GSS : ZRE 231GEF-60M-6(+)Z | -0.37 | 36.54 | 8.58 | 231 | 29.31 | 7.88
1224 | GSS | ZRE 234GEF-60M-6(+)Z | GSS : ZRE 234GEF-60M-6(+)Z | -0.37 | 36.6 | 8.62 | 234 | 29.56 | 7.92
1225 | GSS | ZRE 234GEF-60P-6(+)Z *3 | GSS : ZRE 234GEF-60P-6(+)Z *3 | -0.36 | 36.96 | 8.36 | 234 | 29.75 | 7.87
1226 | GSS | ZRE 237GEF-60M-6(+)Z | GSS : ZRE 237GEF-60M-6(+)Z | -0.37 | 36.78 | 8.66 | 237 | 29.76 | 7.97
1227 | GSS | ZRE 238GEF-60M-6(+)Z | GSS : ZRE 238GEF-60M-6(+)Z | -0.37 | 36.55 | 8.68 | 238 | 29.86 | 7.97
1228 | GSS | ZRE 238GEF-60M-6(+)Z *2 | GSS : ZRE 238GEF-60M-6(+)Z *2 | -0.37 | 36.55 | 8.68 | 238 | 29.86 | 7.97
1229 | GSS | ZRE 238GEF-60M-6(+)Z *3 | GSS : ZRE 238GEF-60M-6(+)Z *3 | -0.37 | 36.45 | 8.42 | 238 | 30.5 | 7.8
1230 | GSS | ZRE 244GEF-60M-6(+)Z | GSS : ZRE 244GEF-60M-6(+)Z | -0.37 | 36.69 | 8.75 | 244 | 30.31 | 8.05
1231 | GSS | ZRE 244GEF-60M-6(+)Z *2 | GSS : ZRE 244GEF-60M-6(+)Z *2 | -0.37 | 36.69 | 8.75 | 244 | 30.31 | 8.05
1232 | GSS | ZRE 244GEF-60M-6(+)Z *3 | GSS : ZRE 244GEF-60M-6(+)Z *3 | -0.37 | 36.5 | 8.52 | 244 | 30.9 | 7.9
1233 | GSS | ZRE 248GEF-60M-6(+)Z *2 | GSS : ZRE 248GEF-60M-6(+)Z *2 | -0.37 | 36.72 | 8.8 | 248 | 30.54 | 8.12
1234 | GSS | ZRE 248GEF-60M-6(+)Z *3 | GSS : ZRE 248GEF-60M-6(+)Z *3 | -0.37 | 36.9 | 8.6 | 248 | 30.9 | 8.02
1235 | GSS | ZRE 250GEF-60M-6(+)Z | GSS : ZRE 250GEF-60M-6(+)Z | -0.37 | 37 | 8.87 | 250 | 30.69 | 8.15
1236 | GSS | ZRE185GEF-50P-6(+)Z-F(L) | GSS : ZRE185GEF-50P-6(+)Z-F(L) | -0.23 | 30.5 | 7.89 | 185 | 25.15 | 7.37
1237 | GSS | ZRE187GEF-72M-5Z-F(L) | GSS : ZRE187GEF-72M-5Z-F(L) | -0.37 | 44.87 | 5.45 | 187 | 36.72 | 5.09
1238 | GSS | ZRE190GEF-50P-6(+)Z-F(L) | GSS : ZRE190GEF-50P-6(+)Z-F(L) | -0.23 | 30.7 | 8 | 190 | 25.42 | 7.49
1239 | GSS | ZRE195GEF-50P-6(+)Z-F(L) | GSS : ZRE195GEF-50P-6(+)Z-F(L) | -0.23 | 31 | 8.12 | 195 | 25.78 | 7.57
1240 | GSS | ZRE198GEF-50M-6(+)Z-F(L) | GSS : ZRE198GEF-50M-6(+)Z-F(L) | -0.32 | 31 | 8.39 | 198 | 25.25 | 7.85
1241 | GSS | ZRE203GEF-50M-6(+)Z-F(L) | GSS : ZRE203GEF-50M-6(+)Z-F(L) | -0.32 | 31.2 | 8.5 | 203 | 25.65 | 7.93
1242 | GSS | ZRE222GEF-60P-6(+)Z-F(L) | GSS : ZRE222GEF-60P-6(+)Z-F(L) | -0.23 | 30.18 | 7.89 | 222 | 36.6 | 7.37
1243 | GSS | ZRE228GEF-60P-6(+)Z-F(L) | GSS : ZRE228GEF-60P-6(+)Z-F(L) | -0.23 | 30.5 | 8 | 228 | 38.8 | 7.49
1244 | GSS | ZRE234GEF-60P-6(+)Z-F(L) | GSS : ZRE234GEF-60P-6(+)Z-F(L) | -0.23 | 30.95 | 8.12 | 234 | 37.2 | 7.57
1245 | GSS | ZRE235GEF-60M-6(+)Z-F(L) | GSS : ZRE235GEF-60M-6(+)Z-F(L) | -0.32 | 37.2 | 8.3 | 235 | 30.3 | 7.76
1246 | GSS | ZRE240GEF-60M-6(+)Z-F(L) | GSS : ZRE240GEF-60M-6(+)Z-F(L) | -0.32 | 37.4 | 8.4 | 240 | 30.85 | 7.8
1247 | GWU Solar | MA 55 | GWU Solar : MA 55 | -0.349 | 21.8 | 3.41 | 52.5 | 17.5 | 3.15
1248 | GWU Solar | MAP 100 | GWU Solar : MAP 100 | -0.367 | 21 | 6.4 | 90 | 17 | 5.6
1249 | GWU Solar | MAP 140 | GWU Solar : MAP 140 | -0.376 | 42.5 | 4.55 | 138 | 35 | 4.14
1250 | GWU Solar | MAP 140 (D) | GWU Solar : MAP 140 (D) | -0.365 | 21.1 | 9 | 134 | 17 | 8.25
1251 | GWU Solar | MAP 50 | GWU Solar : MAP 50 | -0.365 | 21.1 | 3.2 | 47 | 17.2 | 2.9
1252 | GWU Solar | MAP 75 | GWU Solar : MAP 75 | -0.363 | 21.2 | 4.5 | 70 | 17.2 | 4.2
1253 | GWU Solar | SH-M 175 | GWU Solar : SH-M 175 | -0.4 | 44.4 | 5.55 | 175 | 35.4 | 4.95
1254 | GWU Solar | SH-P 160 | GWU Solar : SH-P 160 | -0.4 | 28.4 | 8.04 | 160 | 22.8 | 7.02
1255 | Heckert Solar | HS 115 (12V) | Heckert Solar : HS 115 (12V) | -0.35 | 21.7 | 7.1 | 115 | 16.8 | 6.85
1256 | Heckert Solar | HS 120 (12V) | Heckert Solar : HS 120 (12V) | -0.35 | 21.85 | 7.4 | 120 | 17 | 7.1
1257 | Heckert Solar | HS 125 (12V) | Heckert Solar : HS 125 (12V) | -0.35 | 22 | 7.7 | 125 | 17.4 | 7.15
1258 | Heckert Solar | HS 130 (12V) | Heckert Solar : HS 130 (12V) | -0.35 | 22.15 | 7.8 | 130 | 17.7 | 7.31
1259 | Heckert Solar | HS 135 (12V) | Heckert Solar : HS 135 (12V) | -0.35 | 22.3 | 7.9 | 135 | 18 | 7.48
1260 | Heckert Solar | HS 55 (12V) | Heckert Solar : HS 55 (12V) | -0.35 | 21.4 | 3.6 | 55 | 17.1 | 3.2
1261 | Heckert Solar | HS 60 (12V) | Heckert Solar : HS 60 (12V) | -0.35 | 21.5 | 3.6 | 60 | 17.4 | 3.4
1262 | Heckert Solar | HS-L 125 (12V) | Heckert Solar : HS-L 125 (12V) | -0.33 | 22 | 7.6 | 125 | 17.4 | 7.15
1263 | Heckert Solar | HS-L 130 (12V) | Heckert Solar : HS-L 130 (12V) | -0.33 | 22.15 | 7.8 | 130 | 17.7 | 7.31
1264 | Heckert Solar | HS-L 135 (12V) | Heckert Solar : HS-L 135 (12V) | -0.33 | 22.3 | 7.9 | 135 | 18 | 7.48
1265 | Heckert Solar | HS-MS 145 | Heckert Solar : HS-MS 145 | -0.33 | 36.46 | 5.3 | 145 | 30.97 | 4.69
1266 | Heckert Solar | HS-MS 150 | Heckert Solar : HS-MS 150 | -0.33 | 39.7 | 5.37 | 150 | 31.43 | 4.78
1267 | Heckert Solar | HS-MS 155 | Heckert Solar : HS-MS 155 | -0.33 | 39.94 | 5.43 | 155 | 31.88 | 4.87
1268 | Heckert Solar | HS-MS 160 | Heckert Solar : HS-MS 160 | -0.33 | 40.16 | 5.48 | 160 | 32.27 | 4.96
1269 | Heckert Solar | HS-MS 165 | Heckert Solar : HS-MS 165 | -0.33 | 32.5 | 5.58 | 165 | 32.5 | 5.08
1270 | Heckert Solar | HS-MXL 200 | Heckert Solar : HS-MXL 200 | -0.33 | 31.75 | 8.95 | 200 | 23.79 | 8.4
1271 | Heckert Solar | HS-MXL 205 | Heckert Solar : HS-MXL 205 | -0.33 | 32.25 | 9 | 205 | 24.26 | 8.45
1272 | Heckert Solar | HS-MXL 210 | Heckert Solar : HS-MXL 210 | -0.33 | 32.7 | 9.04 | 210 | 24.73 | 8.49
1273 | Heckert Solar | HS-MXL 215 | Heckert Solar : HS-MXL 215 | -0.33 | 33.2 | 9.08 | 215 | 25.2 | 8.53
1274 | Heckert Solar | HS-MXL 220 | Heckert Solar : HS-MXL 220 | -0.33 | 33.7 | 9.13 | 220 | 25.67 | 8.57
1275 | Heckert Solar | HS-PL 125 | Heckert Solar : HS-PL 125 | -0.31 | 20.6 | 8.17 | 125 | 16.24 | 7.7
1276 | Heckert Solar | HS-PL 130 | Heckert Solar : HS-PL 130 | -0.31 | 21.1 | 8.25 | 130 | 16.7 | 7.78
1277 | Heckert Solar | HS-PL 135 | Heckert Solar : HS-PL 135 | -0.31 | 21.56 | 8.33 | 135 | 17.2 | 7.85
1278 | Heckert Solar | HS-PL 140 | Heckert Solar : HS-PL 140 | -0.31 | 22.1 | 8.4 | 140 | 17.7 | 7.91
1279 | Heckert Solar | HS-PL 145 | Heckert Solar : HS-PL 145 | -0.31 | 22.53 | 8.5 | 145 | 18.13 | 8
1280 | Heckert Solar | HS-PXL 190 | Heckert Solar : HS-PXL 190 | -0.31 | 31.78 | 8.2 | 190 | 24.65 | 7.71
1281 | Heckert Solar | HS-PXL 195 | Heckert Solar : HS-PXL 195 | -0.31 | 32.25 | 8.25 | 195 | 25.13 | 7.76
1282 | Heckert Solar | HS-PXL 200 | Heckert Solar : HS-PXL 200 | -0.31 | 32.7 | 8.3 | 200 | 25.6 | 7.81
1283 | Heckert Solar | HS-PXL 205 | Heckert Solar : HS-PXL 205 | -0.31 | 33.2 | 8.35 | 205 | 26.07 | 7.86
1284 | Heckert Solar | HS-PXL 210 | Heckert Solar : HS-PXL 210 | -0.31 | 33.68 | 8.4 | 210 | 26.55 | 7.91
1285 | Heckert Solar | HS-PXL 215 | Heckert Solar : HS-PXL 215 | -0.31 | 34.1 | 8.45 | 215 | 27 | 7.96
1286 | Heisterholz | Müritz-Solar-Ziegel | Heisterholz : Müritz-Solar-Ziegel | -0.4 | 10.9 | 3.7 | 30 | 8.55 | 3.51
1287 | Helio Sphera | HS-110 | Helio Sphera : HS-110 | -0.33 | 128 | 1.39 | 110 | 97 | 1.14
1288 | Helio Sphera | HS-115 | Helio Sphera : HS-115 | -0.33 | 129 | 1.42 | 115 | 98 | 1.18
1289 | Helio Sphera | HS-120 | Helio Sphera : HS-120 | -0.33 | 130 | 1.44 | 120 | 99 | 1.22
1290 | Helio Sphera | HS-125 | Helio Sphera : HS-125 | -0.33 | 131 | 1.45 | 125 | 100 | 1.25
1291 | Helios | H 1000 (100 Wp) | Helios : H 1000 (100 Wp) | -0.43 | 21 | 6.7 | 100 | 16.7 | 6
1292 | Helios | H 1540 (140 Wp) | Helios : H 1540 (140 Wp) | -0.43 | 23 | 9.24 | 140 | 17.8 | 7.86
1293 | Helios | H 1540 (150Wp) | Helios : H 1540 (150Wp) | -0.43 | 23 | 9.9 | 150 | 17.8 | 8.42
1294 | Helios | H 200 | Helios : H 200 | -0.439 | 20.5 | 1.36 | 20 | 16.5 | 1.21
1295 | Helios | H 250 | Helios : H 250 | -0.419 | 21.5 | 1.56 | 25 | 18 | 1.39
1296 | Helios | H 50 | Helios : H 50 | -0.419 | 21.5 | 3.3 | 50 | 17.5 | 2.86
1297 | Helios | H 500 | Helios : H 500 | -0.431 | 20.9 | 3.65 | 55 | 16.9 | 3.25
1298 | Helios | H 750, 55 W | Helios : H 750, 55 W | -0.417 | 21.6 | 3.48 | 55 | 17.3 | 3.18
1299 | Helios | H 750, 65 W | Helios : H 750, 65 W | -0.417 | 21.6 | 4.15 | 65 | 17.3 | 3.76
1300 | Helios | H 750, 75 W | Helios : H 750, 75 W | -0.417 | 21.6 | 4.78 | 75 | 17.3 | 4.33
1301 | Helios | H 800 | Helios : H 800 | -0.431 | 20.9 | 5.4 | 80 | 17 | 4.7
1302 | Helios | H 800 A | Helios : H 800 A | -0.431 | 20.9 | 5.4 | 80 | 17 | 4.7
1303 | Helios | H 800 X | Helios : H 800 X | -0.431 | 20.9 | 5.05 | 75 | 16.9 | 4.45
1304 | Helios | H 900, 85 W | Helios : H 900, 85 W | -0.429 | 21 | 5.47 | 85 | 17 | 5
1305 | Helios | H 900, 90 W | Helios : H 900, 90 W | -0.435 | 20.7 | 6.2 | 90 | 16.7 | 5.4
1306 | Helios | H1350 | Helios : H1350 | -0.4 | 21 | 6.7 | 100 | 16.7 | 6
1307 | Helios Technology | HMA220 | Helios Technology : HMA220 | -0.38 | 36.95 | 8.11 | 220 | 29.15 | 7.55
1308 | Helios Technology | HMA225 | Helios Technology : HMA225 | -0.38 | 37.45 | 8.17 | 225 | 29.65 | 7.59
1309 | Helios Technology | HMA230 | Helios Technology : HMA230 | -0.38 | 37.85 | 8.23 | 230 | 29.9 | 7.69
1310 | HelioSphera | HS-110 | HelioSphera : HS-110 | -0.28 | 130 | 1.42 | 110 | 102.7 | 1.07
1311 | HelioSphera | HS-115 | HelioSphera : HS-115 | -0.28 | 130 | 1.42 | 115 | 102.7 | 1.12
1312 | HelioSphera | HS-120 | HelioSphera : HS-120 | -0.28 | 130 | 1.42 | 120 | 102.7 | 1.17
1313 | HelioSphera | HS-125 | HelioSphera : HS-125 | -0.28 | 130 | 1.42 | 125 | 102.7 | 1.22
1314 | HelioSphera | HS-130 | HelioSphera : HS-130 | -0.28 | 130 | 1.42 | 130 | 102.7 | 1.27
1315 | Heltron | HE-21-215 | Heltron : HE-21-215 | -0.32 | 36.54 | 7.59 | 215 | 30.48 | 7.05
1316 | Heltron | HE-21-220 | Heltron : HE-21-220 | -0.32 | 36.78 | 7.66 | 220 | 30.78 | 7.25
1317 | Heltron | HE-25-175 | Heltron : HE-25-175 | -0.37 | 43.8 | 5.21 | 175 | 35.8 | 4.91
1318 | Heltron | HE-25-180 | Heltron : HE-25-180 | -0.37 | 44.2 | 5.3 | 180 | 36.1 | 5
1319 | Heltron | HE-25-180 | Heltron : HE-25-180 | -0.37 | 45 | 5.25 | 180 | 37.2 | 4.87
1320 | Heltron | HE-25-185 | Heltron : HE-25-185 | -0.37 | 45.3 | 5.4 | 185 | 37 | 5.02
1321 | Heltron | QC-C02 215 | Heltron : QC-C02 215 | -0.35 | 35.8 | 8.1 | 215 | 28.6 | 7.5
1322 | Heltron | QC-C02 220 | Heltron : QC-C02 220 | -0.35 | 36 | 8.2 | 220 | 29 | 7.6
1323 | Heltron | QC-C02 225 | Heltron : QC-C02 225 | -0.35 | 36.4 | 8.25 | 225 | 29.4 | 7.65
1324 | Heltron | QC-C02 230 | Heltron : QC-C02 230 | -0.35 | 36.6 | 8.3 | 230 | 29.65 | 7.75
1325 | Heltron | TSM-160M | Heltron : TSM-160M | -0.34 | 43.9 | 5.23 | 170 | 35.5 | 4.79
1326 | HEM | 70 | HEM : 70 | -0.34 | 21.5 | 4.5 | 70 | 17 | 4.28
1327 | HEM | 75 | HEM : 75 | -0.34 | 21.5 | 4.7 | 75 | 17.1 | 4.41
1328 | HEM | 80 | HEM : 80 | -0.34 | 21.5 | 5 | 80 | 17.3 | 4.65
1329 | HEM | 85 | HEM : 85 | -0.34 | 21.5 | 5.18 | 85 | 17.5 | 4.86
1330 | Himin | HG150(34)S | Himin : HG150(34)S | -0.38 | 43.4 | 4.66 | 150 | 35.6 | 4.21
1331 | Himin | HG155(34)S | Himin : HG155(34)S | -0.38 | 44 | 4.85 | 155 | 35.6 | 4.49
1332 | Himin | HG160(34)S | Himin : HG160(34)S | -0.38 | 44 | 4.85 | 160 | 35.6 | 4.49
1333 | Himin | HG165(34)S | Himin : HG165(34)S | -0.38 | 44.2 | 5.03 | 165 | 35.6 | 4.64
1334 | Himin | HG170(34)S | Himin : HG170(34)S | -0.38 | 44.5 | 5.15 | 170 | 35.6 | 4.78
1335 | Himin | HG175(34)S | Himin : HG175(34)S | -0.38 | 44.8 | 5.26 | 175 | 35.8 | 4.88
1336 | Himin | HG180(34)S | Himin : HG180(34)S | -0.38 | 45.2 | 5.4 | 180 | 36.3 | 4.96
1337 | Himin | HG185(34)S | Himin : HG185(34)S | -0.38 | 45.4 | 5.49 | 185 | 36.5 | 5.05
1338 | Hyundai | HiM-S085 | Hyundai : HiM-S085 | -0.38 | 14.3 | 8.21 | 85 | 11.6 | 7.27
1339 | Hyundai | HiM-S125 | Hyundai : HiM-S125 | -0.38 | 21.4 | 8.21 | 125 | 17.4 | 21.4
1340 | Hyundai | HiM-S160 | Hyundai : HiM-S160 | -0.38 | 26.3 | 8.3 | 160 | 21.6 | 7.43
1341 | Hyundai | HiM-S170 | Hyundai : HiM-S170 | -0.38 | 28.6 | 8.21 | 170 | 23.2 | 7.27
1342 | Hyundai | HiM-S180 | Hyundai : HiM-S180 | -0.38 | 28.8 | 8.38 | 180 | 23.8 | 7.53
1343 | Hyundai | HiM-S200 | Hyundai : HiM-S200 | -0.38 | 32.3 | 8.36 | 200 | 26.6 | 7.47
1344 | HYUNDAI | HIS-M182-SF | HYUNDAI : HIS-M182-SF | -0.32 | 32.7 | 7.8 | 182 | 25.9 | 7.1
1345 | HYUNDAI | HIS-M185-SF | HYUNDAI : HIS-M185-SF | -0.32 | 32.7 | 7.8 | 185 | 26 | 7.1
1346 | HYUNDAI | HIS-M188-SF | HYUNDAI : HIS-M188-SF | -0.32 | 33 | 7.9 | 188 | 26.2 | 7.2
1347 | HYUNDAI | HIS-M191-SF | HYUNDAI : HIS-M191-SF | -0.32 | 33 | 8 | 191 | 26.3 | 7.2
1348 | HYUNDAI | HIS-M194-SF | HYUNDAI : HIS-M194-SF | -0.32 | 33.1 | 8 | 194 | 26.4 | 7.3
1349 | HYUNDAI | HIS-M197-SF | HYUNDAI : HIS-M197-SF | -0.32 | 33.3 | 8.1 | 197 | 26.6 | 7.4
1350 | HYUNDAI | HIS-M200-SF | HYUNDAI : HIS-M200-SF | -0.32 | 33.6 | 8.2 | 200 | 26.7 | 7.5
1351 | HYUNDAI | HIS-M203-SF | HYUNDAI : HIS-M203-SF | -0.32 | 33.7 | 8.3 | 203 | 26.9 | 7.5
1352 | HYUNDAI | HIS-M206-SF | HYUNDAI : HIS-M206-SF | -0.32 | 33.8 | 8.3 | 206 | 27.1 | 7.6
1353 | HYUNDAI | HIS-S188-SF | HYUNDAI : HIS-S188-SF | -0.34 | 33 | 8.1 | 188 | 25 | 7.5
1354 | HYUNDAI | HIS-S191-SF | HYUNDAI : HIS-S191-SF | -0.34 | 33.2 | 8.2 | 191 | 25.2 | 7.6
1355 | HYUNDAI | HIS-S194-SF | HYUNDAI : HIS-S194-SF | -0.34 | 33.2 | 8.2 | 194 | 25.6 | 7.6
1356 | HYUNDAI | HIS-S197-SF | HYUNDAI : HIS-S197-SF | -0.34 | 33.3 | 8.2 | 197 | 25.9 | 7.6
1357 | HYUNDAI | HIS-S200-SF | HYUNDAI : HIS-S200-SF | -0.34 | 33.4 | 8.3 | 200 | 26.3 | 7.6
1358 | HYUNDAI | HIS-S203-SF | HYUNDAI : HIS-S203-SF | -0.34 | 33.4 | 8.3 | 203 | 26.5 | 7.7
1359 | HYUNDAI | HIS-S206-SF | HYUNDAI : HIS-S206-SF | -0.34 | 33.5 | 8.4 | 206 | 26.8 | 7.7
1360 | HYUNDAI | HIS-S209-SF | HYUNDAI : HIS-S209-SF | -0.34 | 33.5 | 8.5 | 209 | 26.9 | 7.8
1361 | HYUNDAI | HIS-S212-SF | HYUNDAI : HIS-S212-SF | -0.34 | 33.5 | 8.6 | 212 | 27 | 7.9
1362 | I.R.S. Solar | 001-165 | I.R.S. Solar : 001-165 | -0.35 | 99 | 2.6 | 165 | 74 | 2.25
1363 | I.R.S. Solar | 001-173 | I.R.S. Solar : 001-173 | -0.35 | 101 | 2.63 | 173 | 76.1 | 2.32
1364 | I.R.S. Solar | 001-182 | I.R.S. Solar : 001-182 | -0.35 | 102.5 | 2.7 | 182 | 78 | 2.35
1365 | I.R.S. Solar | IRS 175 M | I.R.S. Solar : IRS 175 M | -0.34 | 44.7 | 5.23 | 175 | 35.8 | 4.9
1366 | IBC Solar | IBC MonoSol 230 ET | IBC Solar : IBC MonoSol 230 ET | -0.369 | 36.3 | 8.48 | 230 | 29.1 | 7.92
1367 | IBC Solar | IBC MonoSol 230 MI | IBC Solar : IBC MonoSol 230 MI | -0.349 | 36.7 | 8.23 | 230 | 30.6 | 7.52
1368 | IBC Solar | IBC MonoSol 240 MI | IBC Solar : IBC MonoSol 240 MI | -0.351 | 36.7 | 8.56 | 240 | 30.6 | 7.85
1369 | IBC Solar | IBC-110S Megaline | IBC Solar : IBC-110S Megaline | -0.388 | 20.6 | 7.38 | 110 | 16.4 | 6.7
1370 | IBC Solar | IBC-120 Megaline | IBC Solar : IBC-120 Megaline | -0.381 | 21 | 7.74 | 120 | 16.8 | 7.12
1371 | IBC Solar | IBC-120 Megaline 1998 | IBC Solar : IBC-120 Megaline 1998 | -0.343 | 21.3 | 7.6 | 120 | 17.1 | 7
1372 | IBC Solar | IBC-120 S Megaline | IBC Solar : IBC-120 S Megaline | -0.381 | 21 | 7.74 | 120 | 16.8 | 7.12
1373 | IBC Solar | IBC-155 S Megaline | IBC Solar : IBC-155 S Megaline | -0.362 | 44.2 | 4.8 | 155 | 35 | 4.43
1374 | IBC Solar | IBC-160 M | IBC Solar : IBC-160 M | -0.35 | 43.2 | 5 | 160 | 34.4 | 4.66
1375 | IBC Solar | IBC-160 S Megaline | IBC Solar : IBC-160 S Megaline | -0.382 | 28 | 7.74 | 160 | 22.5 | 7.12
1376 | IBC Solar | IBC-175M | IBC Solar : IBC-175M | -0.35 | 44.4 | 5.55 | 175 | 35.4 | 4.95
1377 | IBC Solar | IBC-190 Megaline | IBC Solar : IBC-190 Megaline | -0.372 | 28.8 | 8.8 | 190 | 24 | 7.92
1378 | IBC Solar | IBC-200 Megaline | IBC Solar : IBC-200 Megaline | -0.369 | 29 | 9.2 | 200 | 24.2 | 8.28
1379 | IBC Solar | IBC-215S MEGALINE | IBC Solar : IBC-215S MEGALINE | -0.369 | 36.8 | 7.75 | 215 | 30 | 7.17
1380 | IBC Solar | IBC-220 Megaline | IBC Solar : IBC-220 Megaline | -0.369 | 29.1 | 10 | 220 | 24.2 | 9.1
1381 | IBC Solar | IBC-225TE | IBC Solar : IBC-225TE | -0.346 | 36.7 | 8.13 | 225 | 30.3 | 7.44
1382 | IBC Solar | IBC-225TE | IBC Solar : IBC-225TE | -0.346 | 36.7 | 8.13 | 225 | 30.3 | 7.44
1383 | IBC Solar | IBC-52 Megaline | IBC Solar : IBC-52 Megaline | -0.388 | 20.6 | 3.69 | 52 | 16.5 | 3.15
1384 | IBC Solar | IBC-80 Megaline 1998 | IBC Solar : IBC-80 Megaline 1998 | -0.348 | 21 | 5.08 | 80 | 17 | 4.71
1385 | IBC Solar | IBC-80 Megaline 1999 | IBC Solar : IBC-80 Megaline 1999 | -0.381 | 21 | 5.08 | 80 | 17 | 4.71
1386 | IBC Solar | IBC-80 S Megaline | IBC Solar : IBC-80 S Megaline | -0.381 | 21 | 5.17 | 80 | 16.8 | 4.75
1387 | IBC Solar | Millenia MST-43-LV | IBC Solar : Millenia MST-43-LV | -0.27 | 22.7 | 3.3 | 43 | 16.5 | 2.6
1388 | IBC Solar | MonoSol 190 MS | IBC Solar : MonoSol 190 MS | -0.432 | 45.2 | 5.56 | 190 | 36.6 | 5.19
1389 | IBC Solar | MonoSol 195 MS | IBC Solar : MonoSol 195 MS | -0.432 | 45.4 | 5.67 | 195 | 36.8 | 5.3
1390 | IBC Solar | STP155s-24/24Ac | IBC Solar : STP155s-24/24Ac | -0.377 | 43.2 | 4.9 | 155 | 34.4 | 4.51
1391 | Innovosolar | TEM110-140P | Innovosolar : TEM110-140P | -0.34 | 21.63 | 8.75 | 140 | 17.8 | 7.87
1392 | Innovosolar | TEM165-180-A | Innovosolar : TEM165-180-A | -0.34 | 44.5 | 5.45 | 180 | 36 | 5
1393 | Innovosolar | TEM165-180-B | Innovosolar : TEM165-180-B | -0.34 | 29.7 | 8.35 | 180 | 23.75 | 7.58
1394 | Innovosolar | TEM170-185P | Innovosolar : TEM170-185P | -0.34 | 28.91 | 8.65 | 185 | 23.7 | 7.81
1395 | Innovosolar | TEM200-230P | Innovosolar : TEM200-230P | -0.34 | 37.31 | 8.19 | 230 | 29.8 | 7.72
1396 | Innovosolar | TEM210-230M | Innovosolar : TEM210-230M | -0.34 | 36.25 | 8.45 | 230 | 29.7 | 7.74
1397 | Innovosolar | TEM210-240M | Innovosolar : TEM210-240M | -0.34 | 58.4 | 5.56 | 240 | 47.5 | 5.1
1398 | Innovosolar | TEM250-280P | Innovosolar : TEM250-280P | -0.34 | 43.77 | 8.76 | 280 | 35.3 | 7.93
1399 | Innovosolar | TEM30M | Innovosolar : TEM30M | -0.34 | 21.35 | 1.88 | 30 | 17.25 | 1.74
1400 | Innovosolar | TEM40M | Innovosolar : TEM40M | -0.34 | 22 | 2.48 | 40 | 17.5 | 2.28
1401 | Innovosolar | TEM50M | Innovosolar : TEM50M | -0.34 | 21.35 | 3.15 | 50 | 17.25 | 2.89
1402 | Innovosolar | TEM60-90M | Innovosolar : TEM60-90M | -0.34 | 22.25 | 5.6 | 90 | 17.95 | 5.01
1403 | Intersolar | B103D | Intersolar : B103D | -0.4 | 23 | 0.39 | 4 | 15 | 0.27
1404 | Intersolar | B103W | Intersolar : B103W | -0.4 | 23 | 0.39 | 3.7 | 15 | 0.25
1405 | Intersolar | B104D | Intersolar : B104D | -0.4 | 23 | 0.58 | 6.5 | 15 | 0.43
1406 | Intersolar | B104W | Intersolar : B104W | -0.4 | 23 | 0.58 | 5.5 | 15 | 0.36
1407 | Intersolar | B107W | Intersolar : B107W | -0.4 | 23 | 0.9 | 12 | 15 | 0.8
1408 | Intersolar | B108D | Intersolar : B108D | -0.4 | 23 | 0.9 | 14 | 15 | 0.93
1409 | Inventux Solar | X 115 | Inventux Solar : X 115 | -0.3 | 160 | 1.15 | 115 | 122 | 0.94
1410 | Inventux Solar | X 120 | Inventux Solar : X 120 | -0.3 | 161 | 1.18 | 120 | 124 | 0.97
1411 | Inventux Solar | X 125 | Inventux Solar : X 125 | -0.3 | 161 | 1.21 | 125 | 125 | 1
1412 | Inventux Solar | X 130 | Inventux Solar : X 130 | -0.3 | 162 | 1.24 | 130 | 126 | 1.03
1413 | Inventux Solar | X 135 | Inventux Solar : X 135 | -0.3 | 162 | 1.27 | 135 | 127 | 1.07
1414 | Inventux Solar | X 140 | Inventux Solar : X 140 | -0.3 | 163 | 1.29 | 140 | 128 | 1.1
1415 | IRES-SOLAR | SRM-160D | IRES-SOLAR : SRM-160D | -0.33 | 43.2 | 5.07 | 160 | 34.5 | 4.64
1416 | IRES-SOLAR | SRM-165D | IRES-SOLAR : SRM-165D | -0.33 | 43.6 | 5.08 | 165 | 35.4 | 4.66
1417 | IRES-SOLAR | SRM-170D | IRES-SOLAR : SRM-170D | -0.33 | 44.2 | 5.15 | 170 | 35.6 | 4.78
1418 | IRES-SOLAR | SRM-175D | IRES-SOLAR : SRM-175D | -0.33 | 44.2 | 5.25 | 175 | 35.8 | 4.89
1419 | IRES-SOLAR | SRM-180D | IRES-SOLAR : SRM-180D | -0.33 | 44.2 | 5.36 | 180 | 36.2 | 4.97
1420 | IRES-SOLAR | SRM-185D | IRES-SOLAR : SRM-185D | -0.33 | 44.2 | 5.51 | 185 | 36.3 | 5.1
1421 | Isofoton | I-05 | Isofoton : I-05 | -0.4 | 19.2 | 0.38 | 5 | 15.5 | 0.32
1422 | Isofoton | I-10 | Isofoton : I-10 | -0.37 | 21.6 | 0.82 | 10 | 17.4 | 0.58
1423 | Isofoton | I-100 / 24 | Isofoton : I-100 / 24 | -0.37 | 43.2 | 3.27 | 100 | 34.8 | 2.87
1424 | Isofoton | I-100 M / 12 | Isofoton : I-100 M / 12 | -0.37 | 21.6 | 6.48 | 100 | 17.4 | 5.75
1425 | Isofoton | I-106 / 12 | Isofoton : I-106 / 12 | -0.37 | 21.6 | 6.54 | 106 | 17.4 | 6.1
1426 | Isofoton | I-106 / 24 | Isofoton : I-106 / 24 | -0.37 | 43.2 | 3.27 | 106 | 34.8 | 3.05
1427 | Isofoton | I-106/24 InDach | Isofoton : I-106/24 InDach | -0.37 | 43.2 | 3.27 | 106 | 34.8 | 3.05
1428 | Isofoton | I-110 / 24 | Isofoton : I-110 / 24 | -0.37 | 43.2 | 3.38 | 110 | 34.8 | 3.16
1429 | Isofoton | I-110 M / 12 | Isofoton : I-110 M / 12 | -0.37 | 21.6 | 6.76 | 110 | 17.4 | 6.32
1430 | Isofoton | I-150 / 12 | Isofoton : I-150 / 12 | -0.38 | 21.1 | 9.5 | 150 | 17.2 | 8.72
1431 | Isofoton | I-150 InDach | Isofoton : I-150 InDach | -0.37 | 21.6 | 9.24 | 150 | 17.4 | 8.62
1432 | Isofoton | I-150S 12V | Isofoton : I-150S 12V | -0.37 | 21.6 | 8.9 | 150 | 17.3 | 8.7
1433 | Isofoton | I-150S 24V | Isofoton : I-150S 24V | -0.37 | 43.2 | 4.45 | 150 | 34.6 | 4.35
1434 | Isofoton | I-159 | Isofoton : I-159 | -0.37 | 21.6 | 9.81 | 159 | 17.4 | 9.15
1435 | Isofoton | I-160 InDach | Isofoton : I-160 InDach | -0.37 | 21.6 | 9.87 | 160 | 17.4 | 9.2
1436 | Isofoton | I-165 | Isofoton : I-165 | -0.37 | 21.6 | 10.14 | 165 | 17.4 | 9.48
1437 | Isofoton | I-22 | Isofoton : I-22 | -0.37 | 21.6 | 1.64 | 22 | 17.4 | 1.26
1438 | Isofoton | I-50 | Isofoton : I-50 | -0.37 | 21.6 | 3.27 | 50 | 17.4 | 2.87
1439 | Isofoton | I-53 | Isofoton : I-53 | -0.37 | 21.6 | 3.27 | 53 | 17.4 | 3.05
1440 | Isofoton | I-55 | Isofoton : I-55 | -0.367 | 21.6 | 3.38 | 55 | 17.4 | 3.38
1441 | Isofoton | IS-150(S) / 12 | Isofoton : IS-150(S) / 12 | -0.37 | 21.6 | 9.3 | 150 | 17.3 | 8.7
1442 | Isofoton | IS-150(S) / 24 | Isofoton : IS-150(S) / 24 | -0.37 | 43.2 | 4.7 | 150 | 34.6 | 4.35
1443 | Isofoton | IS-200(S) / 32 | Isofoton : IS-200(S) / 32 | -0.37 | 57.6 | 4.45 | 200 | 46.08 | 4.35
1444 | Isofoton | ISF-215 | Isofoton : ISF-215 | -0.38 | 36.8 | 8.05 | 215 | 29.5 | 7.29
1445 | Isofoton | ISF-220 | Isofoton : ISF-220 | -0.38 | 36.9 | 8.17 | 220 | 29.6 | 7.48
1446 | Isofoton | ISF-225 | Isofoton : ISF-225 | -0.38 | 36.9 | 8.3 | 225 | 29.6 | 7.62
1447 | Isofoton | ISF-230 | Isofoton : ISF-230 | -0.38 | 37 | 8.3 | 230 | 29.7 | 7.75
1448 | Isofoton | M-180 InDach | Isofoton : M-180 InDach | -0.322 | 44.6 | 5.68 | 180 | 35.6 | 5.05
1449 | Isofoton | PV I-88 | Isofoton : PV I-88 | -0.4 | 7.2 | 16.2 | 88 | 5.8 | 15.2
1450 | Istar Solar | IS4000P-200P | Istar Solar : IS4000P-200P | -0.37 | 32.6 | 8.96 | 200 | 25.4 | 7.83
1451 | JC Solar | JCSM160D | JC Solar : JCSM160D | -0.36 | 43.7 | 4.95 | 160 | 35 | 4.57
1452 | JC Solar | JCSM165D | JC Solar : JCSM165D | -0.36 | 44 | 5.05 | 165 | 35.4 | 4.66
1453 | JC Solar | JCSM170D | JC Solar : JCSM170D | -0.36 | 44.4 | 5.15 | 170 | 35.6 | 4.78
1454 | JC Solar | JCSM175D | JC Solar : JCSM175D | -0.35 | 44.7 | 5.23 | 175 | 35.8 | 4.89
1455 | JC Solar | JCSM180D | JC Solar : JCSM180D | -0.35 | 44.8 | 5.32 | 180 | 36 | 5
1456 | JC Solar | JCSM185D | JC Solar : JCSM185D | -0.35 | 45 | 5.43 | 185 | 36.4 | 5.08
1457 | JC Solar | JCSM190D | JC Solar : JCSM190D | -0.35 | 45.2 | 5.53 | 190 | 36.8 | 5.15
1458 | JC Solar | JCSM210D | JC Solar : JCSM210D | -0.42 | 37.9 | 7.53 | 210 | 28.3 | 7.42
1459 | JC Solar | JCSM215D | JC Solar : JCSM215D | -0.42 | 38 | 7.67 | 215 | 28.5 | 7.54
1460 | JC Solar | JCSM220D | JC Solar : JCSM220D | -0.42 | 38.1 | 7.8 | 220 | 28.7 | 7.67
1461 | JC Solar | JCSM225D | JC Solar : JCSM225D | -0.42 | 38.2 | 7.92 | 225 | 29.1 | 7.79
1462 | JC Solar | JCSM230D | JC Solar : JCSM230D | -0.42 | 38.3 | 8.03 | 230 | 29.1 | 7.9
1463 | JC Solar | JCSM235D | JC Solar : JCSM235D | -0.42 | 38.4 | 8.17 | 235 | 29.3 | 8.02
1464 | JC Solar | JCSM240D | JC Solar : JCSM240D | -0.42 | 38.4 | 8.32 | 240 | 29.6 | 8.11
1465 | JC Solar | JCSM245D | JC Solar : JCSM245D | -0.42 | 38.5 | 8.45 | 245 | 29.8 | 8.22
1466 | JC Solar | JCSM250D | JC Solar : JCSM250D | -0.41 | 38.6 | 8.57 | 250 | 30 | 8.33
1467 | Jetion Solar | JT135SFc 135 | Jetion Solar : JT135SFc 135 | -0.57 | 21.4 | 8.4 | 135 | 18 | 7.5
1468 | Jetion Solar | JT140SFc 140 | Jetion Solar : JT140SFc 140 | -0.57 | 21.8 | 8.55 | 140 | 18.42 | 7.6
1469 | Jetion Solar | JT145SFc 145 | Jetion Solar : JT145SFc 145 | -0.57 | 22.3 | 8.67 | 145 | 18.71 | 7.75
1470 | Jetion Solar | JT150SFc 150 | Jetion Solar : JT150SFc 150 | -0.57 | 22.6 | 8.85 | 150 | 19.11 | 7.85
1471 | Jetion Solar | JT170SAa/SAb 170 | Jetion Solar : JT170SAa/SAb 170 | -0.4 | 43.8 | 5.14 | 170 | 35.2 | 4.83
1472 | Jetion Solar | JT175SAa/SAb 175 | Jetion Solar : JT175SAa/SAb 175 | -0.4 | 44.2 | 5.2 | 175 | 35.3 | 4.956
1473 | Jetion Solar | JT180SAa/SAb 180 | Jetion Solar : JT180SAa/SAb 180 | -0.4 | 44.8 | 5.3 | 180 | 36 | 5
1474 | Jetion Solar | JT180SEc 180 | Jetion Solar : JT180SEc 180 | -0.43 | 28.6 | 8.4 | 180 | 24 | 7.5
1475 | Jetion Solar | JT180SEc 182 | Jetion Solar : JT180SEc 182 | -0.43 | 29.4 | 8.6 | 190 | 24.7 | 7.7
1476 | Jetion Solar | JT180SEc 183 | Jetion Solar : JT180SEc 183 | -0.43 | 29.8 | 8.7 | 195 | 25.06 | 7.78
1477 | Jetion Solar | JT180SEc 184 | Jetion Solar : JT180SEc 184 | -0.43 | 30.1 | 8.85 | 200 | 25.5 | 7.85
1478 | Jetion Solar | JT180SEc 185 | Jetion Solar : JT180SEc 185 | -0.43 | 29 | 8.5 | 185 | 24.3 | 7.6
1479 | Jetion Solar | JT185SAa/SAb 185 | Jetion Solar : JT185SAa/SAb 185 | -0.4 | 45 | 5.5 | 185 | 36.27 | 5.1
1480 | Jetion Solar | JT190SAa/SAb 190 | Jetion Solar : JT190SAa/SAb 190 | -0.4 | 45.2 | 5.6 | 190 | 36.5 | 5.2
1481 | Jetion Solar | JT210SDc Black 210 | Jetion Solar : JT210SDc Black 210 | -0.37 | 33 | 8.48 | 210 | 27.6 | 7.6
1482 | Jetion Solar | JT215SDc Black 215 | Jetion Solar : JT215SDc Black 215 | -0.37 | 33.3 | 8.6 | 215 | 27.9 | 7.7
1483 | Jetion Solar | JT220SDc Black 220 | Jetion Solar : JT220SDc Black 220 | -0.37 | 33.7 | 8.7 | 220 | 28.2 | 7.8
1484 | Jetion Solar | JT225SDc Black 225 | Jetion Solar : JT225SDc Black 225 | -0.37 | 33.9 | 8.85 | 225 | 28.6 | 7.85
1485 | Jetion Solar | JT230SBa/SBb 230 | Jetion Solar : JT230SBa/SBb 230 | -0.3 | 59 | 5.03 | 230 | 49.2 | 4.67
1486 | Jetion Solar | JT230SDc Black 230 | Jetion Solar : JT230SDc Black 230 | -0.37 | 34.4 | 8.9 | 230 | 29.1 | 7.9
1487 | Jetion Solar | JT235SBa/SBb 235 | Jetion Solar : JT235SBa/SBb 235 | -0.3 | 60.3 | 5.2 | 235 | 49.5 | 4.75
1488 | Jetion Solar | JT240SBa/SBb 240 | Jetion Solar : JT240SBa/SBb 240 | -0.3 | 60.4 | 5.3 | 240 | 50 | 4.8
1489 | Jetion Solar | JT245SBa/SBb 245 | Jetion Solar : JT245SBa/SBb 245 | -0.3 | 61.1 | 5.35 | 245 | 50.5 | 4.85
1490 | Jetion Solar | JT250SBa/SBb 250 | Jetion Solar : JT250SBa/SBb 250 | -0.3 | 61.7 | 5.4 | 250 | 51 | 4.9
1491 | JIAWEI | JW-160 | JIAWEI : JW-160 | -0.367 | 43.3 | 4.74 | 160 | 36.3 | 4.41
1492 | JIAWEI | JW-170 | JIAWEI : JW-170 | -0.36 | 44 | 4.95 | 170 | 36.5 | 4.69
1493 | JIAWEI | JW-200 | JIAWEI : JW-200 | -0.36 | 35.9 | 7.76 | 200 | 29.5 | 6.79
1494 | JIAWEI | JW-210 | JIAWEI : JW-210 | -0.356 | 36.2 | 7.89 | 210 | 30 | 7.02
1495 | Jinko | JKM-170M | Jinko : JKM-170M | -0.35 | 44.3 | 5.12 | 170 | 35.5 | 4.79
1496 | Jinko | JKM-175M | Jinko : JKM-175M | -0.35 | 44.7 | 5.23 | 175 | 35.8 | 4.9
1497 | Jinko | JKM-175M | Jinko : JKM-175M | -0.35 | 44.7 | 5.23 | 175 | 35.8 | 4.9
1498 | Jinko | JKM-180M | Jinko : JKM-180M | -0.35 | 44.8 | 5.29 | 180 | 36 | 5
1499 | Jinko | JKM-185M | Jinko : JKM-185M | -0.35 | 45 | 5.43 | 185 | 36.4 | 5.09
1500 | Jinko | JKM-190M (R165) | Jinko : JKM-190M (R165) | -0.35 | 45.2 | 5.56 | 190 | 36.6 | 5.19
1501 | Jinko | JKM-200M | Jinko : JKM-200M | -0.33 | 55.2 | 4.86 | 200 | 46 | 4.34
1502 | Jinko | JKM-205M | Jinko : JKM-205M | -0.33 | 55.8 | 4.94 | 205 | 46.5 | 4.41
1503 | Jinko | JKM-210M | Jinko : JKM-210M | -0.33 | 56.4 | 5.01 | 210 | 47 | 4.47
1504 | Jinko | JKM-215M | Jinko : JKM-215M | -0.33 | 57 | 5.07 | 215 | 47.5 | 4.53
1505 | Jinko | JKM-220M | Jinko : JKM-220M | -0.33 | 57.6 | 5.13 | 220 | 48 | 4.58
1506 | Jinko | JKM-225M | Jinko : JKM-225M | -0.33 | 57.6 | 5.25 | 225 | 48 | 4.69
1507 | Jinko | JKM-230M | Jinko : JKM-230M | -0.33 | 57.6 | 5.36 | 230 | 48 | 4.79
1508 | Jinko | JKM-235M | Jinko : JKM-235M | -0.33 | 57.6 | 5.48 | 235 | 48 | 4.89
1509 | Jinko | JKM-240M | Jinko : JKM-240M | -0.33 | 57.6 | 5.66 | 240 | 48 | 5
1510 | Jintech Solar | JT-160M | Jintech Solar : JT-160M | -0.38 | 43.8 | 5.15 | 160 | 34.8 | 4.6
1511 | Jintech Solar | JT-160P | Jintech Solar : JT-160P | -0.38 | 42 | 5.2 | 160 | 34.5 | 4.64
1512 | Jintech Solar | JT-165M | Jintech Solar : JT-165M | -0.38 | 44 | 5.25 | 165 | 35.2 | 4.69
1513 | Jintech Solar | JT-165P | Jintech Solar : JT-165P | -0.38 | 42.5 | 5.28 | 165 | 35 | 4.72
1514 | Jintech Solar | JT-170M | Jintech Solar : JT-170M | -0.38 | 44.2 | 5.36 | 170 | 35.5 | 4.79
1515 | Jintech Solar | JT-170P | Jintech Solar : JT-170P | -0.38 | 42.5 | 5.44 | 170 | 35 | 4.86
1516 | Jintech Solar | JT-175M | Jintech Solar : JT-175M | -0.38 | 44.4 | 4.47 | 175 | 35.8 | 4.89
1517 | Jintech Solar | JT-175P | Jintech Solar : JT-175P | -0.38 | 42.5 | 5.6 | 175 | 35 | 5
1518 | Jintech Solar | JT-180M | Jintech Solar : JT-180M | -0.38 | 44.6 | 5.57 | 180 | 36.2 | 4.97
1519 | Jintech Solar | JT-185M | Jintech Solar : JT-185M | -0.38 | 44.8 | 5.68 | 185 | 36.5 | 5.07
1520 | Jintech Solar | JT-210M | Jintech Solar : JT-210M | -0.38 | 35.7 | 8.05 | 210 | 28.7 | 7.32
1521 | Jintech Solar | JT-220M | Jintech Solar : JT-220M | -0.38 | 36.4 | 8.28 | 220 | 29.2 | 7.53
1522 | Jintech Solar | JT-230M | Jintech Solar : JT-230M | -0.38 | 37.2 | 8.49 | 230 | 29.8 | 7.72
1523 | JMS Solar | AS-230P 229Wp | JMS Solar : AS-230P 229Wp | -0.33 | 36.78 | 8.88 | 229 | 28.07 | 8.16
1524 | JMS Solar | AS-230P 233Wp | JMS Solar : AS-230P 233Wp | -0.33 | 37.05 | 8.95 | 233 | 28.28 | 8.24
1525 | JMS Solar | AS-230P 237Wp | JMS Solar : AS-230P 237Wp | -0.33 | 37.37 | 9 | 237 | 28.52 | 8.31
1526 | JMS Solar | AS-230P 241Wp | JMS Solar : AS-230P 241Wp | -0.32 | 37.46 | 9.05 | 241 | 28.76 | 8.38
1527 | JMS Solar | AS-230P 244Wp | JMS Solar : AS-230P 244Wp | -0.32 | 37.56 | 9.1 | 244 | 28.95 | 8.43
1528 | JMS Solar | CS 180M (170Wp) | JMS Solar : CS 180M (170Wp) | -0.34 | 43.5 | 5.2 | 170 | 35.9 | 4.74
1529 | JMS Solar | CS 180M (175Wp) | JMS Solar : CS 180M (175Wp) | -0.34 | 43.8 | 5.28 | 175 | 36.2 | 4.83
1530 | JMS Solar | CS 180M (180Wp) | JMS Solar : CS 180M (180Wp) | -0.34 | 44.2 | 5.35 | 180 | 36.5 | 4.93
1531 | JMS Solar | CS 180M (185Wp) | JMS Solar : CS 180M (185Wp) | -0.34 | 44.4 | 5.47 | 185 | 36.6 | 5.05
1532 | JMS Solar | CS 180M (190Wp) | JMS Solar : CS 180M (190Wp) | -0.34 | 44.7 | 5.58 | 190 | 36.8 | 5.16
1533 | JMS Solar | CS 180P (165Wp) | JMS Solar : CS 180P (165Wp) | -0.34 | 28.8 | 7.7 | 165 | 23.5 | 7.02
1534 | JMS Solar | CS 180P (170Wp) | JMS Solar : CS 180P (170Wp) | -0.34 | 29 | 7.82 | 170 | 23.8 | 7.15
1535 | JMS Solar | CS 180P (175Wp) | JMS Solar : CS 180P (175Wp) | -0.34 | 29.2 | 7.96 | 175 | 24 | 7.29
1536 | JMS Solar | CS 180P (180Wp) | JMS Solar : CS 180P (180Wp) | -0.34 | 29.4 | 8.1 | 180 | 24.1 | 7.47
1537 | JMS Solar | CS 180P (185Wp) | JMS Solar : CS 180P (185Wp) | -0.34 | 29.6 | 8.28 | 185 | 24.2 | 7.64
1538 | JMS Solar | CS 200 (190Wp) | JMS Solar : CS 200 (190Wp) | -0.34 | 32.6 | 7.8 | 190 | 26.7 | 7.12
1539 | JMS Solar | CS 200 (195Wp) | JMS Solar : CS 200 (195Wp) | -0.34 | 32.8 | 7.92 | 195 | 26.9 | 7.25
1540 | JMS Solar | CS 200 (200Wp) | JMS Solar : CS 200 (200Wp) | -0.34 | 33 | 8.02 | 200 | 27.1 | 7.38
1541 | JMS Solar | CS 200 (205Wp) | JMS Solar : CS 200 (205Wp) | -0.34 | 33.2 | 8.15 | 205 | 27.2 | 7.54
1542 | JMS Solar | CS 200 (210Wp) | JMS Solar : CS 200 (210Wp) | -0.34 | 33.4 | 8.28 | 210 | 27.4 | 7.66
1543 | JMS Solar | CS 230 (220Wp) | JMS Solar : CS 230 (220Wp) | -0.34 | 36.6 | 7.98 | 220 | 30 | 7.33
1544 | JMS Solar | CS 230 (225Wp) | JMS Solar : CS 230 (225Wp) | -0.34 | 36.8 | 8.1 | 225 | 30.1 | 7.48
1545 | JMS Solar | CS 230 (230Wp) | JMS Solar : CS 230 (230Wp) | -0.34 | 37 | 8.2 | 230 | 30.3 | 7.6
1546 | JMS Solar | Day 4 48MC 170W | JMS Solar : Day 4 48MC 170W | -0.44 | 28.8 | 7.9 | 170 | 23.04 | 7.38
1547 | JMS Solar | Day 4 48MC 175W | JMS Solar : Day 4 48MC 175W | -0.44 | 29.2 | 8.05 | 175 | 23.4 | 7.48
1548 | JMS Solar | Day 4 48MC 180W | JMS Solar : Day 4 48MC 180W | -0.44 | 29.4 | 8.1 | 180 | 23.7 | 7.6
1549 | JMS Solar | Day 4 48MC 185W | JMS Solar : Day 4 48MC 185W | -0.44 | 29.51 | 8.2 | 185 | 23.82 | 7.77
1550 | JMS Solar | Day 4 48MC 190W | JMS Solar : Day 4 48MC 190W | -0.44 | 29.7 | 8.3 | 190 | 24 | 7.92
1551 | JMS Solar | Day 4 60MC 225W | JMS Solar : Day 4 60MC 225W | -0.44 | 36.65 | 8.15 | 225 | 29.56 | 7.62
1552 | JMS Solar | Day 4 60MC 230W | JMS Solar : Day 4 60MC 230W | -0.44 | 36.89 | 8.2 | 230 | 29.78 | 7.74
1553 | JMS Solar | Day 4 60MC 235W | JMS Solar : Day 4 60MC 235W | -0.44 | 37.21 | 8.3 | 235 | 30.18 | 7.8
1554 | JMS Solar | Day 4 60MC 240W | JMS Solar : Day 4 60MC 240W | -0.44 | 37.3 | 8.35 | 240 | 30.22 | 7.96
1555 | JMS Solar | Day 4 60MC 245W | JMS Solar : Day 4 60MC 245W | -0.44 | 37.42 | 8.4 | 245 | 30.4 | 8.06
1556 | JMS Solar | Day 4 60MC 250W | JMS Solar : Day 4 60MC 250W | -0.44 | 37.55 | 8.45 | 250 | 30.58 | 8.18
1557 | JMS Solar | ES-200 P60 195W | JMS Solar : ES-200 P60 195W | -0.34 | 35.5 | 7.4 | 195 | 28.45 | 6.9
1558 | JMS Solar | ES-200 P60 205W | JMS Solar : ES-200 P60 205W | -0.34 | 36.18 | 7.8 | 205 | 28.85 | 7.15
1559 | JMS Solar | ES-200 P60 210W | JMS Solar : ES-200 P60 210W | -0.34 | 36.35 | 7.92 | 210 | 28.95 | 7.24
1560 | JMS Solar | ES-200 P60 215W | JMS Solar : ES-200 P60 215W | -0.34 | 36.5 | 7.95 | 215 | 28.96 | 7.39
1561 | JMS Solar | ES-200 P60 220W | JMS Solar : ES-200 P60 220W | -0.34 | 36.6 | 8.2 | 220 | 29.2 | 7.5
1562 | JMS Solar | ES-200 P60 225W | JMS Solar : ES-200 P60 225W | -0.34 | 36.75 | 8.29 | 225 | 29.35 | 7.65
1563 | JMS Solar | ES-200 P60 230W | JMS Solar : ES-200 P60 230W | -0.34 | 36.88 | 8.5 | 230 | 29.55 | 7.78
1564 | JMS Solar | ES-200 P60 235W | JMS Solar : ES-200 P60 235W | -0.34 | 37.02 | 8.64 | 235 | 29.75 | 7.89
1565 | JMS Solar | FPB1-195W | JMS Solar : FPB1-195W | -0.35 | 32.69 | 7.89 | 195 | 26.1 | 7.45
1566 | JMS Solar | FPB1-200W | JMS Solar : FPB1-200W | -0.35 | 32.89 | 8.02 | 200 | 26.24 | 7.63
1567 | JMS Solar | FPB1-205W | JMS Solar : FPB1-205W | -0.35 | 33.08 | 8.26 | 205 | 26.52 | 7.76
1568 | JMS Solar | FS-272 72,5Wp | JMS Solar : FS-272 72,5Wp | -0.29 | 90 | 1.19 | 72.5 | 67.9 | 1.07
1569 | JMS Solar | FS-275 75Wp | JMS Solar : FS-275 75Wp | -0.29 | 92 | 1.2 | 75 | 69.4 | 1.08
1570 | JMS Solar | German Power P195 (190Wp) | JMS Solar : German Power P195 (190Wp) | -0.34 | 32.6 | 7.98 | 190 | 25.5 | 7.43
1571 | JMS Solar | German Power P195 (195Wp) | JMS Solar : German Power P195 (195Wp) | -0.34 | 32.8 | 8.1 | 195 | 25.7 | 7.57
1572 | JMS Solar | German Power P195 (200Wp) | JMS Solar : German Power P195 (200Wp) | -0.34 | 33 | 8.22 | 200 | 25.9 | 7.71
1573 | JMS Solar | German Power P205 (205Wp) | JMS Solar : German Power P205 (205Wp) | -0.34 | 33.1 | 8.33 | 205 | 26.1 | 7.85
1574 | JMS Solar | German Power P205 (210Wp) | JMS Solar : German Power P205 (210Wp) | -0.34 | 33.2 | 8.42 | 210 | 26.4 | 7.95
1575 | JMS Solar | German Power P205 (215Wp) | JMS Solar : German Power P205 (215Wp) | -0.34 | 33.4 | 8.54 | 215 | 26.5 | 8.11
1576 | JMS Solar | MiaSole MR-100 | JMS Solar : MiaSole MR-100 | -0.36 | 24.7 | 6.5 | 100 | 19.2 | 5.2
1577 | JMS Solar | MiaSole MR-107 | JMS Solar : MiaSole MR-107 | -0.36 | 25.2 | 6.58 | 107 | 20.1 | 5.33
1578 | JMS Solar | MiaSole MR-111 | JMS Solar : MiaSole MR-111 | -0.36 | 24.9 | 6.8 | 111 | 19.4 | 5.7
1579 | JMS Solar | Sol 180M | JMS Solar : Sol 180M | -0.34 | 42.8 | 5.7 | 180 | 34 | 5.29
1580 | JMS Solar | Sol 610 200W | JMS Solar : Sol 610 200W | -0.34 | 36.94 | 7.59 | 200 | 28.59 | 6.99
1581 | JMS Solar | Sol 610 205W | JMS Solar : Sol 610 205W | -0.34 | 37.04 | 7.68 | 205 | 28.79 | 7.11
1582 | JMS Solar | Sol 610 210W | JMS Solar : Sol 610 210W | -0.34 | 36.25 | 7.78 | 210 | 28.95 | 7.23
1583 | JMS Solar | Sol 610 215W | JMS Solar : Sol 610 215W | -0.34 | 37.35 | 7.88 | 215 | 28.99 | 7.35
1584 | JMS Solar | Sol 610 220W | JMS Solar : Sol 610 220W | -0.34 | 37.45 | 7.96 | 220 | 29.2 | 7.45
1585 | JMS Solar | Sol 610 225W | JMS Solar : Sol 610 225W | -0.34 | 36.65 | 8.05 | 225 | 29.8 | 7.54
1586 | JMS Solar | Sol 610 230W | JMS Solar : Sol 610 230W | -0.34 | 37.76 | 8.13 | 230 | 30.11 | 7.63
1587 | JMS Solar | Sol 610 235W | JMS Solar : Sol 610 235W | -0.34 | 37.86 | 8.21 | 235 | 30.41 | 7.72
1588 | JMS Solar | Sol 610 240W | JMS Solar : Sol 610 240W | -0.34 | 37.96 | 8.29 | 240 | 30.71 | 7.81
1589 | JMS Solar | ST 38 | JMS Solar : ST 38 | -0.32 | 60 | 1.04 | 38 | 44 | 0.86
1590 | JMS Solar | ST 40 | JMS Solar : ST 40 | -0.32 | 61 | 1.08 | 40 | 45 | 0.89
1591 | JMS Solar | ST 42 | JMS Solar : ST 42 | -0.32 | 61.25 | 1.14 | 42 | 46.5 | 1.01
1592 | JMS Solar | ST 44 | JMS Solar : ST 44 | -0.32 | 62 | 1.2 | 44 | 47 | 1.1
1593 | JMS Solar | ST-36 | JMS Solar : ST-36 | -0.32 | 59 | 1.02 | 36 | 43 | 0.84
1594 | Kaneka | BRA | Kaneka : BRA | -0.212 | 40.8 | 1.1 | 28 | 30.2 | 0.93
1595 | Kaneka | K 60 | Kaneka : K 60 | -0.38 | 92 | 1.19 | 60 | 67 | 0.9
1596 | Kaneka | K120-V | Kaneka : K120-V | -0.38 | 92 | 2.38 | 120 | 67 | 1.8
1597 | Kaneka | K54 | Kaneka : K54 | -0.4 | 85 | 1.14 | 54 | 62 | 0.87
1598 | Kaneka | Kaneka K108-H | Kaneka : Kaneka K108-H | -0.35 | 85 | 2.28 | 108 | 62 | 1.74
1599 | Kaneka | Kaneka K108-V | Kaneka : Kaneka K108-V | -0.35 | 85 | 2.28 | 108 | 62 | 1.74
1600 | Kaneka | Kaneka K58 | Kaneka : Kaneka K58 | -0.308 | 85 | 1.12 | 58 | 63 | 0.92
1601 | Kaneka | LSU | Kaneka : LSU | -0.286 | 85 | 1.1 | 58 | 63 | 0.92
1602 | Kaneka | PLE | Kaneka : PLE | -0.283 | 23 | 3.65 | 50 | 16.5 | 3.03
1603 | Kaneka | STU005 | Kaneka : STU005 | -0.4 | 41 | 1 | 30 | 31.6 | 0.95
1604 | Kioto | KPV-PE-NEC-190 | Kioto : KPV-PE-NEC-190 | -0.37 | 32.13 | 7.68 | 190 | 25.91 | 7.38
1605 | Kioto | KPV-PE-NEC-195 | Kioto : KPV-PE-NEC-195 | -0.37 | 32.71 | 8.08 | 195 | 26.08 | 7.49
1606 | Kioto | KPV-PE-NEC-200 | Kioto : KPV-PE-NEC-200 | -0.37 | 32.91 | 8.3 | 200 | 26.34 | 7.63
1607 | Kioto | KPV-PE-NEC-205 | Kioto : KPV-PE-NEC-205 | -0.37 | 33.08 | 8.33 | 205 | 26.39 | 7.8
1608 | Kioto | KPV-PE-NEC-210 | Kioto : KPV-PE-NEC-210 | -0.37 | 33.26 | 8.59 | 210 | 26.47 | 7.96
1609 | KIOTO Photovoltaics | KPV ME EC 210 Wp | KIOTO Photovoltaics : KPV ME EC 210 Wp | -0.37 | 32.06 | 8.86 | 210 | 25.81 | 8.28
1610 | KIOTO Photovoltaics | KPV ME EC 215 Wp | KIOTO Photovoltaics : KPV ME EC 215 Wp | -0.37 | 32.42 | 8.95 | 215 | 25.97 | 8.31
1611 | KIOTO Photovoltaics | KPV ME EC 220 Wp | KIOTO Photovoltaics : KPV ME EC 220 Wp | -0.37 | 32.54 | 9.08 | 220 | 25.99 | 8.49
1612 | KIOTO Photovoltaics | KPV QCells 195 Wp | KIOTO Photovoltaics : KPV QCells 195 Wp | -0.36 | 32.42 | 8.11 | 195 | 25.8 | 7.59
1613 | KIOTO Photovoltaics | KPV QCells 200 Wp | KIOTO Photovoltaics : KPV QCells 200 Wp | -0.36 | 32.51 | 8.27 | 200 | 25.83 | 7.79
1614 | KIOTO Photovoltaics | KPV QCells 205 Wp | KIOTO Photovoltaics : KPV QCells 205 Wp | -0.36 | 32.57 | 8.44 | 205 | 25.98 | 7.93
1615 | KIOTO Photovoltaics | KPV QCells 210 Wp | KIOTO Photovoltaics : KPV QCells 210 Wp | -0.36 | 32.8 | 8.46 | 210 | 26.23 | 8.02
1616 | Koncar Solar | SCH 1,8 W/ 12 V | Koncar Solar : SCH 1,8 W/ 12 V | -0.4 | 22 | 0.14 | 1.8 | 14.5 | 0.11
1617 | Koncar Solar | SCH 12 W/ 12 V | Koncar Solar : SCH 12 W/ 12 V | -0.4 | 22 | 1 | 12 | 14.5 | 0.76
1618 | Koncar Solar | SCH 3,6 W/ 12 V | Koncar Solar : SCH 3,6 W/ 12 V | -0.4 | 22 | 0.32 | 3.6 | 14.5 | 0.24
1619 | Koncar Solar | SCH 6 W/ 12 V | Koncar Solar : SCH 6 W/ 12 V | -0.4 | 22 | 0.5 | 6 | 14.5 | 0.38
1620 | Krasnoe Znamya | MDSR-72/48 (12) | Krasnoe Znamya : MDSR-72/48 (12) | -0.36 | 21.3 | 5.47 | 79 | 17 | 4.65
1621 | Krasnoe Znamya | MDSR-72/48 (24V) | Krasnoe Znamya : MDSR-72/48 (24V) | -0.36 | 42.6 | 6.07 | 79.2 | 34 | 2.32
1622 | Krasnoe Znamya | MDSR-80/54 (12V) | Krasnoe Znamya : MDSR-80/54 (12V) | -0.36 | 21.3 | 6.07 | 88 | 17 | 5.17
1623 | Krasnoe Znamya | MDSR-80/54 (24) | Krasnoe Znamya : MDSR-80/54 (24) | -0.36 | 42.6 | 3.04 | 88 | 34 | 2.59
1624 | Kyocera | KC110-1 | Kyocera : KC110-1 | -0.389 | 21.1 | 7.25 | 110 | 16.5 | 6.67
1625 | Kyocera | KC120 | Kyocera : KC120 | -0.381 | 21.5 | 7.45 | 120 | 16.9 | 7.1
1626 | Kyocera | KC120-1 | Kyocera : KC120-1 | -0.381 | 21.5 | 7.45 | 120 | 16.9 | 7.1
1627 | Kyocera | KC125G-2 | Kyocera : KC125G-2 | -0.35 | 21.7 | 8 | 125 | 17.4 | 7.2
1628 | Kyocera | KC130GHT-2 | Kyocera : KC130GHT-2 | -0.37 | 21.9 | 8.02 | 130 | 17.6 | 7.39
1629 | Kyocera | KC167G-2 | Kyocera : KC167G-2 | -0.35 | 28.9 | 8 | 167 | 23.2 | 7.2
1630 | Kyocera | KC170GHT-2 | Kyocera : KC170GHT-2 | -0.38 | 29 | 8.03 | 170 | 23.4 | 7.27
1631 | Kyocera | KC175GHT-2 | Kyocera : KC175GHT-2 | -0.373 | 29.2 | 8.09 | 175 | 23.6 | 7.42
1632 | Kyocera | KC187G | Kyocera : KC187G | -0.4 | 32.5 | 7.96 | 187 | 26.1 | 7.17
1633 | Kyocera | KC190GHT-2 | Kyocera : KC190GHT-2 | -0.38 | 32.5 | 8.08 | 190 | 26.1 | 7.28
1634 | Kyocera | KC200GHT-2 | Kyocera : KC200GHT-2 | -0.373 | 32.9 | 8.21 | 200 | 26.3 | 7.61
1635 | Kyocera | KC35 | Kyocera : KC35 | -0.4 | 18.8 | 2.5 | 35 | 15 | 2.33
1636 | Kyocera | KC40 | Kyocera : KC40 | -0.381 | 21.5 | 2.48 | 40 | 16.9 | 2.34
1637 | Kyocera | KC40T-1 | Kyocera : KC40T-1 | -0.37 | 21.7 | 2.65 | 40 | 17.4 | 2.48
1638 | Kyocera | KC45 | Kyocera : KC45 | -0.4 | 19.2 | 3.1 | 45 | 15 | 3
1639 | Kyocera | KC50 | Kyocera : KC50 | -0.4 | 21.5 | 3.1 | 50 | 16.7 | 3
1640 | Kyocera | KC50T-1 | Kyocera : KC50T-1 | -0.37 | 21.7 | 3.31 | 50 | 17.4 | 3.11
1641 | Kyocera | KC60 | Kyocera : KC60 | -0.381 | 21.5 | 3.73 | 60 | 16.9 | 3.55
1642 | Kyocera | KC60H | Kyocera : KC60H | -0.4 | 26.4 | 3.1 | 60 | 20.2 | 3
1643 | Kyocera | KC65T-1 | Kyocera : KC65T-1 | -0.37 | 21.7 | 3.99 | 65 | 17.4 | 3.75
1644 | Kyocera | KC70 | Kyocera : KC70 | -0.4 | 21.5 | 4.35 | 70 | 16.9 | 4.14
1645 | Kyocera | KC80 | Kyocera : KC80 | -0.381 | 21.5 | 4.97 | 80 | 16.9 | 4.73
1646 | Kyocera | KC80-02 | Kyocera : KC80-02 | -0.381 | 21.5 | 4.97 | 72 | 16.9 | 4.73
1647 | Kyocera | KC85T-1 | Kyocera : KC85T-1 | -0.37 | 21.7 | 5.34 | 85 | 17.4 | 5.02
1648 | Kyocera | KD135GH-2P | Kyocera : KD135GH-2P | -0.359 | 22.1 | 8.37 | 135 | 17.7 | 7.63
1649 | Kyocera | KD180GH-2P | Kyocera : KD180GH-2P | -0.359 | 29.5 | 8.35 | 180 | 23.6 | 7.63
1650 | Kyocera | KD205GH-2P | Kyocera : KD205GH-2P | -0.361 | 33.2 | 8.36 | 205 | 26.6 | 7.71
1651 | Kyocera | KD210GH-2P | Kyocera : KD210GH-2P | -0.361 | 33.2 | 8.58 | 210 | 26.6 | 7.9
1652 | Kyocera | KS10 | Kyocera : KS10 | -0.4 | 20.7 | 0.66 | 10 | 16.3 | 0.61
1653 | Kyocera | KS10A | Kyocera : KS10A | -0.4 | 21 | 0.9 | 10 | 15.3 | 0.68
1654 | Kyocera | KS12 | Kyocera : KS12 | -0.4 | 19.3 | 0.81 | 12 | 15.5 | 0.75
1655 | Kyocera | KS20 | Kyocera : KS20 | -0.4 | 20.7 | 1.33 | 20 | 16.3 | 1.23
1656 | Kyocera | KS20a | Kyocera : KS20a | -0.4 | 20.7 | 1.06 | 10 | 16.3 | 0.98
1657 | Kyocera | KS24 | Kyocera : KS24 | -0.4 | 19.6 | 1.62 | 24 | 15.7 | 1.5
1658 | Kyocera | KS5 | Kyocera : KS5 | -0.4 | 20.7 | 0.34 | 5 | 16.3 | 0.31
1659 | Kyocera | LA361K51S | Kyocera : LA361K51S | -0.4 | 21.2 | 3.25 | 51 | 16.9 | 3.02
1660 | Kyocera | LA361K54S | Kyocera : LA361K54S | -0.363 | 21.5 | 3.35 | 54.1 | 16.9 | 3.2
1661 | Kyocera | LA441G66S | Kyocera : LA441G66S | -0.365 | 26.3 | 3.35 | 66.2 | 20.7 | 3.2
1662 | Kyocera | LA441K63S | Kyocera : LA441K63S | -0.4 | 26 | 3.25 | 63 | 20.7 | 3.03
1663 | Kyocera | LA721G108S | Kyocera : LA721G108S | -0.365 | 43 | 3.35 | 108.2 | 33.8 | 3.2
1664 | Lafarge Braas | SRT 35 | Lafarge Braas : SRT 35 | -0.37 | 10.7 | 4.55 | 35 | 8.5 | 4.15
1665 | Lafarge Braas | SRT 40 | Lafarge Braas : SRT 40 | -0.37 | 11 | 4.8 | 40 | 8.8 | 4.6
1666 | Lafarge Braas | SRT 80 | Lafarge Braas : SRT 80 | -0.36 | 22.1 | 4.8 | 80 | 17.6 | 4.55
1667 | Lemo Solar | 03-05750 | Lemo Solar : 03-05750 | -0.4 | 4.68 | 0.033 | 0.075 | 3.12 | 0.024
1668 | Lemo Solar | 03-120112 | Lemo Solar : 03-120112 | -0.4 | 4.9 | 0.26 | 0.641 | 3.6 | 0.18
1669 | Lemo Solar | 06-05750 | Lemo Solar : 06-05750 | -0.4 | 9.8 | 0.023 | 0.127 | 7.2 | 0.018
1670 | Lemo Solar | 07-242285 | Lemo Solar : 07-242285 | -0.4 | 11.4 | 0.6 | 3.525 | 8.4 | 0.42
1671 | Lemo Solar | 1,5-05750 | Lemo Solar : 1,5-05750 | -0.4 | 2.34 | 0.07 | 0.075 | 1.56 | 0.048
1672 | Lemo Solar | 15-120112 | Lemo Solar : 15-120112 | -0.4 | 24.5 | 0.048 | 0.677 | 18 | 0.038
1673 | Lemo Solar | 15-285194 | Lemo Solar : 15-285194 | -0.4 | 24.5 | 0.22 | 3.11 | 18 | 0.18
1674 | Lemo Solar | 15-285323 | Lemo Solar : 15-285323 | -0.4 | 24.5 | 0.37 | 5.171 | 18 | 0.29
1675 | Lemo Solar | SM 03-2406 | Lemo Solar : SM 03-2406 | -0.4 | 3.2 | 0.26 | 0.62 | 3 | 0.24
1676 | Lemo Solar | SM 06-120 | Lemo Solar : SM 06-120 | -0.4 | 10.6 | 0.13 | 1.04 | 6 | 0.12
1677 | Lemo Solar | SM 06-180 | Lemo Solar : SM 06-180 | -0.4 | 10.5 | 0.19 | 1.57 | 6 | 0.18
1678 | Lemo Solar | SM 06-90 | Lemo Solar : SM 06-90 | -0.4 | 10.5 | 0.09 | 0.76 | 6 | 0.09
1679 | Lemo Solar | SM 09-45 | Lemo Solar : SM 09-45 | -0.4 | 15.7 | 0.046 | 0.56 | 9 | 0.045
1680 | Lemo Solar | SM 1,5-480 | Lemo Solar : SM 1,5-480 | -0.4 | 1.6 | 0.52 | 0.62 | 1.5 | 0.48
1681 | Lemo Solar | SM 12-120 | Lemo Solar : SM 12-120 | -0.4 | 21 | 0.13 | 2.07 | 12 | 0.12
1682 | Lemo Solar | SM 12-1770 | Lemo Solar : SM 12-1770 | -0.4 | 22 | 1.88 | 30 | 12 | 1.77
1683 | Lemo Solar | SM 12-190 | Lemo Solar : SM 12-190 | -0.4 | 21 | 0.2 | 3.23 | 12 | 0.19
1684 | Lemo Solar | SM 12-440 | Lemo Solar : SM 12-440 | -0.4 | 22 | 0.47 | 7.5 | 12 | 0.44
1685 | Lemo Solar | SM 12-880 | Lemo Solar : SM 12-880 | -0.4 | 22 | 0.94 | 15 | 12 | 0.88
1686 | Lemo Solar | SM 12-90 | Lemo Solar : SM 12-90 | -0.4 | 21 | 0.093 | 1.52 | 12 | 0.09
1687 | Lemo Solar | SM 6-1770 | Lemo Solar : SM 6-1770 | -0.4 | 11 | 1.88 | 15 | 6 | 1.77
1688 | Lemo Solar | SM 6-460 | Lemo Solar : SM 6-460 | -0.4 | 11 | 0.47 | 3.7 | 6 | 0.44
1689 | Lemo Solar | SM 6-880 | Lemo Solar : SM 6-880 | -0.4 | 11 | 0.94 | 7.5 | 6 | 0.88
1690 | LIGITEC | LM200BB00 | LIGITEC : LM200BB00 | -0.364 | 36.24 | 7.62 | 200 | 28.44 | 7.04
1691 | LIGITEC | LM210BB00 | LIGITEC : LM210BB00 | -0.368 | 35.9 | 7.76 | 210 | 28.97 | 7.25
1692 | LIGITEC | LM215BB00 | LIGITEC : LM215BB00 | -0.359 | 36.72 | 8 | 215 | 28.55 | 7.54
1693 | LIGITEC | LM220BB00 | LIGITEC : LM220BB00 | -0.358 | 36.9 | 7.85 | 220 | 30.2 | 7.32
1694 | Ligitek Electronics | LM1805S00 | Ligitek Electronics : LM1805S00 | -0.4 | 44.87 | 5.22 | 180 | 37.16 | 4.83
1695 | LINUO photovoltaic | LNGF-100 | LINUO photovoltaic : LNGF-100 | -0.4 | 21.5 | 6.5 | 100 | 17 | 5.8
1696 | LINUO photovoltaic | LNGF-120 | LINUO photovoltaic : LNGF-120 | -0.4 | 24.5 | 7.45 | 120 | 17 | 7.05
1697 | LINUO photovoltaic | LNGF-160 | LINUO photovoltaic : LNGF-160 | -0.4 | 42.6 | 5.53 | 160 | 34.65 | 4.63
1698 | LINUO photovoltaic | LNGF-180 | LINUO photovoltaic : LNGF-180 | -0.4 | 44.06 | 5.08 | 180 | 37.02 | 4.86
1699 | MAAß | TJS 38W 40D | MAAß : TJS 38W 40D | -0.4 | 60 | 1 | 38 | 45 | 0.85
1700 | MAGE POWERTEC | Plus 170 / 5 ME | MAGE POWERTEC : Plus 170 / 5 ME | -0.34 | 29.53 | 5.32 | 170 | 23.92 | 7.74
1701 | MAGE POWERTEC | Plus 175 / 5 ME | MAGE POWERTEC : Plus 175 / 5 ME | -0.34 | 43.4 | 5.2 | 175 | 35 | 4.85
1702 | MAGE POWERTEC | Plus 180 / 5 ME | MAGE POWERTEC : Plus 180 / 5 ME | -0.34 | 43.8 | 5.3 | 180 | 35.3 | 4.95
1703 | MAGE POWERTEC | Plus 185 / 5 ME | MAGE POWERTEC : Plus 185 / 5 ME | -0.38 | 44.5 | 5.5 | 185 | 35.9 | 5.15
1704 | MAGE POWERTEC | Plus 220 / 6 PH | MAGE POWERTEC : Plus 220 / 6 PH | -0.34 | 36.3 | 7.97 | 220 | 29.2 | 7.53
1705 | MAGE POWERTEC | Plus 225 / 6 PH | MAGE POWERTEC : Plus 225 / 6 PH | -0.34 | 36.4 | 8.13 | 225 | 29.3 | 7.68
1706 | MAGE POWERTEC | Plus 230 / 6 PH | MAGE POWERTEC : Plus 230 / 6 PH | -0.34 | 36.4 | 8.31 | 230 | 29.4 | 7.82
1707 | MAGE POWERTEC | Plus 235 / 5 MJ | MAGE POWERTEC : Plus 235 / 5 MJ | -0.347 | 60.3 | 5.2 | 235 | 49.5 | 4.75
1708 | MAGE POWERTEC | Plus 240 / 5 MJ | MAGE POWERTEC : Plus 240 / 5 MJ | -0.347 | 60.4 | 5.3 | 240 | 50 | 4.8
1709 | MAGE POWERTEC | Plus 245 / 5 MJ | MAGE POWERTEC : Plus 245 / 5 MJ | -0.347 | 61.1 | 5.35 | 245 | 50.5 | 4.85
1710 | MAGE POWERTEC | Plus 250 / 5 MI | MAGE POWERTEC : Plus 250 / 5 MI | -0.33 | 59.9 | 5.61 | 250 | 49.6 | 5.05
1711 | MAGE POWERTEC | Plus 250 / 5 MR | MAGE POWERTEC : Plus 250 / 5 MR | -0.347 | 61.2 | 5.38 | 250 | 51.25 | 4.88
1712 | MAGE POWERTEC | Plus 255 / 5 MI | MAGE POWERTEC : Plus 255 / 5 MI | -0.33 | 60.5 | 5.66 | 255 | 50 | 5.1
1713 | MAGE POWERTEC | Plus 255 / 5 MR | MAGE POWERTEC : Plus 255 / 5 MR | -0.347 | 61.3 | 5.4 | 255 | 51.35 | 4.97
1714 | MAGE POWERTEC | Plus 265 / 6 PH | MAGE POWERTEC : Plus 265 / 6 PH | -0.34 | 43.8 | 7.98 | 265 | 35.2 | 7.53
1715 | MAGE POWERTEC | Plus 270 / 6 PH | MAGE POWERTEC : Plus 270 / 6 PH | -0.34 | 43.9 | 8.09 | 270 | 35.4 | 7.63
1716 | MAGE POWERTEC | Plus 275 / 6 PH | MAGE POWERTEC : Plus 275 / 6 PH | -0.34 | 44 | 8.11 | 275 | 35.6 | 7.73
1717 | MAGE POWERTEC | Solid 100 / AC | MAGE POWERTEC : Solid 100 / AC | -0.32 | 100 | 1.65 | 100 | 76 | 1.32
1718 | Martifer Solar | MTS-215P | Martifer Solar : MTS-215P | -0.36 | 36.47 | 8.06 | 215 | 28.12 | 7.65
1719 | Martifer Solar | MTS-220P | Martifer Solar : MTS-220P | -0.36 | 36.93 | 8.18 | 220 | 28.32 | 7.81
1720 | Martifer Solar | MTS-225P | Martifer Solar : MTS-225P | -0.36 | 37.11 | 8.32 | 225 | 28.71 | 7.87
1721 | Martifer Solar | MTS-230P | Martifer Solar : MTS-230P | -0.36 | 37.35 | 8.33 | 230 | 28.93 | 7.79
1722 | MEREG | PE 110 | MEREG : PE 110 | -0.36 | 21 | 7.2 | 110 | 16.4 | 6.7
1723 | MEREG | PE 125 | MEREG : PE 125 | -0.35 | 21.8 | 8.1 | 123 | 17.2 | 7.17
1724 | MEREG | PE 90-16 | MEREG : PE 90-16 | -0.35 | 21.2 | 5.9 | 90 | 16.4 | 5.5
1725 | MEREG | PE 90-32 | MEREG : PE 90-32 | -0.35 | 42.4 | 2.95 | 90 | 32.8 | 2.75
1726 | MEREG | PM 130 | MEREG : PM 130 | -0.37 | 41.6 | 4.5 | 130 | 32.5 | 4
1727 | MEREG | PM 150-17 | MEREG : PM 150-17 | -0.35 | 21.24 | 9.72 | 150 | 17.28 | 8.8
1728 | MEREG | PM 160 | MEREG : PM 160 | -0.34 | 43.1 | 5.1 | 160 | 34.7 | 4.6
1729 | MEREG | PM 170 | MEREG : PM 170 | -0.34 | 43.6 | 5.1 | 170 | 36.17 | 4.7
1730 | MEREG | PM 180 | MEREG : PM 180 | -0.339 | 43.7 | 5.13 | 180 | 37.02 | 4.86
1731 | MEREG | PM 75 | MEREG : PM 75 | -0.35 | 21.4 | 5 | 75 | 17 | 4.4
1732 | MEREG | PM150 / PM150a -34 | MEREG : PM150 / PM150a -34 | -0.35 | 42.48 | 4.86 | 151.9 | 34.5 | 4.4
1733 | MHH | plus 180 (175 wp) | MHH : plus 180 (175 wp) | -0.354 | 24.5 | 9.12 | 175 | 20.1 | 8.7
1734 | MHH | plus 180 (180 wp) | MHH : plus 180 (180 wp) | -0.353 | 24.6 | 9.34 | 180 | 20.2 | 8.91
1735 | MHH | power 65 | MHH : power 65 | -0.4 | 40 | 2.76 | 65 | 27.9 | 2.33
1736 | MHI | MA100 I | MHI : MA100 I | -0.33 | 141 | 1.17 | 100 | 108 | 0.93
1737 | Microsol | M-1206 | Microsol : M-1206 | -0.4 | 20 | 4.86 | 75 | 16 | 4.3
1738 | Microsol | M-1431 | Microsol : M-1431 | -0.4 | 20 | 6.5 | 100 | 16 | 6.1
1739 | Mitsubishi | MA100T2 | Mitsubishi : MA100T2 | -0.33 | 141 | 1.17 | 100 | 108 | 0.93
1740 | Mitsubishi | PV-AD/UD/TD 175MF5 | Mitsubishi : PV-AD/UD/TD 175MF5 | -0.346 | 30.2 | 7.93 | 175 | 23.9 | 7.32
1741 | Mitsubishi | PV-AD/UD/TD 180MF5 | Mitsubishi : PV-AD/UD/TD 180MF5 | -0.346 | 30.4 | 8.03 | 180 | 24.2 | 7.45
1742 | Mitsubishi | PV-AD/UD/TD 185MF5 | Mitsubishi : PV-AD/UD/TD 185MF5 | -0.346 | 30.6 | 8.13 | 185 | 24.4 | 7.58
1743 | Mitsubishi | PV-AD/UD/TD 190MF5 | Mitsubishi : PV-AD/UD/TD 190MF5 | -0.346 | 30.8 | 8.23 | 190 | 24.7 | 7.71
1744 | Mitsubishi | PV-MF110EC3 110Wp | Mitsubishi : PV-MF110EC3 110Wp | -0.36 | 21.2 | 7.16 | 110 | 17.1 | 6.43
1745 | Mitsubishi | PV-MF115UE4N | Mitsubishi : PV-MF115UE4N | -0.343 | 21.5 | 7.6 | 115 | 17.1 | 6.75
1746 | Mitsubishi | PV-MF120EC3 120Wp | Mitsubishi : PV-MF120EC3 120Wp | -0.36 | 22 | 7.36 | 120 | 17.6 | 6.82
1747 | Mitsubishi | PV-MF120UE4N | Mitsubishi : PV-MF120UE4N | -0.343 | 21.6 | 7.75 | 120 | 17.2 | 6.99
1748 | Mitsubishi | PV-MF125EA2LF 125Wp | Mitsubishi : PV-MF125EA2LF 125Wp | -0.36 | 24 | 7.27 | 125 | 18.8 | 6.63
1749 | Mitsubishi | PV-MF125UE4N | Mitsubishi : PV-MF125UE4N | -0.343 | 21.8 | 7.9 | 125 | 17.3 | 7.23
1750 | Mitsubishi | PV-MF130EA2LF 130Wp | Mitsubishi : PV-MF130EA2LF 130Wp | -0.36 | 24.2 | 7.39 | 130 | 19.2 | 6.79
1751 | Mitsubishi | PV-MF130UE4N | Mitsubishi : PV-MF130UE4N | -0.343 | 21.9 | 8.05 | 130 | 17.4 | 7.47
1752 | Mitsubishi | PV-MF160EB3 160Wp | Mitsubishi : PV-MF160EB3 160Wp | -0.36 | 30.2 | 7.34 | 160 | 23.8 | 6.72
1753 | Mitsubishi | PV-MF165EB3 165Wp | Mitsubishi : PV-MF165EB3 165Wp | -0.36 | 30.4 | 7.36 | 165 | 24.2 | 6.83
1754 | Mitsubishi | PV-MF170TD4 | Mitsubishi : PV-MF170TD4 | -0.346 | 29.9 | 7.83 | 170 | 23.7 | 7.19
1755 | Mitsubishi | PV-MF175TD4 | Mitsubishi : PV-MF175TD4 | -0.346 | 30.2 | 7.93 | 175 | 23.9 | 7.32
1756 | Mitsubishi | PV-MF180TD4 | Mitsubishi : PV-MF180TD4 | -0.346 | 30.4 | 8.03 | 180 | 24.2 | 7.45
1757 | Mitsubishi | PV-MF185TD4 | Mitsubishi : PV-MF185TD4 | -0.346 | 30.6 | 8.13 | 185 | 24.4 | 7.58
1758 | Mitsubishi | PV-TJ210GA6 | Mitsubishi : PV-TJ210GA6 | -0.34 | 35.8 | 8 | 210 | 29.2 | 7.19
1759 | Mitsubishi | PV-TJ220GA6 | Mitsubishi : PV-TJ220GA6 | -0.34 | 36.2 | 8.2 | 220 | 29.7 | 7.39
1760 | Mitsubishi | PV-TJ225GA6 | Mitsubishi : PV-TJ225GA6 | -0.34 | 36.4 | 8.3 | 225 | 30 | 7.5
1761 | Mitsubishi | PV-TJ230GA6 | Mitsubishi : PV-TJ230GA6 | -0.34 | 36.6 | 8.39 | 230 | 30.2 | 7.62
1762 | Mitsubishi | PV-TJ235GA6 | Mitsubishi : PV-TJ235GA6 | -0.34 | 36.8 | 8.49 | 235 | 30.5 | 7.71
1763 | Mitsubishi | PV-UE115MF5N | Mitsubishi : PV-UE115MF5N | -0.34 | 21.5 | 7.6 | 115 | 17.1 | 6.75
1764 | Mitsubishi | PV-UE120MF5N | Mitsubishi : PV-UE120MF5N | -0.34 | 21.6 | 7.75 | 120 | 17.2 | 6.99
1765 | Mitsubishi | PV-UE125MF5N | Mitsubishi : PV-UE125MF5N | -0.34 | 21.8 | 7.9 | 125 | 17.3 | 7.23
1766 | Mitsubishi | PV-UE130MF5N | Mitsubishi : PV-UE130MF5N | -0.34 | 21.9 | 8.05 | 130 | 17.4 | 7.47
1767 | Mitsubishi | Superstratum Type 120 W | Mitsubishi : Superstratum Type 120 W | -0.347 | 23.9 | 6.89 | 120 | 19 | 6.3
1768 | Mitsubishi | Superstratum Type 123 W | Mitsubishi : Superstratum Type 123 W | -0.346 | 24 | 7.01 | 123 | 19.1 | 6.42
1769 | Mitsubishi | Superstratum Type 140 W | Mitsubishi : Superstratum Type 140 W | -0.396 | 24.5 | 7.66 | 140 | 19.6 | 7.15
1770 | Moser Baer | MBPV-CAAP 200 | Moser Baer : MBPV-CAAP 200 | -0.34 | 36.25 | 7.7 | 200 | 28.78 | 6.95
1771 | Moser Baer | MBPV-CAAP 205 | Moser Baer : MBPV-CAAP 205 | -0.34 | 36.3 | 7.72 | 205 | 28.87 | 7.1
1772 | Moser Baer | MBPV-CAAP 210 | Moser Baer : MBPV-CAAP 210 | -0.34 | 36.36 | 7.74 | 210 | 29.37 | 7.15
1773 | Moser Baer | MBPV-CAAP 215 | Moser Baer : MBPV-CAAP 215 | -0.34 | 36.44 | 7.79 | 215 | 29.86 | 7.2
1774 | Moser Baer | MBPV-CAAP 220 | Moser Baer : MBPV-CAAP 220 | -0.34 | 36.52 | 7.84 | 220 | 30.35 | 7.25
1775 | Moser Baer | MBPV-CAAP 225 | Moser Baer : MBPV-CAAP 225 | -0.34 | 36.68 | 7.91 | 225 | 30.57 | 7.36
1776 | Moser Baer | MBPV-CAAP 230 | Moser Baer : MBPV-CAAP 230 | -0.34 | 36.83 | 7.95 | 230 | 30.91 | 7.44
1777 | Moser Baer Solar | MBPV CAAP 180W | Moser Baer Solar : MBPV CAAP 180W | -0.34 | 36.1 | 7.55 | 180 | 26.95 | 6.68
1778 | Moser Baer Solar | MBPV CAAP 185W | Moser Baer Solar : MBPV CAAP 185W | -0.34 | 36.15 | 7.62 | 185 | 27.53 | 6.72
1779 | Moser Baer Solar | MBPV CAAP 190W | Moser Baer Solar : MBPV CAAP 190W | -0.34 | 36.18 | 7.65 | 190 | 27.94 | 6.8
1780 | Moser Baer Solar | MBPV CAAP 195W | Moser Baer Solar : MBPV CAAP 195W | -0.34 | 36.2 | 7.68 | 195 | 28.47 | 6.85
1781 | Moser Baer Solar | MBPV CAAP 200W | Moser Baer Solar : MBPV CAAP 200W | -0.34 | 35.99 | 7.65 | 200 | 28.81 | 6.97
1782 | Moser Baer Solar | MBPV CAAP 205W | Moser Baer Solar : MBPV CAAP 205W | -0.34 | 35.92 | 7.71 | 205 | 28.9 | 7.11
1783 | Moser Baer Solar | MBPV CAAP 210W | Moser Baer Solar : MBPV CAAP 210W | -0.34 | 36.02 | 7.85 | 210 | 29.12 | 7.21
1784 | Moser Baer Solar | MBPV CAAP 215W | Moser Baer Solar : MBPV CAAP 215W | -0.34 | 36.21 | 7.93 | 215 | 29.21 | 7.36
1785 | Moser Baer Solar | MBPV CAAP 220W | Moser Baer Solar : MBPV CAAP 220W | -0.34 | 36.46 | 8 | 220 | 29.42 | 7.47
1786 | Moser Baer Solar | MBPV CAAP 225W | Moser Baer Solar : MBPV CAAP 225W | -0.34 | 36.85 | 8.09 | 225 | 29.8 | 7.55
1787 | Moser Baer Solar | MBPV CAAP 230W | Moser Baer Solar : MBPV CAAP 230W | -0.34 | 37.11 | 8.18 | 230 | 30.12 | 7.62
1788 | Moser Baer Solar | MBPV CAAP 235W | Moser Baer Solar : MBPV CAAP 235W | -0.34 | 37.34 | 8.24 | 235 | 30.59 | 7.68
1789 | Moser Baer Solar | MBPV CAAP 240W | Moser Baer Solar : MBPV CAAP 240W | -0.34 | 37.69 | 8.34 | 240 | 30.8 | 7.8
1790 | Moserbaer | MBPV CAAP 200Wp | Moserbaer : MBPV CAAP 200Wp | -0.35 | 36.05 | 7.7 | 200 | 28.6 | 7.15
1791 | Moserbaer | MBPV CAAP 210Wp | Moserbaer : MBPV CAAP 210Wp | -0.35 | 36.2 | 7.7 | 210 | 28.7 | 7.4
1792 | Moserbaer | MBPV CAAP 220Wp | Moserbaer : MBPV CAAP 220Wp | -0.35 | 36.2 | 7.72 | 220 | 28.8 | 7.5
1793 | Moserbaer | MBPV CAAP 230Wp | Moserbaer : MBPV CAAP 230Wp | -0.35 | 36.3 | 7.75 | 230 | 29 | 7.6
1794 | Moserbaer | MBPV Max 156 180Wp | Moserbaer : MBPV Max 156 180Wp | -0.35 | 35.5 | 7.4 | 180 | 27 | 6.6
1795 | Moserbaer | MBPV Max 156 190Wp | Moserbaer : MBPV Max 156 190Wp | -0.35 | 35.7 | 7.4 | 190 | 27.7 | 6.8
1796 | Moserbaer | MBPV Max 156 200Wp | Moserbaer : MBPV Max 156 200Wp | -0.35 | 35.9 | 7.5 | 200 | 28 | 7
1797 | Moserbaer | MBPV Serie 125 130Wp | Moserbaer : MBPV Serie 125 130Wp | -0.35 | 36 | 4.9 | 130 | 28.5 | 4.5
1798 | Moserbaer | MBPV-P-Max 60/156 200Wp | Moserbaer : MBPV-P-Max 60/156 200Wp | -0.35 | 35.98 | 7.58 | 200 | 28.54 | 7
1799 | Moserbaer | MBTF 85Wp | Moserbaer : MBTF 85Wp | -0.33 | 94 | 1.43 | 85 | 74.5 | 1.11
1800 | Moserbear | MBTF-340-BIN>360w | Moserbear : MBTF-340-BIN>360w | -0.33 | 191.7 | 3.13 | 431 | 154.6 | 2.79
1801 | Moserbear | MBTF-340-BIN330+15w | Moserbear : MBTF-340-BIN330+15w | -0.33 | 192 | 2.9 | 395 | 151.6 | 2.6
1802 | Moserbear | MBTF-340-BIN345+15w | Moserbear : MBTF-340-BIN345+15w | -0.33 | 171.7 | 3 | 413 | 152 | 2.7
1803 | Moserbear | MBTF-85- 86w | Moserbear : MBTF-85- 86w | -0.33 | 94.4 | 1.55 | 103 | 76.1 | 1.36
1804 | Moserbear | MBTF-85-84w | Moserbear : MBTF-85-84w | -0.33 | 94.6 | 1.51 | 101 | 76.1 | 1.32
1805 | Moserbear | MBTF-85-88w | Moserbear : MBTF-85-88w | -0.33 | 94.7 | 1.57 | 105 | 77 | 1.37
1806 | MSK Corporation | LPP 155-170 | MSK Corporation : LPP 155-170 | -0.331 | 29 | 8.27 | 170 | 23.4 | 7.27
1807 | MSK Corporation | LPP125-120 | MSK Corporation : LPP125-120 | -0.334 | 32.3 | 5.3 | 120 | 25.8 | 4.64
1808 | MSK Corporation | LPP125-160 | MSK Corporation : LPP125-160 | -0.335 | 43 | 5.3 | 160 | 34.5 | 4.64
1809 | MSK Corporation | LPS 125-135 | MSK Corporation : LPS 125-135 | -0.322 | 33.5 | 5.68 | 135 | 26.6 | 5.05
1810 | MSK Corporation | LPS 125-180 | MSK Corporation : LPS 125-180 | -0.323 | 44.6 | 5.68 | 180 | 35.6 | 5.05
1811 | MSK Corporation | TFC210-W | MSK Corporation : TFC210-W | -0.342 | 33.3 | 8.64 | 210 | 26.7 | 7.87
1812 | MSK Corporation | TP 156-190 | MSK Corporation : TP 156-190 | -0.347 | 33 | 8.08 | 190 | 26.5 | 7.18
1813 | MSK Corporation | TS 156-210 | MSK Corporation : TS 156-210 | -0.342 | 33.3 | 8.64 | 210 | 26.7 | 7.87
1814 | MX GROUP | suncase MX48-175 | MX GROUP : suncase MX48-175 | -0.33 | 33.1 | 7.93 | 175 | 25.7 | 7.36
1815 | MX GROUP | suncase MX54-200 | MX GROUP : suncase MX54-200 | -0.33 | 29.17 | 8 | 200 | 22.3 | 7.49
1816 | MX GROUP | suncase MX60-210 | MX GROUP : suncase MX60-210 | -0.33 | 36.9 | 8.05 | 210 | 28.3 | 7.42
1817 | MX GROUP | suncase MX60-220 | MX GROUP : suncase MX60-220 | -0.33 | 37.1 | 8.29 | 220 | 28.5 | 7.72
1818 | MX GROUP | suncase MX60-230 | MX GROUP : suncase MX60-230 | -0.33 | 37.7 | 8.54 | 230 | 29 | 7.93
1819 | MX GROUP | suncase MX60-240 | MX GROUP : suncase MX60-240 | -0.33 | 38 | 8.73 | 240 | 29.5 | 8.14
1820 | Naps Systems Oy | NM 120 A | Naps Systems Oy : NM 120 A | -0.4 | 21 | 7.7 | 120 | 16.9 | 7.1
1821 | Naps Systems Oy | NM 25 S | Naps Systems Oy : NM 25 S | -0.4 | 21 | 1.65 | 25 | 16.5 | 1.5
1822 | Naps Systems Oy | NM 27 G | Naps Systems Oy : NM 27 G | -0.4 | 21.7 | 1.75 | 27 | 17.4 | 1.5
1823 | Naps Systems Oy | NM 27 GT | Naps Systems Oy : NM 27 GT | -0.4 | 21.7 | 1.75 | 27 | 17.4 | 1.55
1824 | Naps Systems Oy | NM 38 G | Naps Systems Oy : NM 38 G | -0.4 | 21.9 | 2.5 | 38 | 17.1 | 2.2
1825 | Naps Systems Oy | NM 55 G | Naps Systems Oy : NM 55 G | -0.4 | 21.7 | 3.5 | 55 | 17.4 | 3.16
1826 | Naps Systems Oy | NM 55 GK | Naps Systems Oy : NM 55 GK | -0.4 | 21.7 | 3.5 | 55 | 17.4 | 3.16
1827 | Naps Systems Oy | NM 55 S | Naps Systems Oy : NM 55 S | -0.4 | 21.7 | 3.4 | 55 | 17.4 | 3.15
1828 | Naps Systems Oy | NM 65 A | Naps Systems Oy : NM 65 A | -0.4 | 20.5 | 4.7 | 65 | 16.3 | 4
1829 | Naps Systems Oy | NM 75 A | Naps Systems Oy : NM 75 A | -0.4 | 21 | 4.8 | 75 | 17 | 4.4
1830 | Naps Systems Oy | NM 75 G | Naps Systems Oy : NM 75 G | -0.4 | 21.9 | 5.05 | 75 | 17.1 | 4.4
1831 | Naps Systems Oy | NP 100 G/12 | Naps Systems Oy : NP 100 G/12 | -0.4 | 21.6 | 6.7 | 100 | 16.7 | 6
1832 | Naps Systems Oy | NP 110 G/12 | Naps Systems Oy : NP 110 G/12 | -0.4 | 21.7 | 6.8 | 110 | 17.4 | 6.3
1833 | Naps Systems Oy | NP 12 RSS | Naps Systems Oy : NP 12 RSS | -0.4 | 21.6 | 0.8 | 12 | 16.7 | 0.7
1834 | Naps Systems Oy | NP 120 GK | Naps Systems Oy : NP 120 GK | -0.4 | 22 | 7.4 | 120 | 17.4 | 6.9
1835 | Naps Systems Oy | NP 150 G | Naps Systems Oy : NP 150 G | -0.4 | 42.2 | 5 | 150 | 32.8 | 4.6
1836 | Naps Systems Oy | NP 165 G | Naps Systems Oy : NP 165 G | -0.4 | 43.4 | 5.1 | 165 | 34.7 | 4.8
1837 | Naps Systems Oy | NP 20 S | Naps Systems Oy : NP 20 S | -0.4 | 21 | 1.3 | 20 | 16.5 | 1.2
1838 | Naps Systems Oy | NP 24 RSS | Naps Systems Oy : NP 24 RSS | -0.4 | 21.6 | 1.61 | 24 | 16.7 | 1.4
1839 | Naps Systems Oy | NP 35 RSS | Naps Systems Oy : NP 35 RSS | -0.4 | 21.1 | 2.31 | 35 | 16.4 | 2.13
1840 | Naps Systems Oy | NP 50 G | Naps Systems Oy : NP 50 G | -0.4 | 21.6 | 3.35 | 50 | 16.7 | 3
1841 | Naps Systems Oy | NP 50 GK | Naps Systems Oy : NP 50 GK | -0.4 | 21.6 | 3.35 | 50 | 16.7 | 3
1842 | Naps Systems Oy | NP 50 RSS | Naps Systems Oy : NP 50 RSS | -0.4 | 21.1 | 3.2 | 50 | 16.7 | 3
1843 | Naps Systems Oy | NP 61 GK | Naps Systems Oy : NP 61 GK | -0.4 | 26.3 | 3.35 | 61 | 20.4 | 3
1844 | Naps Systems Oy | NP 63 K | Naps Systems Oy : NP 63 K | -0.4 | 26 | 3.25 | 63 | 20.7 | 3.03
1845 | Naps Systems Oy | NP 75 G | Naps Systems Oy : NP 75 G | -0.4 | 21.1 | 4.95 | 75 | 16.4 | 4.57
1846 | Naps Systems Oy | NP 75 GK | Naps Systems Oy : NP 75 GK | -0.4 | 21.1 | 5 | 75 | 16.4 | 4.6
1847 | Naps Systems Oy | NP 85 GK | Naps Systems Oy : NP 85 GK | -0.4 | 21.7 | 5.2 | 85 | 17.4 | 4.9
1848 | Naps Systems Oy | NP125GK | Naps Systems Oy : NP125GK | -0.37 | 21.9 | 7.9 | 125 | 17.1 | 7.3
1849 | Naps Systems Oy | NP130GK | Naps Systems Oy : NP130GK | -0.37 | 22.1 | 8.1 | 130 | 17.3 | 7.5
1850 | Naps Systems Oy | NP195GK | Naps Systems Oy : NP195GK | -0.37 | 33.1 | 8.1 | 195 | 26 | 7.5
1851 | Naps Systems Oy | NP200GK | Naps Systems Oy : NP200GK | -0.37 | 33.4 | 8.2 | 200 | 26.2 | 7.63
1852 | Naps Systems Oy | NR 100 G/12 | Naps Systems Oy : NR 100 G/12 | -0.4 | 21.1 | 6.5 | 100 | 16.7 | 6
1853 | Naps Systems Oy | NR 100 G/24 | Naps Systems Oy : NR 100 G/24 | -0.341 | 42.2 | 3.23 | 100 | 33.3 | 3
1854 | Naps Systems Oy | NR 50 G | Naps Systems Oy : NR 50 G | -0.4 | 21.1 | 3.2 | 50 | 16.7 | 3
1855 | Naps Systems Oy | NR 50 GK (12V) | Naps Systems Oy : NR 50 GK (12V) | -0.34 | 21.1 | 3.2 | 50 | 16.7 | 3
1856 | Naps Systems Oy | NR 61 GK | Naps Systems Oy : NR 61 GK | -0.4 | 25.8 | 3.2 | 61 | 20.4 | 3
1857 | Naps Systems Oy | NT 13 N | Naps Systems Oy : NT 13 N | -0.4 | 22 | 0.8 | 12 | 17.3 | 0.6
1858 | Nelumbo | TPS-155M | Nelumbo : TPS-155M | -0.38 | 43.2 | 4.8 | 155 | 34.4 | 4.5
1859 | Nelumbo | TPS-160M 12V | Nelumbo : TPS-160M 12V | -0.38 | 21.6 | 9.8 | 160 | 17.2 | 9.3
1860 | Nelumbo | TPS-160M 24V | Nelumbo : TPS-160M 24V | -0.38 | 43.2 | 4.9 | 160 | 34.2 | 4.65
1861 | NexPower | NT-130AX | NexPower : NT-130AX | -0.32 | 77.6 | 2.45 | 130 | 62.2 | 2.09
1862 | NexPower | NT-135AX | NexPower : NT-135AX | -0.32 | 78.4 | 2.52 | 135 | 62.3 | 2.17
1863 | NexPower | NT-140AX | NexPower : NT-140AX | -0.32 | 78.4 | 2.59 | 140 | 62.3 | 2.25
1864 | NexPower | NT-145AX | NexPower : NT-145AX | -0.32 | 78.4 | 2.67 | 145 | 62.5 | 2.32
1865 | Ningbo Ardson | SL180CE-36M | Ningbo Ardson : SL180CE-36M | -0.38 | 44.71 | 5.1 | 180 | 37.72 | 4.77
1866 | Ningbo Qixin | SL240CE-48M | Ningbo Qixin : SL240CE-48M | -0.38 | 59.61 | 5.1 | 240 | 50.3 | 4.77
1867 | Ningbo Solar | TDB103x103-72-P 100Wp | Ningbo Solar : TDB103x103-72-P 100Wp | -0.35 | 43.2 | 3.26 | 100 | 34.2 | 2.92
1868 | Ningbo Solar | TDB103x103-72-P 110Wp | Ningbo Solar : TDB103x103-72-P 110Wp | -0.35 | 43.4 | 3.47 | 110 | 34.6 | 3.18
1869 | Ningbo Solar | TDB125x125-72-P 140Wp | Ningbo Solar : TDB125x125-72-P 140Wp | -0.35 | 42.6 | 4.75 | 140 | 33.6 | 4.17
1870 | Ningbo Solar | TDB125x125-72-P 145Wp | Ningbo Solar : TDB125x125-72-P 145Wp | -0.35 | 42.8 | 4.88 | 145 | 33.6 | 4.32
1871 | Ningbo Solar | TDB125x125-72-P 150Wp | Ningbo Solar : TDB125x125-72-P 150Wp | -0.35 | 43.2 | 5.1 | 150 | 34.2 | 4.39
1872 | Ningbo Solar | TDB125x125-72-P 155Wp | Ningbo Solar : TDB125x125-72-P 155Wp | -0.35 | 43.4 | 5.13 | 155 | 34.4 | 4.51
1873 | Ningbo Solar | TDB125x125-72-P 160Wp | Ningbo Solar : TDB125x125-72-P 160Wp | -0.35 | 43.6 | 5.19 | 160 | 34.6 | 4.63
1874 | Ningbo Solar | TDB125x125-72-P 165Wp | Ningbo Solar : TDB125x125-72-P 165Wp | -0.35 | 43.8 | 5.26 | 165 | 34.8 | 4.74
1875 | Ningbo Solar | TDB125x125-72-P 170Wp | Ningbo Solar : TDB125x125-72-P 170Wp | -0.35 | 44 | 5.36 | 170 | 35 | 4.86
1876 | Ningbo Solar | TDB125x125-72-P 175Wp | Ningbo Solar : TDB125x125-72-P 175Wp | -0.35 | 44 | 5.48 | 175 | 35.2 | 4.96
1877 | Ningbo Solar | TDB125x125-72-P 180Wp | Ningbo Solar : TDB125x125-72-P 180Wp | -0.35 | 44.2 | 5.53 | 180 | 35.4 | 5.08
1878 | Ningbo Solar | TPB125x125-72-P 140Wp | Ningbo Solar : TPB125x125-72-P 140Wp | -0.35 | 42.5 | 4.56 | 140 | 34 | 4.12
1879 | Ningbo Solar | TPB125x125-72-P 145Wp | Ningbo Solar : TPB125x125-72-P 145Wp | -0.35 | 42.6 | 4.66 | 145 | 34.2 | 4.24
1880 | Ningbo Solar | TPB125x125-72-P 150Wp | Ningbo Solar : TPB125x125-72-P 150Wp | -0.35 | 42.8 | 4.77 | 150 | 34.4 | 4.36
1881 | Ningbo Solar | TPB125x125-72-P 155Wp | Ningbo Solar : TPB125x125-72-P 155Wp | -0.35 | 43 | 4.87 | 155 | 34.6 | 4.48
1882 | Ningbo Solar | TPB125x125-72-P 160Wp | Ningbo Solar : TPB125x125-72-P 160Wp | -0.35 | 43.2 | 4.97 | 160 | 34.8 | 4.6
1883 | Ningbo Solar | TPB125x125-72-P 165Wp | Ningbo Solar : TPB125x125-72-P 165Wp | -0.35 | 43.4 | 5.07 | 165 | 35 | 4.72
1884 | Ningbo Solar | TPB125x125-72-P 170Wp | Ningbo Solar : TPB125x125-72-P 170Wp | -0.35 | 43.6 | 5.17 | 170 | 35.2 | 4.83
1885 | Ningbo Solar | TPB125x125-72-P 175Wp | Ningbo Solar : TPB125x125-72-P 175Wp | -0.35 | 43.8 | 5.26 | 175 | 35.4 | 4.95
1886 | Ningbo Solar | TPB125x125-72-P 180Wp | Ningbo Solar : TPB125x125-72-P 180Wp | -0.35 | 44 | 5.35 | 180 | 35.6 | 5.06
1887 | Nova Solar GmbH | 105Wp 72 Cells | Nova Solar GmbH : 105Wp 72 Cells | -0.35 | 43.3 | 3.26 | 105 | 34.6 | 3.03
1888 | OPEL | HCPV MKI | OPEL : HCPV MKI | -0.14915 | 17.7 | 5.7 | 80.7 | 15 | 5.3
1889 | OPEL | LCPV MKIII | OPEL : LCPV MKIII | -0.38 | 30 | 6.1 | 120 | 23.1 | 5.2
1890 | Open Renewables | 100-MM36 | Open Renewables : 100-MM36 | -0.24 | 22.5 | 5.6 | 100 | 18.7 | 5.2
1891 | Open Renewables | 230-ME60 | Open Renewables : 230-ME60 | -0.33 | 36.24 | 8.28 | 230 | 30.09 | 7.65
1892 | Open Renewables | 235-ME60 | Open Renewables : 235-ME60 | -0.33 | 36.43 | 8.36 | 235 | 30.36 | 7.74
1893 | Open Renewables | 240-ME60 | Open Renewables : 240-ME60 | -0.33 | 36.52 | 8.46 | 240 | 30.69 | 7.82
1894 | Open Renewables | 245-ME60 | Open Renewables : 245-ME60 | -0.33 | 36.59 | 8.59 | 245 | 31.01 | 7.9
1895 | Open Renewables | 250-ME60 | Open Renewables : 250-ME60 | -0.33 | 36.88 | 8.65 | 250 | 31.25 | 8
1896 | Open Renewables | 85-MM36 | Open Renewables : 85-MM36 | -0.24 | 22.2 | 5.5 | 85 | 17.7 | 5
1897 | Open Renewables | 90-MM36 | Open Renewables : 90-MM36 | -0.24 | 22.3 | 5.5 | 90 | 18 | 5.1
1898 | Open Renewables | 95-MM36 | Open Renewables : 95-MM36 | -0.24 | 22.4 | 5.5 | 95 | 18.3 | 5.2
1899 | PerfectSolar | PS 170M | PerfectSolar : PS 170M | -0.38 | 44.1 | 5.17 | 170 | 35.9 | 4.74
1900 | PerfectSolar | PS 170P | PerfectSolar : PS 170P | -0.29 | 29.04 | 7.76 | 170 | 23.39 | 7.25
1901 | PerfectSolar | PS 175M | PerfectSolar : PS 175M | -0.39 | 44.4 | 5.29 | 175 | 35.7 | 4.91
1902 | PerfectSolar | PS 180M | PerfectSolar : PS 180M | -0.42 | 44.7 | 5.35 | 180 | 35.9 | 5.03
1903 | PerfectSolar | PS 180P | PerfectSolar : PS 180P | -0.29 | 29.56 | 7.97 | 180 | 24.33 | 7.43
1904 | PerfectSolar | PS 220P | PerfectSolar : PS 220P | -0.36 | 36.9 | 7.85 | 220 | 30.2 | 7.32
1905 | PerfectSolar | PS 230M | PerfectSolar : PS 230M | -0.38 | 36.75 | 8.26 | 230 | 29.4 | 7.82
1906 | PFIXX Systems | PF40 | PFIXX Systems : PF40 | -0.33 | 63 | 1.03 | 40 | 47 | 8.6
1907 | PFIXX Systems | PF43 | PFIXX Systems : PF43 | -0.33 | 63 | 1.16 | 43 | 47 | 9.2
1908 | Pfleiderer | Terra-Piatta | Pfleiderer : Terra-Piatta | -0.35 | 21.2 | 3.1 | 50 | 17.3 | 2.9
1909 | Pfleiderer | Terra-Piatta Zelle ASE mono | Pfleiderer : Terra-Piatta Zelle ASE mono | -0.362 | 21.8 | 3.4 | 56 | 18.6 | 3.05
1910 | Pfleiderer | Terra-Piatta Zelle ASE poly | Pfleiderer : Terra-Piatta Zelle ASE poly | -0.333 | 14.4 | 4.85 | 51 | 12 | 4.25
1911 | Pfleiderer | Terra-Piatta Zelle Sunways | Pfleiderer : Terra-Piatta Zelle Sunways | -0.359 | 22 | 3.05 | 51 | 17.5 | 2.9
1912 | Philadelphia Solar | 215Wp | Philadelphia Solar : 215Wp | -0.23 | 33.3 | 8.35 | 215 | 27.7 | 7.8
1913 | Philadelphia Solar | 240Wp | Philadelphia Solar : 240Wp | -0.23 | 37.1 | 8.35 | 240 | 30.8 | 7.8
1914 | Philadelphia Solar | 250Wc | Philadelphia Solar : 250Wc | -0.23 | 37.44 | 8.63 | 250 | 30.6 | 8.17
1915 | Philadelphia Solar | PHS A72 - 165W | Philadelphia Solar : PHS A72 - 165W | -0.37 | 43.2 | 5.47 | 165 | 34.8 | 4.9
1916 | Philips | PSM125 | Philips : PSM125 | -0.2 | 32.3 | 5.46 | 125 | 26 | 4.6
1917 | Philips | PSM165 | Philips : PSM165 | -0.2 | 43.1 | 5.46 | 165 | 34.6 | 4.77
1918 | Phönix | MA 100 | Phönix : MA 100 | -0.33 | 141 | 1.17 | 100 | 108 | 0.93
1919 | Phönix | Newtec-Solardachziegel SDZ 36 | Phönix : Newtec-Solardachziegel SDZ 36 | -0.396 | 14.4 | 3.38 | 36 | 11.6 | 3.11
1920 | Photovoltech | HI LINE A0136 75Wp | Photovoltech : HI LINE A0136 75Wp | -0.329 | 21.3 | 4.85 | 75 | 17.3 | 4.34
1921 | Photovoltech | HI LINE A0136 80Wp | Photovoltech : HI LINE A0136 80Wp | -0.326 | 21.5 | 5.05 | 80 | 17.4 | 4.6
1922 | Photovoltech | HI LINE A0136 85Wp | Photovoltech : HI LINE A0136 85Wp | -0.323 | 21.7 | 5.28 | 85 | 17.6 | 4.86
1923 | Photovoltech | HI LINE A0136 90Wp | Photovoltech : HI LINE A0136 90Wp | -0.322 | 21.9 | 5.4 | 90 | 17.8 | 5.05
1924 | Photovoltech | HI LINE A0154 120Wp | Photovoltech : HI LINE A0154 120Wp | -0.34 | 32.3 | 5.05 | 120 | 26.1 | 4.6
1925 | Photovoltech | HI LINE A0154 127Wp | Photovoltech : HI LINE A0154 127Wp | -0.34 | 32.6 | 5.28 | 127 | 26.3 | 4.86
1926 | Photovoltech | HI LINE A0154 135Wp | Photovoltech : HI LINE A0154 135Wp | -0.334 | 32.9 | 5.4 | 135 | 26.7 | 5.05
1927 | Photovoltech | HI LINE A0172 160Wp | Photovoltech : HI LINE A0172 160Wp | -0.372 | 43 | 5.05 | 160 | 34.8 | 4.6
1928 | Photovoltech | HI LINE A0172 170Wp | Photovoltech : HI LINE A0172 170Wp | -0.369 | 43.4 | 5.28 | 170 | 35 | 4.86
1929 | Photovoltech | HI LINE A0172 180Wp | Photovoltech : HI LINE A0172 180Wp | -0.365 | 43.8 | 5.4 | 180 | 35.6 | 5.05
1930 | Photowatt | PW100 | Photowatt : PW100 | -0.361 | 21.5 | 0.72 | 12 | 17 | 0.65
1931 | Photowatt | PW1000/100Wp | Photowatt : PW1000/100Wp | -0.361 | 43.2 | 3 | 100 | 34.4 | 2.9
1932 | Photowatt | PW1000/105Wp | Photowatt : PW1000/105Wp | -0.361 | 43.2 | 3.15 | 105 | 34.6 | 3.05
1933 | Photowatt | PW1000/90Wp | Photowatt : PW1000/90Wp | -0.363 | 43 | 2.8 | 90 | 33.6 | 2.7
1934 | Photowatt | PW1000/95Wp | Photowatt : PW1000/95Wp | -0.361 | 43.2 | 2.9 | 95 | 34 | 2.8
1935 | Photowatt | PW1250/115Wp | Photowatt : PW1250/115Wp | -0.368 | 31.9 | 4.7 | 115 | 25.4 | 4.5
1936 | Photowatt | PW1250/125Wp | Photowatt : PW1250/125Wp | -0.367 | 32.3 | 5 | 125 | 25.9 | 4.8
1937 | Photowatt | PW1250/135Wp | Photowatt : PW1250/135Wp | -0.365 | 32.4 | 5.3 | 135 | 26.4 | 5.1
1938 | Photowatt | PW1400 130W | Photowatt : PW1400 130W | -0.37089 | 42.6 | 4.3 | 130 | 33.2 | 3.9
1939 | Photowatt | PW1400 140W | Photowatt : PW1400 140W | -0.36916 | 42.8 | 4.5 | 140 | 33.4 | 4.2
1940 | Photowatt | PW1400 150W | Photowatt : PW1400 150W | -0.36916 | 42.8 | 4.65 | 150 | 33.8 | 4.45
1941 | Photowatt | PW1400 160W | Photowatt : PW1400 160W | -0.36574 | 43.2 | 4.8 | 160 | 34.1 | 4.7
1942 | Photowatt | PW1500-12V 145Wp | Photowatt : PW1500-12V 145Wp | -0.37 | 21.4 | 9.1 | 145 | 16.8 | 8.6
1943 | Photowatt | PW1500-12V 155Wp | Photowatt : PW1500-12V 155Wp | -0.36 | 21.5 | 9.6 | 155 | 17 | 9.1
1944 | Photowatt | PW1500-12V 165Wp | Photowatt : PW1500-12V 165Wp | -0.36 | 21.6 | 10.2 | 165 | 17.2 | 9.6
1945 | Photowatt | PW1500-24V 145Wp | Photowatt : PW1500-24V 145Wp | -0.37 | 42.8 | 4.5 | 145 | 33.6 | 4.32
1946 | Photowatt | PW1500-24V 155Wp | Photowatt : PW1500-24V 155Wp | -0.36 | 43 | 4.8 | 155 | 34 | 4.56
1947 | Photowatt | PW1500-24V 165Wp | Photowatt : PW1500-24V 165Wp | -0.36 | 43.2 | 5.1 | 165 | 34.4 | 4.8
1948 | Photowatt | PW1650/155Wp | Photowatt : PW1650/155Wp | -0.368 | 43 | 4.8 | 155 | 33.8 | 4.6
1949 | Photowatt | PW1650/165Wp | Photowatt : PW1650/165Wp | -0.367 | 43.2 | 5.1 | 165 | 34.4 | 4.8
1950 | Photowatt | PW1650/175Wp | Photowatt : PW1650/175Wp | -0.365 | 43.2 | 5.3 | 175 | 35 | 5
1951 | Photowatt | PW200 | Photowatt : PW200 | -0.386 | 21.5 | 1.44 | 22 | 17 | 1.3
1952 | Photowatt | PW500/42Wp | Photowatt : PW500/42Wp | -0.366 | 21.3 | 2.7 | 42 | 16.8 | 2.5
1953 | Photowatt | PW500/47,5Wp | Photowatt : PW500/47,5Wp | -0.361 | 21.5 | 3.1 | 47.5 | 17 | 2.8
1954 | Photowatt | PW500/52Wp | Photowatt : PW500/52Wp | -0.356 | 21.6 | 3.3 | 52 | 17.3 | 3
1955 | Photowatt | PW6-110 | Photowatt : PW6-110 | -0.4 | 21.7 | 6.9 | 110 | 17.2 | 6.4
1956 | Photowatt | PW6-123 | Photowatt : PW6-123 | -0.4 | 21.9 | 7.6 | 123 | 17.6 | 7
1957 | Photowatt | PW6-230 | Photowatt : PW6-230 | -0.4 | 43.6 | 7.2 | 230 | 34.9 | 6.6
1958 | Photowatt | PW750/70Wp | Photowatt : PW750/70Wp | -0.366 | 21.3 | 4.5 | 70 | 16.7 | 4.2
1959 | Photowatt | PW750/75Wp | Photowatt : PW750/75Wp | -0.361 | 21.5 | 4.7 | 75 | 17 | 4.4
1960 | Photowatt | PW750/80Wp | Photowatt : PW750/80Wp | -0.356 | 21.6 | 5 | 80 | 17.3 | 4.6
1961 | Photowatt | PW850/75Wp | Photowatt : PW850/75Wp | -0.366 | 21.5 | 4.7 | 75 | 17 | 4.4
1962 | Photowatt | PW850/75Wp | Photowatt : PW850/75Wp | -0.366 | 21.5 | 4.7 | 75 | 17 | 4.4
1963 | Photowatt | PW850/80Wp | Photowatt : PW850/80Wp | -0.361 | 21.6 | 5 | 80 | 17.3 | 4.6
1964 | Photowatt | PW850/80Wp | Photowatt : PW850/80Wp | -0.361 | 21.6 | 5 | 80 | 17.3 | 4.6
1965 | Photowatt | PW850/85Wp | Photowatt : PW850/85Wp | -0.356 | 21.6 | 5.2 | 85 | 17.6 | 4.8
1966 | Photowatt | PW850/85Wp | Photowatt : PW850/85Wp | -0.356 | 21.6 | 5.2 | 85 | 17.6 | 4.8
1967 | Photowatt | PWM1650-12/24V 165Wp | Photowatt : PWM1650-12/24V 165Wp | -0.356 | 44.4 | 5.1 | 165 | 35.2 | 4.7
1968 | Photowatt | PWM1650-12/24V 175Wp | Photowatt : PWM1650-12/24V 175Wp | -0.354 | 44.6 | 5.3 | 175 | 35.4 | 4.95
1969 | Photowatt | PWM1700-12/24V 170Wp | Photowatt : PWM1700-12/24V 170Wp | -0.356 | 44.4 | 5.3 | 170 | 35.2 | 4.85
1970 | Photowatt | PWM1700-12/24V 180Wp | Photowatt : PWM1700-12/24V 180Wp | -0.354 | 44.6 | 5.5 | 180 | 35.4 | 5.1
1971 | Photowatt | PWM1700-12/24V 190Wp | Photowatt : PWM1700-12/24V 190Wp | -0.353 | 44.8 | 5.8 | 190 | 35.6 | 5.35
1972 | Photowatt | PWX100 | Photowatt : PWX100 | -0.361 | 21.5 | 0.72 | 12 | 17 | 0.65
1973 | Photowatt | PWX200 | Photowatt : PWX200 | -0.386 | 21.5 | 1.44 | 22 | 17 | 1.3
1974 | Photowatt | PWX500/42Wp | Photowatt : PWX500/42Wp | -0.366 | 21.3 | 2.7 | 42 | 16.8 | 2.5
1975 | Photowatt | PWX500/47,5Wp | Photowatt : PWX500/47,5Wp | -0.361 | 21.5 | 3.1 | 47.5 | 17 | 2.8
1976 | Photowatt | PWX500/52Wp | Photowatt : PWX500/52Wp | -0.356 | 21.6 | 3.3 | 52 | 17.3 | 3
1977 | Photowatt | PWX750/70Wp | Photowatt : PWX750/70Wp | -0.366 | 21.3 | 4.5 | 70 | 16.7 | 4.2
1978 | Photowatt | PWX750/75Wp | Photowatt : PWX750/75Wp | -0.361 | 21.5 | 4.7 | 75 | 17 | 4.4
1979 | Photowatt | PWX750/80Wp | Photowatt : PWX750/80Wp | -0.356 | 21.6 | 5 | 80 | 17.3 | 4.6
1980 | Plaston | SDZ 36-10 | Plaston : SDZ 36-10 | -0.234 | 14.5 | 3.45 | 36 | 11.6 | 3.15
1981 | Power Glaz | SMT 6(48)P (165W) | Power Glaz : SMT 6(48)P (165W) | -0.37 | 28.8 | 8.1 | 165 | 22.1 | 7.5
1982 | Power Glaz | SMT 6(48)P (170W) | Power Glaz : SMT 6(48)P (170W) | -0.36 | 29.5 | 8.1 | 170 | 22.5 | 7.6
1983 | Power Glaz | SMT 6(48)P (175W) | Power Glaz : SMT 6(48)P (175W) | -0.36 | 29.7 | 8.2 | 175 | 23 | 7.6
1984 | Power Glaz | SMT 6(48)P (180W) | Power Glaz : SMT 6(48)P (180W) | -0.35 | 29.8 | 8.3 | 180 | 23.1 | 7.8
1985 | Power Glaz | SMT 6(48)P (185W) | Power Glaz : SMT 6(48)P (185W) | -0.35 | 30.4 | 8.3 | 185 | 23.6 | 7.8
1986 | Power Glaz | SMT 6(48)P (190W) | Power Glaz : SMT 6(48)P (190W) | -0.35 | 30.6 | 8.4 | 190 | 24.1 | 7.9
1987 | Power Glaz | SMT 6(54)P (185W) | Power Glaz : SMT 6(54)P (185W) | -0.37 | 32.3 | 8.1 | 185 | 24.8 | 7.5
1988 | Power Glaz | SMT 6(54)P (190W) | Power Glaz : SMT 6(54)P (190W) | -0.37 | 33.1 | 8.1 | 190 | 25.3 | 7.5
1989 | Power Glaz | SMT 6(54)P (195W) | Power Glaz : SMT 6(54)P (195W) | -0.36 | 33.4 | 8.2 | 195 | 25.8 | 7.6
1990 | Power Glaz | SMT 6(54)P (200W) | Power Glaz : SMT 6(54)P (200W) | -0.35 | 33.6 | 8.3 | 200 | 26 | 7.7
1991 | Power Glaz | SMT 6(54)P (205W) | Power Glaz : SMT 6(54)P (205W) | -0.35 | 34.2 | 8.3 | 205 | 26.3 | 7.8
1992 | Power Glaz | SMT 6(54)P (210W) | Power Glaz : SMT 6(54)P (210W) | -0.35 | 34.5 | 8.4 | 210 | 26.8 | 7.9
1993 | Power Glaz | SMT 6(60)P (210W) | Power Glaz : SMT 6(60)P (210W) | -0.35 | 36.4 | 8.1 | 210 | 28.2 | 7.5
1994 | Power Glaz | SMT 6(60)P (215W) | Power Glaz : SMT 6(60)P (215W) | -0.35 | 36.5 | 8.2 | 215 | 28.3 | 7.6
1995 | Power Glaz | SMT 6(60)P (220W) | Power Glaz : SMT 6(60)P (220W) | -0.35 | 36.9 | 8.2 | 220 | 28.7 | 7.7
1996 | Power Glaz | SMT 6(60)P (225W) | Power Glaz : SMT 6(60)P (225W) | -0.35 | 37.3 | 8.4 | 225 | 28.9 | 7.8
1997 | Power Glaz | SMT 6(60)P (230W) | Power Glaz : SMT 6(60)P (230W) | -0.35 | 37.5 | 8.4 | 230 | 29.2 | 7.9
1998 | Power Glaz | SMT 6(60)P (235W) | Power Glaz : SMT 6(60)P (235W) | -0.35 | 37.8 | 8.4 | 235 | 29.7 | 7.9
1999 | PoweRRoof Evalon V-Solar | Solar 136 | PoweRRoof Evalon V-Solar : Solar 136 | -0.21 | 46.2 | 5.1 | 136 | 33 | 4.13
2000 | PoweRRoof Evalon V-Solar | Solar 204 | PoweRRoof Evalon V-Solar : Solar 204 | -0.21 | 69.3 | 5.1 | 204 | 49.5 | 4.13
2001 | PoweRRoof Evalon V-Solar | Solar 272 | PoweRRoof Evalon V-Solar : Solar 272 | -0.21 | 92.4 | 5.1 | 272 | 66 | 4.13
2002 | PoweRRoof Evalon V-Solar | Solar 408 | PoweRRoof Evalon V-Solar : Solar 408 | -0.21 | 138.6 | 5.1 | 408 | 99 | 4.13
2003 | PowerTile | Solar Tile Model P4 | PowerTile : Solar Tile Model P4 | -0.346 | 4.9 | 8.8 | 30.5 | 4 | 7.63
2004 | PRAMAC LUCE | APH 80Wp | PRAMAC LUCE : APH 80Wp | -0.28 | 134 | 1 | 80 | 100 | 0.8
2005 | PRAMAC LUCE | APH 90Wp | PRAMAC LUCE : APH 90Wp | -0.28 | 140 | 1.08 | 90 | 106 | 0.86
2006 | PRAMAC LUCE | AS 40Wp | PRAMAC LUCE : AS 40Wp | -0.3 | 62.2 | 1.14 | 40 | 44.8 | 0.93
2007 | PRAMAC LUCE | MC 200Wp | PRAMAC LUCE : MC 200Wp | -0.34 | 35.8 | 7.85 | 200 | 28.7 | 6.97
2008 | PRAMAC LUCE | MC 210Wp | PRAMAC LUCE : MC 210Wp | -0.34 | 36.2 | 8 | 210 | 28.9 | 7.27
2009 | PRAMAC LUCE | MC 220Wp | PRAMAC LUCE : MC 220Wp | -0.34 | 36.8 | 8.1 | 220 | 29.1 | 7.56
2010 | PRAMAC LUCE | MC 225Wp | PRAMAC LUCE : MC 225Wp | -0.34 | 37 | 8.2 | 225 | 29.2 | 7.71
2011 | PRAMAC LUCE | MC 230Wp | PRAMAC LUCE : MC 230Wp | -0.34 | 34.2 | 8.3 | 230 | 29.4 | 7.82
2012 | PRAMAC LUCE | MCPH 105W | PRAMAC LUCE : MCPH 105W | -0.39 | 123 | 1.5 | 105 | 105 | 1
2013 | PRAMAC LUCE | MCPH 105Wp | PRAMAC LUCE : MCPH 105Wp | -0.39 | 123 | 1.5 | 105 | 105 | 1
2014 | PRAMAC LUCE | MCPH 115 W | PRAMAC LUCE : MCPH 115 W | -0.39 | 128 | 1.5 | 115 | 105 | 1.1
2015 | PRAMAC LUCE | MCPH 115Wp | PRAMAC LUCE : MCPH 115Wp | -0.39 | 128 | 1.5 | 115 | 105 | 1.1
2016 | PRAMAC LUCE | MCPH 125 W | PRAMAC LUCE : MCPH 125 W | -0.39 | 134 | 1.5 | 125 | 105 | 1.2
2017 | PRAMAC LUCE | MCPH 125Wp | PRAMAC LUCE : MCPH 125Wp | -0.39 | 134 | 1.5 | 125 | 105 | 1.2
2018 | PRAMAC LUCE | SC 170Wp | PRAMAC LUCE : SC 170Wp | -0.38 | 43.35 | 4.99 | 170 | 36.18 | 4.7
2019 | PRAMAC LUCE | SC 175Wp | PRAMAC LUCE : SC 175Wp | -0.38 | 43.39 | 5.12 | 175 | 36.21 | 4.83
2020 | PROSOLAR | PM 116 12V | PROSOLAR : PM 116 12V | -0.38 | 22 | 7.4 | 116 | 18.1 | 6.4
2021 | PROSOLAR | PM 116 24V | PROSOLAR : PM 116 24V | -0.38 | 44 | 3.7 | 116 | 35.8 | 3.22
2022 | PROSOLAR | PM 160 | PROSOLAR : PM 160 | -0.38 | 21.7 | 10.1 | 160 | 17.6 | 9.09
2023 | PROSOLAR | PM 180 | PROSOLAR : PM 180 | -0.38 | 61 | 3.81 | 180 | 54 | 3.33
2024 | PROSOLAR | PM 36-58 | PROSOLAR : PM 36-58 | -0.38 | 22 | 3.7 | 58 | 18 | 3.28
2025 | PSFU/AES | P 150 | PSFU/AES : P 150 | -0.4 | 44 | 4.8 | 150 | 34.2 | 4.4
2026 | PSFU/AES | P 160 | PSFU/AES : P 160 | -0.4 | 43.4 | 4.87 | 160 | 36 | 4.5
2027 | PSFU/AES | P 80 | PSFU/AES : P 80 | -0.4 | 21.7 | 4.87 | 80 | 18 | 4.5
2028 | Pure-Stroom | PS-240 | Pure-Stroom : PS-240 | -0.367 | 43.2 | 7.6 | 240 | 34.95 | 6.88
2029 | Pure-Stroom | PS-250 | Pure-Stroom : PS-250 | -0.367 | 43.2 | 7.7 | 250 | 35.2 | 7.12
2030 | Pure-Stroom | PS-260 | Pure-Stroom : PS-260 | -0.367 | 43.49 | 7.79 | 260 | 36 | 7.23
2031 | Pure-Stroom | PS-270 | Pure-Stroom : PS-270 | -0.367 | 43.63 | 8.1 | 270 | 36.4 | 7.42
2032 | Pure-Stroom | PS-280 | Pure-Stroom : PS-280 | -0.367 | 43.78 | 8.3 | 280 | 36.72 | 7.63
2033 | PVT-Austria | PVT-200AE-C Poly 200Wp | PVT-Austria : PVT-200AE-C Poly 200Wp | -0.32 | 36.65 | 7.47 | 200 | 29.8 | 6.8
2034 | PVT-Austria | PVT-200MAE-A Mono 200Wp | PVT-Austria : PVT-200MAE-A Mono 200Wp | -0.33 | 52.8 | 5.3 | 200 | 43.6 | 4.6
2035 | PVT-Austria | PVT-205AE-C Poly 205Wp | PVT-Austria : PVT-205AE-C Poly 205Wp | -0.32 | 36.8 | 7.53 | 205 | 30 | 6.9
2036 | PVT-Austria | PVT-205AE-C Poly 205Wp | PVT-Austria : PVT-205AE-C Poly 205Wp | -0.32 | 36.8 | 7.53 | 205 | 30 | 6.9
2037 | PVT-Austria | PVT-205AE-C Poly 205Wp | PVT-Austria : PVT-205AE-C Poly 205Wp | -0.32 | 36.8 | 7.53 | 205 | 30 | 6.9
2038 | PVT-Austria | PVT-210AE-B Mono | PVT-Austria : PVT-210AE-B Mono | -0.33 | 36.3 | 7.88 | 210 | 29.37 | 7.15
2039 | PVT-Austria | PVT-210AE-C Poly 210Wp | PVT-Austria : PVT-210AE-C Poly 210Wp | -0.32 | 36.9 | 7.58 | 210 | 30.2 | 6.97
2040 | PVT-Austria | PVT-210MAE-C Mono 210Wp | PVT-Austria : PVT-210MAE-C Mono 210Wp | -0.38 | 36 | 8.26 | 210 | 28.8 | 7.3
2041 | PVT-Austria | PVT-215AE-C Poly 215Wp | PVT-Austria : PVT-215AE-C Poly 215Wp | -0.32 | 37.1 | 7.7 | 215 | 30.4 | 7.1
2042 | PVT-Austria | PVT-215AE-C Poly 215Wp | PVT-Austria : PVT-215AE-C Poly 215Wp | -0.32 | 37.1 | 7.7 | 215 | 30.4 | 7.1
2043 | PVT-Austria | PVT-215MAE-C Mono 215Wp | PVT-Austria : PVT-215MAE-C Mono 215Wp | -0.38 | 36.06 | 8.3 | 215 | 29.3 | 7.35
2044 | PVT-Austria | PVT-220AE-C Poly 220Wp | PVT-Austria : PVT-220AE-C Poly 220Wp | -0.32 | 37.3 | 7.8 | 220 | 30.7 | 7.2
2045 | PVT-Austria | PVT-220MAE-C Mono 220Wp | PVT-Austria : PVT-220MAE-C Mono 220Wp | -0.38 | 36.18 | 8.36 | 220 | 29.67 | 7.46
2046 | PVT-Austria | PVT-225MAE-C Mono 225Wp | PVT-Austria : PVT-225MAE-C Mono 225Wp | -0.38 | 36.3 | 8.44 | 225 | 29.88 | 7.55
2047 | PVT-Austria | PVT-230MAE-C Mono 230Wp | PVT-Austria : PVT-230MAE-C Mono 230Wp | -0.38 | 36.42 | 8.49 | 230 | 30.12 | 7.67
2048 | PVT-Austria | PVT-230MAE-C Mono 230Wp | PVT-Austria : PVT-230MAE-C Mono 230Wp | -0.38 | 36.42 | 8.49 | 230 | 30.12 | 7.67
2049 | PVT-Austria | PVT-235MAE-C Mono 235Wp | PVT-Austria : PVT-235MAE-C Mono 235Wp | -0.38 | 36.54 | 8.5 | 235 | 30.6 | 7.73
2050 | Q.Cells | Q.PRO-210 | Q.Cells : Q.PRO-210 | -0.3 | 35.83 | 8.09 | 210 | 28.35 | 5.57
2051 | Q.Cells | Q.PRO-215 | Q.Cells : Q.PRO-215 | -0.3 | 36 | 8.12 | 215 | 28.82 | 7.6
2052 | Q.Cells | Q.PRO-220 | Q.Cells : Q.PRO-220 | -0.3 | 36.15 | 8.2 | 220 | 29.04 | 7.69
2053 | Q.Cells | Q.PRO-225 | Q.Cells : Q.PRO-225 | -0.3 | 36.36 | 8.25 | 225 | 29.29 | 7.77
2054 | Q.Cells | Q.PRO-230 | Q.Cells : Q.PRO-230 | -0.3 | 36.61 | 8.3 | 230 | 29.56 | 7.84
2055 | Q.Cells | Q.PRO-235 | Q.Cells : Q.PRO-235 | -0.3 | 36.92 | 8.38 | 235 | 29.89 | 7.89
2056 | Q.Cells | Q.PRO-240 | Q.Cells : Q.PRO-240 | -0.3 | 37.2 | 8.45 | 240 | 30.2 | 7.96
2057 | Q.Cells | Q.PRO-245 | Q.Cells : Q.PRO-245 | -0.3 | 37.48 | 8.52 | 245 | 30.55 | 8.03
2058 | Q.Cells | SL2-100 | Q.Cells : SL2-100 | -0.36 | 89.2 | 1.57 | 100 | 70.3 | 1.42
2059 | Q.Cells | SL2-105 | Q.Cells : SL2-105 | -0.36 | 91.0 | 1.6 | 105 | 72.6 | 1.45
2060 | Q.Cells | SL2-110 | Q.Cells : SL2-110 | -0.36 | 92.8 | 1.61 | 110 | 74.9 | 1.47
2061 | Q.Cells | SL2-115 | Q.Cells : SL2-115 | -0.36 | 94.7 | 1.61 | 115 | 77 | 1.49
2062 | Q.Cells | SL2-95 | Q.Cells : SL2-95 | -0.36 | 87.5 | 1.56 | 95 | 68 | 1.4
2063 | RAH | Solar Mono WXS-180s | RAH : Solar Mono WXS-180s | -0.33 | 44.28 | 5.6 | 185 | 35.65 | 5.05
2064 | RAH | Solar Mono WXS-185s | RAH : Solar Mono WXS-185s | -0.33 | 44.28 | 5.6 | 190 | 35.9 | 5.15
2065 | RAH | Solar Mono WXS-190S | RAH : Solar Mono WXS-190S | -0.33 | 44.28 | 5.85 | 195 | 36.72 | 5.17
2066 | Raimann | RV Energy 150M | Raimann : RV Energy 150M | -0.35 | 43.29 | 5 | 150 | 34.39 | 4.39
2067 | Raimann | RV Energy 160M | Raimann : RV Energy 160M | -0.35 | 44.49 | 5.34 | 160 | 33.43 | 4.8
2068 | Raimann | RV SC-150M | Raimann : RV SC-150M | -0.38 | 43.6 | 5.2 | 150 | 34.4 | 4.8
2069 | Raimann | RV SC-160M | Raimann : RV SC-160M | -0.32 | 43.6 | 5.2 | 160 | 34.4 | 4.66
2070 | Rajasthan | Module 37 W | Rajasthan : Module 37 W | -0.119 | 21 | 2.6 | 37 | 16.5 | 2.25
2071 | Rajasthan | Module 74 W | Rajasthan : Module 74 W | -0.119 | 21 | 5.1 | 74 | 16.5 | 4.6
2072 | Ralos | Ra 110 | Ralos : Ra 110 | -0.429 | 21 | 7.37 | 110 | 16.7 | 6.59
2073 | Ralos | Ra 115 | Ralos : Ra 115 | -0.429 | 21 | 7.65 | 115 | 16.7 | 6.89
2074 | Ralos | Ra 120 P (110 W) | Ralos : Ra 120 P (110 W) | -0.338 | 23.7 | 6.51 | 110 | 18.8 | 5.87
2075 | Ralos | Ra 120 P (120 W) | Ralos : Ra 120 P (120 W) | -0.335 | 23.9 | 6.89 | 120 | 19 | 6.3
2076 | Ralos | Ra 155 M | Ralos : Ra 155 M | -0.363 | 21.5 | 10 | 155 | 17.3 | 8.96
2077 | Ralos | Ra 155 P | Ralos : Ra 155 P | -0.364 | 21.4 | 9.4 | 145 | 17.2 | 8.43
2078 | Ralos | Ra 165 M | Ralos : Ra 165 M | -0.419 | 21.5 | 10.4 | 165 | 17.3 | 9.54
2079 | Ralos | Ra 80 M | Ralos : Ra 80 M | -0.363 | 21.5 | 5.17 | 80 | 17.3 | 4.63
2080 | Ralos | Ra 80 P | Ralos : Ra 80 P | -0.366 | 21.3 | 4.87 | 75 | 17.2 | 4.36
2081 | Ralos | W 900 | Ralos : W 900 | -0.372 | 24.2 | 5.68 | 85 | 16.7 | 5.68
2082 | RAP | RAP 100 | RAP : RAP 100 | -0.4 | 43.2 | 3 | 100 | 34.6 | 2.9
2083 | RAP | RAP 100 Laminat | RAP : RAP 100 Laminat | -0.4 | 43.2 | 3 | 100 | 34.6 | 2.9
2084 | RAP | RAP 110 | RAP : RAP 110 | -0.4 | 43.6 | 3.3 | 110 | 36.3 | 3.1
2085 | RAP | RAP 110 Laminat | RAP : RAP 110 Laminat | -0.4 | 43.6 | 3.3 | 110 | 36.3 | 3.1
2086 | RAP | RAP 50 | RAP : RAP 50 | -0.4 | 21.6 | 3 | 50 | 17.3 | 2.9
2087 | RAP | RAP 50 Laminat | RAP : RAP 50 Laminat | -0.4 | 21.6 | 3 | 50 | 17.3 | 2.9
2088 | RAP | RAP 55 | RAP : RAP 55 | -0.4 | 21.8 | 3.1 | 56 | 18.1 | 3.1
2089 | RAP | RAP 55 Laminat | RAP : RAP 55 Laminat | -0.4 | 21.8 | 3.1 | 56 | 18.1 | 3.1
2090 | Rathscheck | Solar Sklent | Rathscheck : Solar Sklent | -0.381 | 24.9 | 2.84 | 55 | 20.8 | 2.65
2091 | REC Solar | 215PE | REC Solar : 215PE | -0.32 | 36.3 | 8.1 | 215 | 28.3 | 7.6
2092 | REC Solar | 220PE | REC Solar : 220PE | -0.32 | 36.6 | 8.2 | 220 | 28.7 | 7.7
2093 | REC Solar | 225PE | REC Solar : 225PE | -0.32 | 36.8 | 8.2 | 225 | 29.1 | 7.7
2094 | REC Solar | 230PE | REC Solar : 230PE | -0.32 | 37.1 | 8.3 | 230 | 29.4 | 7.8
2095 | REC Solar | 235PE | REC Solar : 235PE | -0.32 | 37.4 | 8.3 | 235 | 29.8 | 7.9
2096 | REC Solar | 240PE | REC Solar : 240PE | -0.32 | 37.7 | 8.4 | 240 | 30.4 | 7.9
2097 | Rec Solar | Premium 210Wp | Rec Solar : Premium 210Wp | -0.335 | 36.1 | 8.1 | 210 | 28 | 7.5
2098 | Rec Solar | Premium 215Wp | Rec Solar : Premium 215Wp | -0.33 | 36.3 | 8.1 | 215 | 28.3 | 7.6
2099 | Rec Solar | Premium 220Wp | Rec Solar : Premium 220Wp | -0.331 | 36.6 | 8.2 | 220 | 28.7 | 7.7
2100 | Rec Solar | Premium 225Wp | Rec Solar : Premium 225Wp | -0.329 | 36.8 | 8.2 | 225 | 29.1 | 7.7
2101 | Rec Solar | Premium 230Wp | Rec Solar : Premium 230Wp | -0.326 | 37.1 | 8.3 | 230 | 29.4 | 7.8
2102 | Rec Solar | Premium 235Wp | Rec Solar : Premium 235Wp | -0.324 | 37.4 | 8.3 | 235 | 29.8 | 7.9
2103 | Rec Solar | REC-205AE | Rec Solar : REC-205AE | -0.34 | 36 | 8.3 | 205 | 27.2 | 7.6
2104 | Rec Solar | REC-210AE | Rec Solar : REC-210AE | -0.34 | 36.1 | 8.3 | 210 | 27.6 | 7.6
2105 | Rec Solar | REC-215AE | Rec Solar : REC-215AE | -0.34 | 36.3 | 8.3 | 215 | 28 | 7.7
2106 | Rec Solar | REC-220AE | Rec Solar : REC-220AE | -0.34 | 36.4 | 8.4 | 220 | 28.4 | 7.8
2107 | Rec Solar | REC-225AE | Rec Solar : REC-225AE | -0.34 | 36.6 | 8.4 | 225 | 28.8 | 7.8
2108 | Rec Solar | REC-230AE | Rec Solar : REC-230AE | -0.34 | 36.8 | 8.4 | 230 | 29.1 | 7.9
2109 | REC Solar | SCM 210 205Wp | REC Solar : SCM 210 205Wp | -0.288 | 36.09 | 7.93 | 205 | 28.08 | 7.33
2110 | REC Solar | SCM 210 210Wp | REC Solar : SCM 210 210Wp | -0.287 | 36.26 | 8.11 | 210 | 28.17 | 7.46
2111 | REC Solar | SCM 210 215Wp | REC Solar : SCM 210 215Wp | -0.286 | 36.37 | 8.21 | 215 | 28.27 | 7.59
2112 | REC Solar | SCM 210 220Wp | REC Solar : SCM 210 220Wp | -0.285 | 36.51 | 8.32 | 220 | 28.33 | 7.71
2113 | REC solar | SCM 210 225Wp | REC solar : SCM 210 225Wp | -0.283 | 36.7 | 8.5 | 225 | 28.4 | 7.9
2114 | REC solar | SCM 210 230Wp | REC solar : SCM 210 230Wp | -0.283 | 36.7 | 8.6 | 230 | 28.5 | 8
2115 | REM | Q215 | REM : Q215 | -0.3646 | 36.2 | 8.11 | 215 | 28.8 | 7.47
2116 | REM | Q220 | REM : Q220 | -0.3626 | 36.4 | 8.22 | 220 | 29 | 7.59
2117 | REM | Q225 | REM : Q225 | -0.3607 | 36.6 | 8.33 | 225 | 29.2 | 7.71
2118 | REM | Q230 | REM : Q230 | -0.3587 | 36.8 | 8.44 | 230 | 29.4 | 7.82
2119 | REM | Q235 | REM : Q235 | -0.3568 | 37 | 8.55 | 235 | 29.6 | 7.94
2120 | REM | Q240 | REM : Q240 | -0.3548 | 37.2 | 8.66 | 240 | 29.8 | 8.01
2121 | Rezosolar | RS 210 | Rezosolar : RS 210 | -0.37 | 33.6 | 8.32 | 210 | 27 | 7.81
2122 | RISEN | SYP175S-50M | RISEN : SYP175S-50M | -0.37 | 44.2 | 5.2 | 175 | 35.2 | 4.95
2123 | RISEN | SYP180S-50M | RISEN : SYP180S-50M | -0.37 | 44.8 | 5.3 | 180 | 36 | 5
2124 | Risen Corporation | SYP160S-50M | Risen Corporation : SYP160S-50M | -0.37 | 43.5 | 5 | 160 | 35.6 | 4.5
2125 | Risen Corporation | SYP165S-50M | Risen Corporation : SYP165S-50M | -0.37 | 44 | 5.1 | 165 | 35.8 | 4.61
2126 | Risen Corporation | SYP170S-50M | Risen Corporation : SYP170S-50M | -0.37 | 44.5 | 5.12 | 170 | 35.9 | 4.74
2127 | Risen Corporation | SYP175S-50M | Risen Corporation : SYP175S-50M | -0.37 | 44.8 | 5.17 | 175 | 36 | 4.86
2128 | Risen Corporation | SYP180S-50M | Risen Corporation : SYP180S-50M | -0.37 | 45 | 5.32 | 180 | 36.7 | 4.91
2129 | Risen Corporation | SYP200S | Risen Corporation : SYP200S | -0.39 | 36.5 | 7.65 | 200 | 28.6 | 6.98
2130 | Risen Corporation | SYP210S | Risen Corporation : SYP210S | -0.39 | 36.5 | 7.88 | 210 | 29 | 7.24
2131 | Risen Corporation | SYP220S | Risen Corporation : SYP220S | -0.39 | 37 | 8.1 | 220 | 29.5 | 7.45
2132 | Risen Corporation | SYP230S | Risen Corporation : SYP230S | -0.39 | 37 | 8.22 | 230 | 29.8 | 7.73
2133 | Risen Corporation | SYP240S | Risen Corporation : SYP240S | -0.39 | 37.2 | 8.33 | 240 | 30.2 | 7.95
2134 | Risen Corporation | SYP250S | Risen Corporation : SYP250S | -0.39 | 44.8 | 7.87 | 250 | 34.6 | 7.23
2135 | Risen Corporation | SYP260S | Risen Corporation : SYP260S | -0.39 | 44 | 8.09 | 260 | 34.8 | 7.47
2136 | Risen Corporation | SYP270S | Risen Corporation : SYP270S | -0.39 | 44.5 | 8.2 | 270 | 35 | 7.71
2137 | Risen Corporation | SYP280S | Risen Corporation : SYP280S | -0.39 | 44.8 | 8.33 | 280 | 35.2 | 7.95
2138 | Risen Corporation | SYP40S-M | Risen Corporation : SYP40S-M | -0.37 | 21.8 | 2.48 | 40 | 17.6 | 2.27
2139 | Risen Corporation | SYP60S-M | Risen Corporation : SYP60S-M | -0.37 | 21 | 3.86 | 60 | 16.8 | 3.57
2140 | Risen Corporation | SYP75S-M | Risen Corporation : SYP75S-M | -0.37 | 21.9 | 4.87 | 75 | 17.2 | 4.36
2141 | Risen Corporation | SYP80S-M | Risen Corporation : SYP80S-M | -0.37 | 21.6 | 5 | 80 | 17.2 | 4.65
2142 | Risen Corporation | SYP85S-M | Risen Corporation : SYP85S-M | -0.37 | 21.9 | 5.14 | 85 | 17.6 | 4.83
2143 | Risen Corporation | SYP90S-M | Risen Corporation : SYP90S-M | -0.37 | 22.4 | 5.3 | 90 | 18 | 5
2144 | Risun | RSM200P | Risun : RSM200P | -0.38 | 35.8 | 7.76 | 200 | 29.4 | 6.8
2145 | Risun | RSM210P | Risun : RSM210P | -0.38 | 36.2 | 7.82 | 210 | 29.7 | 7.08
2146 | Risun | RSM220P | Risun : RSM220P | -0.38 | 36.5 | 8.12 | 220 | 29.8 | 7.4
2147 | Risun | RSM230P | Risun : RSM230P | -0.38 | 36.8 | 8.34 | 230 | 30 | 7.67
2148 | Risun | RSM240P | Risun : RSM240P | -0.38 | 37 | 8.54 | 240 | 30.2 | 7.95
2149 | Roto Frank AG | RPV 18/14 | Roto Frank AG : RPV 18/14 | -0.4 | 61.4 | 6 | 272 | 50.5 | 5.35
2150 | Roto Frank AG | RPV 9/14 | Roto Frank AG : RPV 9/14 | -0.4 | 25 | 6 | 111 | 21 | 5.35
2151 | RV Energytechnik | PM 110 | RV Energytechnik : PM 110 | -0.35 | 43.26 | 3.4 | 110 | 34.6 | 3.18
2152 | RV Energytechnik | RV Energy 150 M | RV Energytechnik : RV Energy 150 M | -0.32 | 43.29 | 5 | 150 | 34.39 | 4.39
2153 | RV Energytechnik | RV Energy 160 M | RV Energytechnik : RV Energy 160 M | -0.32 | 44.49 | 5.34 | 160 | 33.43 | 4.8
2154 | RV Energytechnik | RV Energy 180 M 12V | RV Energytechnik : RV Energy 180 M 12V | -0.32 | 22.6 | 11.5 | 180 | 17.3 | 10.4
2155 | RV Energytechnik | RV Energy 180 M 24V | RV Energytechnik : RV Energy 180 M 24V | -0.32 | 45.2 | 5.75 | 180 | 34.6 | 5.2
2156 | RV Energytechnik | RV Energy PM 70 | RV Energytechnik : RV Energy PM 70 | -0.25 | 21 | 5 | 70 | 16.5 | 4.25
2157 | RV Energytechnik | RV Energy PM 75 | RV Energytechnik : RV Energy PM 75 | -0.42 | 21.4 | 5 | 75 | 17 | 4.4
2158 | RV Energytechnik | RV Energy PM 80 | RV Energytechnik : RV Energy PM 80 | -0.25 | 21.5 | 5.1 | 80 | 17.3 | 4.63
2159 | RWE Solar | ASE-100 | RWE Solar : ASE-100 | -0.38 | 42.5 | 3.2 | 100 | 34.5 | 2.9
2160 | RWE Solar | ASE-100-GT-FT, 100 W | RWE Solar : ASE-100-GT-FT, 100 W | -0.376 | 42.5 | 3.2 | 100 | 34.5 | 2.9
2161 | RWE Solar | ASE-100-GT-FT, 105 W | RWE Solar : ASE-100-GT-FT, 105 W | -0.376 | 42.6 | 3.3 | 105 | 35 | 3
2162 | RWE Solar | ASE-100-GT-FT, 95 W | RWE Solar : ASE-100-GT-FT, 95 W | -0.378 | 42.3 | 3.2 | 95 | 34.1 | 2.8
2163 | RWE Solar | ASE-100-GT-FT/K, 100 W | RWE Solar : ASE-100-GT-FT/K, 100 W | -0.376 | 42.5 | 3.2 | 105 | 34.5 | 2.9
2164 | RWE Solar | ASE-100-GT-FT/K, 102 W | RWE Solar : ASE-100-GT-FT/K, 102 W | -0.38 | 29.2 | 4.88 | 102 | 23.2 | 4.4
2165 | RWE Solar | ASE-100-GT-FT/K, 105 W | RWE Solar : ASE-100-GT-FT/K, 105 W | -0.376 | 42.6 | 3.3 | 105 | 35 | 3
2166 | RWE Solar | ASE-100-GT-FT/K, 95 W | RWE Solar : ASE-100-GT-FT/K, 95 W | -0.378 | 42.3 | 3.2 | 95 | 34.1 | 2.8
2167 | RWE Solar | ASE-100-GT-FT/MC, 105 W | RWE Solar : ASE-100-GT-FT/MC, 105 W | -0.38 | 29.5 | 4.92 | 105 | 23.5 | 4.47
2168 | RWE Solar | ASE-100-GT-FT/MC, 99 W | RWE Solar : ASE-100-GT-FT/MC, 99 W | -0.38 | 28.7 | 4.84 | 99 | 22.8 | 4.34
2169 | RWE Solar | ASE-145-GT-FT 145Wp | RWE Solar : ASE-145-GT-FT 145Wp | -0.38 | 42.2 | 4.69 | 145 | 34.1 | 4.24
2170 | RWE Solar | ASE-160-GT-FT (150W) | RWE Solar : ASE-160-GT-FT (150W) | -0.38 | 69.4 | 3.03 | 150 | 56.5 | 2.65
2171 | RWE Solar | ASE-160-GT-FT (155W) | RWE Solar : ASE-160-GT-FT (155W) | -0.38 | 69.6 | 3.08 | 155 | 56.7 | 2.73
2172 | RWE Solar | ASE-160-GT-FT (160W) | RWE Solar : ASE-160-GT-FT (160W) | -0.38 | 70.4 | 3.13 | 160 | 56.9 | 2.81
2173 | RWE Solar | ASE-160-GT-FT (165W) | RWE Solar : ASE-160-GT-FT (165W) | -0.38 | 70.5 | 3.2 | 165 | 57 | 2.9
2174 | RWE Solar | ASE-160-GT-FT (170Wp) | RWE Solar : ASE-160-GT-FT (170Wp) | -0.38 | 71.2 | 3.24 | 170 | 57 | 2.99
2175 | RWE Solar | ASE-165-GT-FT /MC (160Wp) | RWE Solar : ASE-165-GT-FT /MC (160Wp) | -0.38 | 43.5 | 5.12 | 160 | 35.9 | 4.46
2176 | RWE Solar | ASE-165-GT-FT/MC (165Wp) | RWE Solar : ASE-165-GT-FT/MC (165Wp) | -0.38 | 43.8 | 5.18 | 165 | 36 | 4.58
2177 | RWE Solar | ASE-165-GT-FT/MC (170Wp) | RWE Solar : ASE-165-GT-FT/MC (170Wp) | -0.38 | 44 | 5.25 | 170 | 36 | 4.71
2178 | RWE Solar | ASE-190-GT-FT/TF (180Wp) | RWE Solar : ASE-190-GT-FT/TF (180Wp) | -0.36 | 44.1 | 5.6 | 180 | 36 | 5.01
2179 | RWE Solar | ASE-190-GT-FT/TF (188Wp) | RWE Solar : ASE-190-GT-FT/TF (188Wp) | -0.36 | 44.6 | 5.7 | 188 | 36 | 5.22
2180 | RWE Solar | ASE-200-GT-FT (218Wp) | RWE Solar : ASE-200-GT-FT (218Wp) | -0.38 | 58.3 | 5.05 | 218 | 48 | 4.55
2181 | RWE Solar | ASE-205 | RWE Solar : ASE-205 | -0.38 | 57.8 | 4.97 | 210 | 48 | 4.38
2182 | RWE Solar | ASE-210 | RWE Solar : ASE-210 | -0.38 | 57.7 | 4.8 | 210 | 47.7 | 4.4
2183 | RWE Solar | ASE-250-DG-FR/MC 15, 250 W | RWE Solar : ASE-250-DG-FR/MC 15, 250 W | -0.381 | 72 | 4.86 | 250 | 59.5 | 4.2
2184 | RWE Solar | ASE-250-DG-FR/MC 15, 260 W | RWE Solar : ASE-250-DG-FR/MC 15, 260 W | -0.38 | 72.6 | 4.9 | 260 | 59.8 | 4.35
2185 | RWE Solar | ASE-250-DG-FT/MC (265 Wp) | RWE Solar : ASE-250-DG-FT/MC (265 Wp) | -0.38 | 72.4 | 4.96 | 265 | 58.7 | 4.52
2186 | RWE Solar | ASE-250-DG-FT/MC (275 Wp) | RWE Solar : ASE-250-DG-FT/MC (275 Wp) | -0.38 | 73.1 | 5.07 | 275 | 59.1 | 4.65
2187 | RWE Solar | ASE-250-DG-FT/MC (285 Wp) | RWE Solar : ASE-250-DG-FT/MC (285 Wp) | -0.38 | 73.6 | 5.15 | 285 | 59.7 | 4.77
2188 | RWE Solar | ASE-250-DG-UR/MC 15, 250 W | RWE Solar : ASE-250-DG-UR/MC 15, 250 W | -0.381 | 72 | 4.86 | 250 | 59.5 | 4.2
2189 | RWE Solar | ASE-250-DG-UR/MC 15, 260 W | RWE Solar : ASE-250-DG-UR/MC 15, 260 W | -0.38 | 72.6 | 4.9 | 260 | 59.8 | 4.35
2190 | RWE Solar | ASE-260-DG-FT (250Wp) | RWE Solar : ASE-260-DG-FT (250Wp) | -0.38 | 70.4 | 4.78 | 250 | 57.1 | 4.37
2191 | RWE Solar | ASE-260-DG-FT (260Wp) | RWE Solar : ASE-260-DG-FT (260Wp) | -0.38 | 70.9 | 4.91 | 260 | 57.1 | 4.55
2192 | RWE Solar | ASE-260-DG-FT (268Wp) | RWE Solar : ASE-260-DG-FT (268Wp) | -0.38 | 71.4 | 5 | 268 | 57.2 | 4.69
2193 | RWE Solar | ASE-275-DG-FT (275W) | RWE Solar : ASE-275-DG-FT (275W) | -0.38 | 73.1 | 5.07 | 275 | 59.1 | 4.65
2194 | RWE Solar | ASE-275-DG-FT (285W) | RWE Solar : ASE-275-DG-FT (285W) | -0.38 | 73.6 | 5.15 | 285 | 59.7 | 4.77
2195 | RWE Solar | ASE-300-DG-FT / 17 V, 300 W | RWE Solar : ASE-300-DG-FT / 17 V, 300 W | -0.38 | 20 | 19.1 | 300 | 17.2 | 17.4
2196 | RWE Solar | ASE-300-DG-FT, 285 W | RWE Solar : ASE-300-DG-FT, 285 W | -0.38 | 60 | 6.2 | 285 | 50.5 | 5.64
2197 | RWE Solar | ASE-300-DG-FT, 300 W | RWE Solar : ASE-300-DG-FT, 300 W | -0.38 | 60 | 6.4 | 300 | 51.2 | 5.9
2198 | RWE Solar | ASE-300-DG-FT, 315 W | RWE Solar : ASE-300-DG-FT, 315 W | -0.38 | 64.5 | 6.7 | 315 | 51.7 | 6.1
2199 | RWE Solar | ASE-300-DG-FT/MC, 330 W | RWE Solar : ASE-300-DG-FT/MC, 330 W | -0.381 | 66.2 | 6.6 | 330 | 54.7 | 6.04
2200 | RWE Solar | ASE-300-DG-UT, 300 W | RWE Solar : ASE-300-DG-UT, 300 W | -0.38 | 60 | 6.4 | 300 | 51.2 | 5.9
2201 | RWE Solar | ASE-30-DG-UT, opak, 17 | RWE Solar : ASE-30-DG-UT, opak, 17 | -0.33 | 22.8 | 2.5 | 32 | 16.8 | 1.92
2202 | RWE Solar | ASE-30-DG-UT, opak, 36 V | RWE Solar : ASE-30-DG-UT, opak, 36 V | -0.331 | 49 | 1.13 | 32 | 36 | 0.89
2203 | RWE Solar | ASE-30-DG-UT, opak, 68 V | RWE Solar : ASE-30-DG-UT, opak, 68 V | -0.33 | 93 | 0.6 | 32 | 68 | 0.47
2204 | RWE Solar | ASE-30-DG-UT, semitransp,, 36 V | RWE Solar : ASE-30-DG-UT, semitransp,, 36 V | -0.331 | 49 | 1.02 | 27 | 36 | 0.75
2205 | RWE Solar | ASE-30-DG-UT, semitransp,, 68 V | RWE Solar : ASE-30-DG-UT, semitransp,, 68 V | -0.33 | 93 | 0.54 | 27 | 68 | 0.4
2206 | RWE Solar | ASE-50-ETF/17, 45 W | RWE Solar : ASE-50-ETF/17, 45 W | -0.38 | 20 | 2.9 | 45 | 17 | 2.65
2207 | RWE Solar | ASE-50-ETF/17, 50 W | RWE Solar : ASE-50-ETF/17, 50 W | -0.38 | 20 | 3.2 | 50 | 17.2 | 2.9
2208 | RWE Solar | ASI - F 32/12 (39,3W) | RWE Solar : ASI - F 32/12 (39,3W) | -0.35 | 22.8 | 2.5 | 32.2 | 16.8 | 1.92
2209 | RWE Solar | ASITHRU-30-SG | RWE Solar : ASITHRU-30-SG | -0.331 | 49 | 1.02 | 27 | 36 | 0.75
2210 | RWE Solar | InDax-100 | RWE Solar : InDax-100 | -0.38 | 26.8 | 5.05 | 100 | 22 | 4.54
2211 | RWE Solar | InDax-250 | RWE Solar : InDax-250 | -0.381 | 63.8 | 5.13 | 242 | 52.5 | 4.61
2212 | S.A.G. Solarstrom | 250 Plus | S.A.G. Solarstrom : 250 Plus | -0.33 | 36.3 | 9.5 | 250 | 30.3 | 8.3
2213 | S.A.G. Solarstrom | P 150 - Q5 | S.A.G. Solarstrom : P 150 - Q5 | -0.33 | 43.5 | 4.66 | 150 | 36.3 | 4.15
2214 | S.A.G. Solarstrom | S.A.G. 120 Q6 | S.A.G. Solarstrom : S.A.G. 120 Q6 | -0.346 | 22.1 | 7.2 | 120 | 18.5 | 6.5
2215 | S.A.G. Solarstrom | S.A.G. 200 Q6 | S.A.G. Solarstrom : S.A.G. 200 Q6 | -0.346 | 36.8 | 7.26 | 200 | 29.4 | 6.8
2216 | S.A.G. Solarstrom | SV-T-180 | S.A.G. Solarstrom : SV-T-180 | -0.34 | 21.3 | 11.64 | 180 | 17.1 | 10.53
2217 | S.A.G. Solarstrom | SV-T-190 | S.A.G. Solarstrom : SV-T-190 | -0.34 | 21.5 | 11.95 | 190 | 17.4 | 10.92
2218 | S.A.G. Solarstrom | SV-T-195 | S.A.G. Solarstrom : SV-T-195 | -0.34 | 21.7 | 12.11 | 195 | 17.6 | 11.08
2219 | S.A.G. Solarstrom | SV-T-200 | S.A.G. Solarstrom : SV-T-200 | -0.34 | 21.8 | 12.26 | 200 | 17.7 | 11.3
2220 | Saint-Gobain | Prosol-180KD | Saint-Gobain : Prosol-180KD | -0.4 | 42.1 | 7.4 | 240 | 33.8 | 7.02
2221 | Sanyo | HIP - 180BE3 180Wp | Sanyo : HIP - 180BE3 180Wp | -0.26 | 66.4 | 3.65 | 180 | 54 | 3.33
2222 | Sanyo | HIP - 180NE1 180Wp | Sanyo : HIP - 180NE1 180Wp | -0.26 | 45.5 | 5.49 | 180 | 36.5 | 4.93
2223 | Sanyo | HIP - 190BE3 190Wp | Sanyo : HIP - 190BE3 190Wp | -0.25 | 67.6 | 3.75 | 190 | 54.8 | 3.47
2224 | Sanyo | HIP - 190NE1 190Wp | Sanyo : HIP - 190NE1 190Wp | -0.25 | 46.4 | 5.57 | 190 | 37.6 | 5.05
2225 | Sanyo | HIP - 200NHE1 | Sanyo : HIP - 200NHE1 | -0.26 | 49.6 | 5.5 | 200 | 40 | 5
2226 | Sanyo | HIP-180BA3 | Sanyo : HIP-180BA3 | -0.26 | 66.4 | 3.65 | 180 | 54 | 3.33
2227 | Sanyo | HIP-180DA3 | Sanyo : HIP-180DA3 | -0.25 | 67 | 3.62 | 180 | 54.4 | 3.31
2228 | Sanyo | HIP-186BA3 | Sanyo : HIP-186BA3 | -0.25 | 67 | 3.71 | 186 | 54.4 | 3.42
2229 | Sanyo | HIP-186DA3 | Sanyo : HIP-186DA3 | -0.25 | 67.5 | 3.68 | 186 | 54.8 | 3.4
2230 | Sanyo | HIP-190BA3 | Sanyo : HIP-190BA3 | -0.25 | 67.5 | 3.75 | 190 | 54.8 | 3.47
2231 | Sanyo | HIP-190DA3 | Sanyo : HIP-190DA3 | -0.25 | 68.1 | 3.7 | 190 | 55.3 | 3.44
2232 | Sanyo | HIP-195BA3 | Sanyo : HIP-195BA3 | -0.25 | 68.1 | 3.79 | 195 | 55.3 | 3.53
2233 | Sanyo | HIP-195DA3 | Sanyo : HIP-195DA3 | -0.25 | 68.7 | 3.73 | 195 | 55.8 | 3.5
2234 | Sanyo | HIP-200BA3 | Sanyo : HIP-200BA3 | -0.25 | 68.7 | 3.83 | 200 | 55.8 | 3.59
2235 | Sanyo | HIP-200DA3 | Sanyo : HIP-200DA3 | -0.25 | 68.8 | 3.75 | 200 | 56.2 | 3.56
2236 | Sanyo | HIP-205BA3 | Sanyo : HIP-205BA3 | -0.25 | 68.8 | 3.84 | 205 | 56.7 | 3.62
2237 | Sanyo | HIP-205NKHE1 | Sanyo : HIP-205NKHE1 | -0.25 | 50.3 | 5.54 | 205 | 40.7 | 5.05
2238 | Sanyo | HIP-210NKHE1 | Sanyo : HIP-210NKHE1 | -0.25 | 50.9 | 5.57 | 210 | 41.3 | 5.09
2239 | Sanyo | HIP-215HDE1 | Sanyo : HIP-215HDE1 | -0.249 | 40.9 | 6.99 | 215 | 33.1 | 6.5
2240 | Sanyo | HIP-215NKHE1 | Sanyo : HIP-215NKHE1 | -0.25 | 51.6 | 5.61 | 215 | 42 | 5.13
2241 | Sanyo | HIP-220HDE1 | Sanyo : HIP-220HDE1 | -0.25 | 41.4 | 7.07 | 220 | 33.5 | 6.57
2242 | Sanyo | HIP-225HDE1 | Sanyo : HIP-225HDE1 | -0.251 | 41.9 | 7.14 | 225 | 33.9 | 6.64
2243 | Sanyo | HIP-230HDE1 | Sanyo : HIP-230HDE1 | -0.25 | 42.3 | 7.22 | 230 | 34.3 | 6.71
2244 | Sanyo | HIP-5618 | Sanyo : HIP-5618 | -0.4 | 23.9 | 3.61 | 56 | 18.1 | 3.09
2245 | Sanyo | HIP-6219 | Sanyo : HIP-6219 | -0.4 | 24.3 | 3.63 | 62.5 | 19 | 3.29
2246 | Sanyo | HIP-G751BI | Sanyo : HIP-G751BI | -0.4 | 64.9 | 3.63 | 167 | 51.4 | 3.25
2247 | Sanyo | HIP-H552BI | Sanyo : HIP-H552BI | -0.4 | 65.7 | 3.64 | 175 | 52.9 | 3.31
2248 | Sanyo | HIP-J54BI | Sanyo : HIP-J54BI | -0.4 | 66.4 | 3.65 | 180 | 54 | 3.33
2249 | Sanyo | HIT-235HDE4 | Sanyo : HIT-235HDE4 | -0.3 | 43.4 | 7.33 | 235 | 35.1 | 6.7
2250 | Sanyo | HIT-240HDE4 | Sanyo : HIT-240HDE4 | -0.3 | 43.6 | 7.37 | 240 | 35.5 | 6.77
2251 | Sanyo | HIT-N230SE10 | Sanyo : HIT-N230SE10 | -0.25 | 51.2 | 5.83 | 230 | 42.3 | 5.45
2252 | Sanyo | HIT-N235SE10 | Sanyo : HIT-N235SE10 | -0.25 | 51.8 | 5.84 | 235 | 43 | 5.48
2253 | Scanmodule | SCM 160 | Scanmodule : SCM 160 | -0.34 | 30.6 | 7.5 | 160 | 23.1 | 7.2
2254 | Scanmodule | SCM 180 | Scanmodule : SCM 180 | -0.34 | 30.6 | 8.2 | 180 | 24.5 | 7.5
2255 | Scheuten | 150-P5 A | Scheuten : 150-P5 A | -0.33 | 42.4 | 4.97 | 150 | 33.4 | 4.49
2256 | Scheuten | 150-P5-S | Scheuten : 150-P5-S | -0.33 | 43.9 | 5 | 160 | 35 | 4.57
2257 | Scheuten | 155 Wp (24V) | Scheuten : 155 Wp (24V) | -0.33 | 44.7 | 4.75 | 155 | 36.8 | 4.22
2258 | Scheuten | 180-P6 A | Scheuten : 180-P6 A | -0.34 | 32.3 | 7.81 | 185 | 25.5 | 7.25
2259 | Scheuten | 180-P6 S | Scheuten : 180-P6 S | -0.34 | 32.6 | 8.28 | 195 | 25.5 | 7.67
2260 | Scheuten | 200-P5 S | Scheuten : 200-P5 S | -0.33 | 58.1 | 5.07 | 215 | 47.4 | 4.54
2261 | Scheuten | 200-P5 S+ | Scheuten : 200-P5 S+ | -0.33 | 58.8 | 5.14 | 230 | 47.5 | 4.84
2262 | Scheuten | M5-96 220Wp | Scheuten : M5-96 220Wp | -0.33 | 58 | 5.13 | 220 | 46.4 | 4.74
2263 | Scheuten | M5-96 225Wp | Scheuten : M5-96 225Wp | -0.33 | 58.2 | 5.19 | 225 | 46.6 | 4.82
2264 | Scheuten | M5-96 230Wp | Scheuten : M5-96 230Wp | -0.33 | 58.4 | 5.24 | 230 | 46.9 | 4.9
2265 | Scheuten | M5-96 235Wp | Scheuten : M5-96 235Wp | -0.33 | 58.7 | 5.3 | 235 | 47.2 | 4.97
2266 | Scheuten | M5-96 240Wp | Scheuten : M5-96 240Wp | -0.33 | 59 | 5.36 | 240 | 47.5 | 5.05
2267 | Scheuten | M6-54 200Wp | Scheuten : M6-54 200Wp | -0.34 | 33.4 | 8.28 | 200 | 26.1 | 7.66
2268 | Scheuten | M6-54 205Wp | Scheuten : M6-54 205Wp | -0.34 | 33.5 | 8.3 | 205 | 26.6 | 7.72
2269 | Scheuten | M6-54 210Wp | Scheuten : M6-54 210Wp | -0.34 | 33.6 | 8.32 | 210 | 27 | 7.79
2270 | Scheuten | M6-66 250Wp | Scheuten : M6-66 250Wp | -0.34 | 40.9 | 8.3 | 250 | 32.4 | 7.72
2271 | Scheuten | M6-66 255Wp | Scheuten : M6-66 255Wp | -0.34 | 41 | 8.31 | 255 | 32.9 | 7.76
2272 | Scheuten | M6-66 260Wp | Scheuten : M6-66 260Wp | -0.34 | 41.1 | 8.32 | 260 | 33.3 | 7.81
2273 | Scheuten | M6-66 265Wp | Scheuten : M6-66 265Wp | -0.34 | 41.2 | 8.35 | 265 | 33.7 | 7.86
2274 | Scheuten | MULTISOL 150A 150Wp | Scheuten : MULTISOL 150A 150Wp | -0.33 | 43.6 | 4.49 | 150 | 36.4 | 4.13
2275 | Scheuten | MULTISOL 150S 160Wp | Scheuten : MULTISOL 150S 160Wp | -0.33 | 43.7 | 5.1 | 160 | 35.2 | 4.65
2276 | Scheuten | MULTISOL 180 180Wp | Scheuten : MULTISOL 180 180Wp | -0.33 | 32.5 | 7.5 | 180 | 25.9 | 7
2277 | Scheuten | MULTISOL 200A 200Wp | Scheuten : MULTISOL 200A 200Wp | -0.33 | 57.5 | 5.01 | 200 | 47.5 | 4.21
2278 | Scheuten | MULTISOL 200S 210Wp | Scheuten : MULTISOL 200S 210Wp | -0.33 | 57.7 | 4.6 | 210 | 47.5 | 4.42
2279 | Scheuten | Optisol P045072W | Scheuten : Optisol P045072W | -0.34 | 44.9 | 8.29 | 269.6 | 34.2 | 7.88
2280 | Scheuten | P5-96 205Wp | Scheuten : P5-96 205Wp | -0.33 | 57 | 4.91 | 205 | 45.5 | 4.51
2281 | Scheuten | P5-96 210Wp | Scheuten : P5-96 210Wp | -0.33 | 57.3 | 4.98 | 210 | 45.7 | 4.6
2282 | Scheuten | P5-96 215Wp | Scheuten : P5-96 215Wp | -0.33 | 57.6 | 5.06 | 215 | 46 | 4.68
2283 | Scheuten | P5-96 220Wp | Scheuten : P5-96 220Wp | -0.33 | 57.9 | 5.13 | 220 | 46.2 | 4.77
2284 | Scheuten | P5-96 225Wp | Scheuten : P5-96 225Wp | -0.33 | 58.2 | 5.2 | 225 | 46.4 | 4.85
2285 | Scheuten | P6-54 180Wp | Scheuten : P6-54 180Wp | -0.34 | 32.2 | 7.75 | 180 | 25.2 | 7.16
2286 | Scheuten | P6-54 185Wp | Scheuten : P6-54 185Wp | -0.34 | 32.4 | 7.87 | 185 | 25.4 | 7.29
2287 | Scheuten | P6-54 190Wp | Scheuten : P6-54 190Wp | -0.34 | 32.6 | 7.98 | 190 | 25.5 | 7.43
2288 | Scheuten | P6-54 195Wp | Scheuten : P6-54 195Wp | -0.34 | 32.8 | 8.1 | 195 | 25.7 | 7.57
2289 | Scheuten | P6-54 200Wp | Scheuten : P6-54 200Wp | -0.34 | 33 | 8.22 | 200 | 25.9 | 7.71
2290 | Scheuten | P6-54 205Wp | Scheuten : P6-54 205Wp | -0.34 | 33.1 | 8.33 | 205 | 26.1 | 7.85
2291 | Scheuten | P6-54 210Wp | Scheuten : P6-54 210Wp | -0.34 | 33.2 | 8.42 | 210 | 26.4 | 7.95
2292 | Scheuten | P6-66 240Wp | Scheuten : P6-66 240Wp | -0.34 | 40.1 | 8.12 | 240 | 31.5 | 7.6
2293 | Scheuten | P6-66 245Wp | Scheuten : P6-66 245Wp | -0.34 | 40.3 | 8.22 | 245 | 31.7 | 7.71
2294 | Scheuten | P6-66 250Wp | Scheuten : P6-66 250Wp | -0.34 | 40.5 | 8.31 | 250 | 31.9 | 7.83
2295 | Scheuten | P6-66 255Wp | Scheuten : P6-66 255Wp | -0.34 | 40.6 | 8.4 | 255 | 32.1 | 7.94
2296 | Scheuten | P6-66 260Wp | Scheuten : P6-66 260Wp | -0.34 | 40.8 | 8.5 | 260 | 32.3 | 8.05
2297 | Schlosser Systems | SSP 180 160Wp | Schlosser Systems : SSP 180 160Wp | -0.38 | 43.2 | 4.88 | 160 | 36 | 4.45
2298 | Schlosser Systems | SSP 180 165Wp | Schlosser Systems : SSP 180 165Wp | -0.38 | 43.2 | 5.04 | 165 | 36 | 4.58
2299 | Schlosser Systems | SSP 180 170Wp | Schlosser Systems : SSP 180 170Wp | -0.38 | 43.2 | 5.19 | 170 | 36 | 4.72
2300 | Schlosser Systems | SSP 180 175Wp | Schlosser Systems : SSP 180 175Wp | -0.38 | 43.8 | 5.33 | 175 | 36.15 | 4.84
2301 | Schlosser Systems | SSP 180 48 Cells 180Wp | Schlosser Systems : SSP 180 48 Cells 180Wp | -0.2 | 28.5 | 8.1 | 180 | 24 | 7.5
2302 | Schlosser Systems | SSP 180 54 Cells 200Wp | Schlosser Systems : SSP 180 54 Cells 200Wp | -0.38 | 32.67 | 8.08 | 200 | 27.22 | 7.35
2303 | Schlosser Systems | SSP 180 54 Cells 210Wp | Schlosser Systems : SSP 180 54 Cells 210Wp | -0.38 | 32.76 | 8.46 | 180 | 27.3 | 7.7
2304 | Schlosser Systems | SSP 180 54 Cells 220Wp | Schlosser Systems : SSP 180 54 Cells 220Wp | -0.38 | 32.88 | 8.83 | 220 | 27.4 | 8.03
2305 | Schlosser Systems | SSP 180 72 Cells 180Wp | Schlosser Systems : SSP 180 72 Cells 180Wp | -0.38 | 43.64 | 5.45 | 180 | 36.36 | 4.95
2306 | Schlosser Systems | SSP 180 72 Cells 260Wp | Schlosser Systems : SSP 180 72 Cells 260Wp | -0.38 | 43.2 | 7.95 | 260 | 36 | 7.23
2307 | Schlosser Systems | SSP 180 72 Cells 270Wp | Schlosser Systems : SSP 180 72 Cells 270Wp | -0.38 | 43.2 | 8.25 | 270 | 36 | 7.5
2308 | Schlosser Systems | SSP 180 72 Cells 280Wp | Schlosser Systems : SSP 180 72 Cells 280Wp | -0.38 | 43.2 | 8.55 | 280 | 36 | 7.78
2309 | Schott solar | ASE-165-GT-FT 160Wp | Schott solar : ASE-165-GT-FT 160Wp | -0.38 | 43.5 | 5.12 | 160 | 35.9 | 4.46
2310 | Schott solar | ASE-165-GT-FT 165Wp | Schott solar : ASE-165-GT-FT 165Wp | -0.38 | 43.6 | 5.27 | 165 | 35.1 | 4.7
2311 | Schott solar | ASE-165-GT-FT 170Wp | Schott solar : ASE-165-GT-FT 170Wp | -0.38 | 44 | 5.3 | 170 | 35.5 | 4.78
2312 | Schott solar | ASE-165-GT-FT 175Wp | Schott solar : ASE-165-GT-FT 175Wp | -0.38 | 44.3 | 5.34 | 175 | 35.9 | 4.87
2313 | Schott solar | ASE-260-DG-FT 250Wp | Schott solar : ASE-260-DG-FT 250Wp | -0.38 | 70.4 | 4.78 | 250 | 57.1 | 4.37
2314 | Schott solar | ASE-260-DG-FT 260Wp | Schott solar : ASE-260-DG-FT 260Wp | -0.38 | 70.9 | 4.91 | 260 | 57.1 | 4.55
2315 | Schott solar | ASE-260-DG-FT 268Wp | Schott solar : ASE-260-DG-FT 268Wp | -0.38 | 71.4 | 5 | 268 | 57.2 | 4.69
2316 | Schott solar | ASE-270-DGF/50 260Wp | Schott solar : ASE-270-DGF/50 260Wp | -0.38 | 60.8 | 5.9 | 260 | 48.7 | 5.3
2317 | Schott solar | ASE-270-DGF/50 270Wp | Schott solar : ASE-270-DGF/50 270Wp | -0.38 | 61.3 | 6.1 | 270 | 49.1 | 5.5
2318 | Schott solar | ASE-275-DG-FT/MC 265Wp | Schott solar : ASE-275-DG-FT/MC 265Wp | -0.38 | 70.9 | 5.13 | 265 | 56.7 | 4.68
2319 | Schott solar | ASE-275-DG-FT/MC 274Wp | Schott solar : ASE-275-DG-FT/MC 274Wp | -0.38 | 71.5 | 5.23 | 274 | 57.4 | 4.78
2320 | Schott solar | ASE-283-DG-FT/MC 283Wp | Schott solar : ASE-283-DG-FT/MC 283Wp | -0.38 | 72.3 | 5.33 | 283 | 58.2 | 4.87
2321 | Schott solar | ASI-F-32/12 39,3Wp | Schott solar : ASI-F-32/12 39,3Wp | -0.33 | 22.8 | 2.5 | 39.3 | 16.8 | 1.92
2322 | Schott solar | ASIOPAK-30-SG | Schott solar : ASIOPAK-30-SG | -0.31 | 49 | 1.13 | 32.2 | 36 | 0.89
2323 | Schott solar | ASITHRU-30-SG | Schott solar : ASITHRU-30-SG | -0.33 | 49 | 1.02 | 33 | 36 | 0.75
2324 | Schott solar | ASI-tm 100 | Schott solar : ASI-tm 100 | -0.31 | 23.8 | 6.79 | 100 | 17.5 | 5.71
2325 | Schott solar | ASI-tm 87 | Schott solar : ASI-tm 87 | -0.31 | 23.3 | 6.5 | 87 | 17.2 | 5.07
2326 | Schott solar | ASI-tm 90 | Schott solar : ASI-tm 90 | -0.31 | 23.4 | 6.6 | 90 | 17.3 | 5.21
2327 | Schott solar | ASI-tm 95 | Schott solar : ASI-tm 95 | -0.31 | 23.6 | 6.69 | 95 | 17.4 | 5.47
2328 | Schott solar | EGM TM 155 | Schott solar : EGM TM 155 | -0.38 | 42.4 | 5.15 | 155 | 33.3 | 4.66
2329 | Schott solar | EGM TM 160 | Schott solar : EGM TM 160 | -0.38 | 42.8 | 5.23 | 160 | 33.6 | 4.77
2330 | Schott solar | EGM TM 165 | Schott solar : EGM TM 165 | -0.38 | 43.1 | 5.32 | 165 | 33.8 | 4.88
2331 | SCHOTT solar | MONO 180 | SCHOTT solar : MONO 180 | -0.326 | 44.8 | 5.4 | 180 | 36.2 | 4.97
2332 | SCHOTT solar | MONO 185 | SCHOTT solar : MONO 185 | -0.326 | 45 | 5.43 | 185 | 36.3 | 5.1
2333 | SCHOTT solar | MONO 190 | SCHOTT solar : MONO 190 | -0.326 | 45.2 | 5.46 | 190 | 36.4 | 5.22
2334 | Schott Solar | Ploy 230 | Schott Solar : Ploy 230 | -0.38 | 36.9 | 8.33 | 230 | 30 | 7.66
2335 | Schott Solar | Poly 210 | Schott Solar : Poly 210 | -0.38 | 36.1 | 7.95 | 210 | 29.3 | 7.16
2336 | Schott Solar | Poly 220 | Schott Solar : Poly 220 | -0.38 | 36.5 | 8.15 | 220 | 29.7 | 7.41
2337 | SCHOTT solar | POLY 225 | SCHOTT solar : POLY 225 | -0.335 | 36.7 | 8.24 | 225 | 29.8 | 7.55
2338 | SCHOTT solar | POLY 230 | SCHOTT solar : POLY 230 | -0.333 | 36.9 | 8.33 | 230 | 30 | 7.66
2339 | SCHOTT solar | POLY 235 | SCHOTT solar : POLY 235 | -0.334 | 37.1 | 8.42 | 235 | 30.2 | 7.78
2340 | SCHOTT solar | POLY 290 | SCHOTT solar : POLY 290 | -0.334 | 48.5 | 8.1 | 290 | 39.5 | 7.33
2341 | Schott solar | Poly TM 165 | Schott solar : Poly TM 165 | -0.38 | 43.6 | 5.27 | 165 | 35.1 | 4.7
2342 | Schott solar | Poly TM 170 | Schott solar : Poly TM 170 | -0.38 | 44 | 5.3 | 170 | 35.5 | 4.78
2343 | Schott solar | Poly TM 175 | Schott solar : Poly TM 175 | -0.38 | 44.3 | 5.35 | 175 | 35.9 | 4.87
2344 | Schott solar | Poly TM 180 | Schott solar : Poly TM 180 | -0.38 | 44.6 | 5.39 | 180 | 36.3 | 4.95
2345 | Schott solar | Poly TM 217 | Schott solar : Poly TM 217 | -0.38 | 36.4 | 8.1 | 217 | 29.6 | 7.33
2346 | Schott solar | Poly TM 225 | Schott solar : Poly TM 225 | -0.38 | 36.7 | 8.24 | 225 | 29.8 | 7.55
2347 | Schott solar | Poly TM 232 | Schott solar : Poly TM 232 | -0.38 | 37 | 8.36 | 232 | 30.1 | 7.7
2348 | Schuco | CS5A 170M dark | Schuco : CS5A 170M dark | -0.36 | 43.2 | 5.38 | 170 | 34.4 | 4.95
2349 | Schüco | MPE-MS04-210 | Schüco : MPE-MS04-210 | -0.35 | 36.4 | 7.91 | 210 | 28.9 | 7.26
2350 | Schüco | MPE-MS04-215 | Schüco : MPE-MS04-215 | -0.35 | 36.5 | 8.01 | 215 | 29 | 7.43
2351 | Schüco | MPE-MS04-220 | Schüco : MPE-MS04-220 | -0.35 | 36.6 | 8.09 | 220 | 29.3 | 7.52
2352 | Schüco | MPE-MS04-225 | Schüco : MPE-MS04-225 | -0.35 | 36.7 | 8.19 | 225 | 29.5 | 7.63
2353 | Schüco | MPE-MS04-230 | Schüco : MPE-MS04-230 | -0.35 | 36.7 | 8.34 | 230 | 29.8 | 7.71
2354 | Schüco | MPE-MS04-235 | Schüco : MPE-MS04-235 | -0.35 | 36.9 | 8.47 | 235 | 30.1 | 7.82
2355 | Schüco | MPE-MS04-240 | Schüco : MPE-MS04-240 | -0.35 | 37 | 8.61 | 240 | 30.4 | 7.91
2356 | Schüco | MPE-MS05-175 | Schüco : MPE-MS05-175 | -0.38 | 44 | 5.48 | 175 | 35.2 | 4.98
2357 | Schüco | MPE-MS05-180 | Schüco : MPE-MS05-180 | -0.38 | 44.3 | 5.59 | 180 | 35.4 | 5.11
2358 | Schüco | MPE-MS05-185 | Schüco : MPE-MS05-185 | -0.38 | 44.6 | 5.68 | 185 | 35.6 | 5.21
2359 | Schüco | MPE-MS06-170 | Schüco : MPE-MS06-170 | -0.35 | 43.59 | 5.2 | 170 | 34.7 | 4.9
2360 | Schüco | MPE-MS06-175 | Schüco : MPE-MS06-175 | -0.35 | 44.4 | 5.3 | 175 | 35 | 5
2361 | Schüco | MPE-MS06-180 | Schüco : MPE-MS06-180 | -0.35 | 44.8 | 5.45 | 180 | 35.3 | 5.1
2362 | Schüco | MPE-MS06-185 | Schüco : MPE-MS06-185 | -0.35 | 45.2 | 5.5 | 185 | 36 | 5.15
2363 | Schüco | MPE-MS06-190 | Schüco : MPE-MS06-190 | -0.35 | 45.6 | 5.55 | 190 | 36.5 | 5.2
2364 | Schüco | MPE-PS04-210 | Schüco : MPE-PS04-210 | -0.35 | 36.4 | 7.91 | 210 | 28.9 | 7.26
2365 | Schüco | MPE-PS04-215 | Schüco : MPE-PS04-215 | -0.35 | 36.5 | 8.01 | 215 | 29 | 7.43
2366 | Schüco | MpE-PS04-220 | Schüco : MpE-PS04-220 | -0.35 | 36.6 | 8.09 | 220 | 29.3 | 7.52
2367 | Schüco | MPE-PS04-230 | Schüco : MPE-PS04-230 | -0.35 | 36.8 | 8.34 | 230 | 29.8 | 7.71
2368 | Schüco | MPE-PS15-220 | Schüco : MPE-PS15-220 | -0.32 | 36.5 | 8.12 | 220 | 29.8 | 7.4
2369 | Schüco | MPE-PS15-225 | Schüco : MPE-PS15-225 | -0.32 | 36.7 | 8.18 | 225 | 29.9 | 7.53
2370 | Schüco | MPE-PS15-230 | Schüco : MPE-PS15-230 | -0.32 | 36.8 | 8.34 | 230 | 30 | 7.67
2371 | Schüco | MPE-PS15-235 | Schüco : MPE-PS15-235 | -0.32 | 36.8 | 8.44 | 235 | 30.1 | 7.81
2372 | Schüco | MPE-PS15-240 | Schüco : MPE-PS15-240 | -0.32 | 37 | 8.54 | 240 | 30.2 | 7.95
2373 | Schüco | PME-PS04-225 | Schüco : PME-PS04-225 | -0.35 | 36.7 | 8.19 | 225 | 29.5 | 7.63
2374 | Schüco | S 125-SP | Schüco : S 125-SP | -0.364 | 24 | 7.27 | 125 | 18.8 | 6.65
2375 | Schüco | S 130-SP | Schüco : S 130-SP | -0.358 | 24.2 | 7.39 | 130 | 19.2 | 6.79
2376 | Schüco | S 158-SP | Schüco : S 158-SP | -0.346 | 30.1 | 7.33 | 158 | 23.6 | 6.68
2377 | Schüco | S 158-SP | Schüco : S 158-SP | -0.35 | 30.1 | 7.33 | 158 | 23.6 | 6.68
2378 | Schüco | S 165-SP | Schüco : S 165-SP | -0.335 | 30.4 | 7.36 | 165 | 24.2 | 6.83
2379 | Schüco | S 165-SP-4 | Schüco : S 165-SP-4 | -0.346 | 29.7 | 7.73 | 165 | 23.4 | 7.06
2380 | Schüco | S 170-SP-4 | Schüco : S 170-SP-4 | -0.346 | 29.9 | 7.83 | 170 | 23.7 | 7.19
2381 | Schüco | S 175-SP-4 | Schüco : S 175-SP-4 | -0.346 | 30.2 | 7.93 | 175 | 23.9 | 7.32
2382 | Schüco | S 180-SP-4 | Schüco : S 180-SP-4 | -0.346 | 30.4 | 8.03 | 180 | 24.2 | 7.45
2383 | Schüco | S 300 K | Schüco : S 300 K | -0.38 | 64 | 6.3 | 300 | 53.5 | 5.6
2384 | Schüco | S 300-1 | Schüco : S 300-1 | -0.4 | 84 | 4.55 | 288 | 66.6 | 4.32
2385 | Schüco | S 300-K | Schüco : S 300-K | -0.4 | 65 | 6.2 | 300 | 53.5 | 5.6
2386 | Schüco | S 310-PM-5/-6 | Schüco : S 310-PM-5/-6 | -0.35 | 87.5 | 5 | 310 | 73.3 | 4.25
2387 | Schüco | S 315-PM | Schüco : S 315-PM | -0.331 | 87.6 | 4.62 | 315 | 72.9 | 4.32
2388 | Schüco | S 320-PM-5/-6 | Schüco : S 320-PM-5/-6 | -0.35 | 87.8 | 5.1 | 320 | 73.8 | 4.35
2389 | Schüco | S 325 K | Schüco : S 325 K | -0.38 | 64 | 6.8 | 325 | 53.5 | 6.1
2390 | Schüco | S 325-K | Schüco : S 325-K | -0.4 | 65 | 6.8 | 325 | 53.5 | 6.1
2391 | Schüco | S 325-PM | Schüco : S 325-PM | -0.331 | 87.8 | 4.69 | 325 | 73.4 | 4.43
2392 | Schüco | S 325-PP | Schüco : S 325-PP | -0.33 | 88.3 | 5.05 | 325 | 72 | 4.51
2393 | Schüco | S 330-PM-5/-6 | Schüco : S 330-PM-5/-6 | -0.35 | 88.4 | 5.2 | 330 | 73.9 | 4.5
2394 | Schüco | S 340 K | Schüco : S 340 K | -0.33 | 67.7 | 6.6 | 340 | 55.6 | 6.13
2395 | Schüco | S 340-K | Schüco : S 340-K | -0.4 | 67.7 | 6.6 | 340 | 53.6 | 6.1
2396 | Schüco | S 340-PM-5/-6 | Schüco : S 340-PM-5/-6 | -0.35 | 89.3 | 5.3 | 340 | 74.1 | 4.6
2397 | Schüco | S 340-PP | Schüco : S 340-PP | -0.33 | 88.3 | 5.13 | 340 | 72 | 4.66
2398 | Schüco | S 350-PM-5/-6 | Schüco : S 350-PM-5/-6 | -0.35 | 89.4 | 5.4 | 350 | 74.2 | 4.75
2399 | Schüco | S 360-PM-5/-6 | Schüco : S 360-PM-5/-6 | -0.35 | 89.4 | 5.5 | 360 | 74.3 | 4.9
2400 | Schüco | SPV 165-SMC-2 | Schüco : SPV 165-SMC-2 | -0.35 | 43.2 | 5.23 | 165 | 34.4 | 4.8
2401 | Schüco | SPV 165-SMY-1/-2 | Schüco : SPV 165-SMY-1/-2 | -0.35 | 44 | 5.2 | 165 | 34.8 | 4.74
2402 | Schüco | SPV 170-SMC-2 | Schüco : SPV 170-SMC-2 | -0.35 | 43.4 | 5.38 | 170 | 34.6 | 4.91
2403 | Schüco | SPV 170-SMY-1/-2 | Schüco : SPV 170-SMY-1/-2 | -0.35 | 44.2 | 5.28 | 170 | 35 | 4.86
2404 | Schüco | SPV 175-SMC-2 | Schüco : SPV 175-SMC-2 | -0.35 | 43.6 | 5.55 | 175 | 34.8 | 5.03
2405 | Schüco | SPV 175-SMY-1/-2 | Schüco : SPV 175-SMY-1/-2 | -0.35 | 44.4 | 5.36 | 175 | 35.2 | 4.97
2406 | Schüco | SPV 180-SMC-2 | Schüco : SPV 180-SMC-2 | -0.35 | 43.6 | 5.6 | 180 | 35 | 5.14
2407 | Schüco | SPV 180-SMY-1/-2 | Schüco : SPV 180-SMY-1/-2 | -0.35 | 44.6 | 5.42 | 180 | 35.4 | 5.08
2408 | Schüco | SPV 190-SPS-1/-2/-3 | Schüco : SPV 190-SPS-1/-2/-3 | -0.38 | 32.6 | 7.98 | 190 | 26.7 | 7.12
2409 | Schüco | SPV 195-SPS-1/-2/-3 | Schüco : SPV 195-SPS-1/-2/-3 | -0.38 | 32.7 | 8.06 | 195 | 26.8 | 7.28
2410 | Schüco | SPV 200-SPS-1/-2/-3 | Schüco : SPV 200-SPS-1/-2/-3 | -0.38 | 32.8 | 8.24 | 200 | 26.9 | 7.44
2411 | Schüco | SPV 205-SPS-1/-2/-3 | Schüco : SPV 205-SPS-1/-2/-3 | -0.38 | 32.9 | 8.35 | 205 | 27 | 7.6
2412 | Schüco | SPV 210-SPS-1/-2/-3 | Schüco : SPV 210-SPS-1/-2/-3 | -0.38 | 33 | 8.48 | 210 | 27.1 | 7.75
2413 | SchwabenSolar | AS 165 | SchwabenSolar : AS 165 | -0.4 | 43.1 | 5.43 | 165 | 34.6 | 4.77
2414 | SE Project | SEM160/150S 12V | SE Project : SEM160/150S 12V | -0.368 | 21.5 | 9.2 | 150 | 17.5 | 8.6
2415 | SE Project | SEM160/150S 24V | SE Project : SEM160/150S 24V | -0.368 | 43 | 4.6 | 150 | 34.9 | 4.3
2416 | SE Project | SEM160/160S 12V | SE Project : SEM160/160S 12V | -0.366 | 21.62 | 9.8 | 160 | 17.68 | 9.04
2417 | SE Project | SEM160/160S 24V | SE Project : SEM160/160S 24V | -0.366 | 43.24 | 4.9 | 160 | 35.35 | 4.52
2418 | SE Project | SEM160/170S 12V | SE Project : SEM160/170S 12V | -0.353 | 22.43 | 10.2 | 170 | 17.82 | 9.54
2419 | SE Project | SEM160/170S 24V | SE Project : SEM160/170S 24V | -0.353 | 44.86 | 5.1 | 170 | 35.64 | 4.77
2420 | SE Project | SEM160/175S 12V | SE Project : SEM160/175S 12V | -0.352 | 22.53 | 10.42 | 175 | 17.82 | 9.82
2421 | SE Project | SEM160/175S 24V | SE Project : SEM160/175S 24V | -0.352 | 45.06 | 5.21 | 175 | 35.64 | 4.91
2422 | SE Project | SEM160/180S 12V | SE Project : SEM160/180S 12V | -0.351 | 22.55 | 10.46 | 180 | 17.82 | 10.1
2423 | SE Project | SEM160/180S 24V | SE Project : SEM160/180S 24V | -0.351 | 45.1 | 5.23 | 180 | 17.82 | 10.1
2424 | SE Project | SEM160-M 180W | SE Project : SEM160-M 180W | -0.22 | 44.2 | 5.28 | 180 | 36.36 | 4.95
2425 | Sensotec | ST200P-20 | Sensotec : ST200P-20 | -0.34 | 36.5 | 7.28 | 200 | 29.2 | 6.85
2426 | Sensotec | ST210P-20 | Sensotec : ST210P-20 | -0.34 | 36.69 | 7.6 | 210 | 29.4 | 7.14
2427 | Sensotec | ST210W (60) | Sensotec : ST210W (60) | -0.33 | 36.2 | 8.08 | 210 | 28.1 | 7.48
2428 | Sensotec | ST220P-20 | Sensotec : ST220P-20 | -0.34 | 36.9 | 7.93 | 220 | 29.41 | 7.48
2429 | Sensotec | ST220W (60) | Sensotec : ST220W (60) | -0.33 | 36.8 | 8.15 | 220 | 29 | 7.6
2430 | Sensotec | ST230P-20 | Sensotec : ST230P-20 | -0.34 | 37.31 | 8.19 | 230 | 29.8 | 7.72
2431 | Sensotec | ST230W (60) | Sensotec : ST230W (60) | -0.33 | 37 | 8.26 | 230 | 29.8 | 7.72
2432 | Sensotec | ST235W (60) | Sensotec : ST235W (60) | -0.33 | 37.1 | 8.33 | 235 | 30.1 | 7.81
2433 | Sensotec | ST240P-24 | Sensotec : ST240P-24 | -0.34 | 43.2 | 7.7 | 240 | 34.4 | 6.98
2434 | Sensotec | ST240W (60) | Sensotec : ST240W (60) | -0.33 | 37.2 | 8.37 | 240 | 30.4 | 7.89
2435 | Sensotec | ST250P-24 | Sensotec : ST250P-24 | -0.34 | 42.9 | 8.51 | 250 | 34.6 | 7.23
2436 | Sensotec | ST260P-24 | Sensotec : ST260P-24 | -0.34 | 43.03 | 8.57 | 260 | 34.7 | 7.49
2437 | Sensotec | ST270P-24 | Sensotec : ST270P-24 | -0.34 | 43.65 | 8.59 | 270 | 35.02 | 7.71
2438 | Sensotec | ST280P-24 | Sensotec : ST280P-24 | -0.34 | 43.77 | 8.76 | 280 | 35.3 | 7.93
2439 | SES 21 AG | SES 210 Main | SES 21 AG : SES 210 Main | -0.4 | 26.8 | 9.5 | 210 | 22.2 | 9
2440 | SES 21 AG | SES Solo-50 | SES 21 AG : SES Solo-50 | -0.4 | 13.3 | 4.8 | 50 | 11.1 | 4.5
2441 | Sesol | Sesol Quick D4 (45.5 Wp) | Sesol : Sesol Quick D4 (45.5 Wp) | -0.33 | 12.2 | 4.92 | 45.5 | 10 | 4.5
2442 | Sesol | Sesol Quick D4 (46.5 Wp) | Sesol : Sesol Quick D4 (46.5 Wp) | -0.33 | 8.4 | 7.5 | 46.5 | 6.8 | 6.8
2443 | Sesol | Solardachstein Ty Fr Pf 1-4/47 | Sesol : Solardachstein Ty Fr Pf 1-4/47 | -0.4 | 18.6 | 3.4 | 47 | 14.7 | 3.2
2444 | SET GmbH | MM 110 - 12 | SET GmbH : MM 110 - 12 | -0.4 | 21 | 7.44 | 110 | 17 | 6.47
2445 | SET GmbH | MP 105 - 12 | SET GmbH : MP 105 - 12 | -0.4 | 21 | 7.44 | 110 | 17 | 6.47
2446 | Shanghai Solar | S-165D | Shanghai Solar : S-165D | -0.38 | 29 | 7.82 | 165 | 23.5 | 7.02
2447 | Shanghai Solar | S-100D | Shanghai Solar : S-100D | -0.4 | 21.5 | 6.42 | 100 | 17 | 5.89
2448 | Shanghai Solar | S-120D | Shanghai Solar : S-120D | -0.4 | 21.5 | 7.7 | 120 | 17 | 7.06
2449 | Shanghai Solar | S-125DJ | Shanghai Solar : S-125DJ | -0.4 | 22 | 7.8 | 125 | 17.5 | 7.15
2450 | Shanghai Solar | S-165DJ | Shanghai Solar : S-165DJ | -0.4 | 29 | 7.82 | 165 | 23.5 | 7.02
2451 | Shanghai Solar | S-165DJ-T | Shanghai Solar : S-165DJ-T | -0.4 | 44 | 5.21 | 165 | 35 | 4.65
2452 | Sharp | NA-801WP | Sharp : NA-801WP | -0.3 | 63.3 | 2.08 | 80 | 47.6 | 1.68
2453 | Sharp | NA-851WP | Sharp : NA-851WP | -0.3 | 63.8 | 2.11 | 85 | 49 | 1.74
2454 | Sharp | NA-901WP | Sharp : NA-901WP | -0.3 | 65.2 | 2.11 | 90 | 49.3 | 1.83
2455 | Sharp | NA-F110 (A5) | Sharp : NA-F110 (A5) | -0.3 | 233 | 0.8 | 110 | 172 | 0.64
2456 | Sharp | NA-F115 (A5) | Sharp : NA-F115 (A5) | -0.3 | 238 | 0.81 | 115 | 174 | 0.661
2457 | Sharp | NA-F115 (G5) | Sharp : NA-F115 (G5) | -0.35 | 59.6 | 3.34 | 135.4 | 47.7 | 2.85
2458 | Sharp | NA-F121 (A5) | Sharp : NA-F121 (A5) | -0.3 | 238 | 0.83 | 121 | 180 | 0.673
2459 | Sharp | NA-F128 (G5) | Sharp : NA-F128 (G5) | -0.3 | 60.8 | 3.54 | 150.6 | 48.6 | 3.1
2460 | Sharp | ND- N8(E3EF) | Sharp : ND- N8(E3EF) | -0.14 | 28.4 | 7.61 | 148 | 22.3 | 6.64
2461 | Sharp | ND- P8(E3EF) | Sharp : ND- P8(E3EF) | -0.14 | 28.6 | 7.92 | 158 | 22.5 | 7.03
2462 | Sharp | ND- Q2(E3EF) | Sharp : ND- Q2(E3EF) | -0.14 | 28.8 | 7.95 | 162 | 22.7 | 7.14
2463 | Sharp | ND-158 (E1), ND-158 (E1D) 158Wp | Sharp : ND-158 (E1), ND-158 (E1D) 158Wp | -0.366 | 28.4 | 7.85 | 158 | 22.5 | 7.04
2464 | Sharp | ND-158 (E1F) | Sharp : ND-158 (E1F) | -0.14 | 28.8 | 7.92 | 158 | 22.5 | 7.03
2465 | Sharp | ND-158 (E1F) 158Wp | Sharp : ND-158 (E1F) 158Wp | -0.364 | 28.6 | 7.92 | 158 | 22.5 | 7.03
2466 | Sharp | ND-162 (E1F) | Sharp : ND-162 (E1F) | -0.14 | 29.3 | 7.95 | 162 | 22.7 | 7.14
2467 | Sharp | ND-162 (E1F), ND-Q2 (E3EF) 162Wp | Sharp : ND-162 (E1F), ND-Q2 (E3EF) 162Wp | -0.361 | 28.8 | 7.95 | 162 | 22.7 | 7.14
2468 | Sharp | ND-170 (E1F) | Sharp : ND-170 (E1F) | -0.14 | 29.2 | 8.04 | 170 | 23.2 | 7.33
2469 | Sharp | ND-170 (E1F) 170Wp | Sharp : ND-170 (E1F) 170Wp | -0.355 | 29.3 | 8.04 | 170 | 23.2 | 7.33
2470 | Sharp | ND-175 (E1F) | Sharp : ND-175 (E1F) | -0.14 | 29.4 | 8.1 | 175 | 23.3 | 7.52
2471 | Sharp | ND-200(E1F) | Sharp : ND-200(E1F) | -0.361 | 36 | 7.9 | 200 | 28.4 | 7.05
2472 | Sharp | ND-210(E1F) | Sharp : ND-210(E1F) | -0.357 | 36.4 | 8.03 | 210 | 28.8 | 7.3
2473 | Sharp | ND220-E1F | Sharp : ND220-E1F | -0.36 | 36.5 | 8.2 | 220 | 29.2 | 7.54
2474 | Sharp | ND-F210A1 | Sharp : ND-F210A1 | -0.355 | 36.6 | 7.68 | 210 | 30.1 | 6.98
2475 | Sharp | ND-L3E6E | Sharp : ND-L3E6E | -0.35 | 21.3 | 8.12 | 123 | 17.2 | 7.16
2476 | Sharp | NDQ0E3E / ND160E1 160W | Sharp : NDQ0E3E / ND160E1 160W | -0.37 | 28.4 | 7.82 | 160 | 22.8 | 7.82
2477 | Sharp | ND-Q0E6E | Sharp : ND-Q0E6E | -0.35 | 28.4 | 8.04 | 160 | 22.8 | 7.02
2478 | Sharp | ND-Q0E7H | Sharp : ND-Q0E7H | -0.4 | 28.4 | 8.04 | 160 | 22.8 | 7.02
2479 | Sharp | NDQ2E3E / ND162E1 162W | Sharp : NDQ2E3E / ND162E1 162W | -0.3662 | 28.4 | 7.92 | 162 | 22.8 | 7.11
2480 | Sharp | NE-80E4H | Sharp : NE-80E4H | -0.4 | 21.3 | 5.31 | 80 | 17.1 | 4.67
2481 | Sharp | NE-L5E2E | Sharp : NE-L5E2E | -0.35 | 32.3 | 5.46 | 125 | 26 | 4.8
2482 | Sharp | NE-L5E3H | Sharp : NE-L5E3H | -0.4 | 32.3 | 5.46 | 125 | 26 | 4.8
2483 | Sharp | NE-Q5E2B -165 Wp | Sharp : NE-Q5E2B -165 Wp | -0.4 | 43.1 | 5.46 | 165 | 34.6 | 4.77
2484 | Sharp | NE-Q5E2E | Sharp : NE-Q5E2E | -0.35 | 43.1 | 5.46 | 165 | 34.6 | 4.77
2485 | Sharp | NE-Q5E3E | Sharp : NE-Q5E3E | -0.35 | 43.1 | 5.46 | 165 | 34.6 | 4.77
2486 | Sharp | NE-Q5E3H | Sharp : NE-Q5E3H | -0.4 | 43.1 | 5.46 | 165 | 34.6 | 4.77
2487 | Sharp | NT 51A 85S | Sharp : NT 51A 85S | -0.35 | 22 | 5.5 | 85.5 | 17.4 | 4.91
2488 | Sharp | NT-170 (E1), NT-R0 (E3E) 170Wp | Sharp : NT-170 (E1), NT-R0 (E3E) 170Wp | -0.353 | 44.2 | 5.3 | 170 | 35 | 4.86
2489 | Sharp | NT41A57E | Sharp : NT41A57E | -0.4 | 22 | 3.6 | 57 | 17.4 | 3.29
2490 | Sharp | NT50A72E/S | Sharp : NT50A72E/S | -0.4 | 21.8 | 4.55 | 72 | 17.3 | 4.17
2491 | Sharp | NT-R5E2E | Sharp : NT-R5E2E | -0.35 | 44.4 | 5.55 | 175 | 35.4 | 4.95
2492 | Sharp | NT-R5E3E | Sharp : NT-R5E3E | -0.35 | 44.4 | 5.55 | 175 | 35.4 | 4.95
2493 | Sharp | NT-R5E3H | Sharp : NT-R5E3H | -0.4 | 44.4 | 5.55 | 175 | 35.4 | 4.95
2494 | Sharp | NT-S5E3E | Sharp : NT-S5E3E | -0.34 | 44.9 | 5.6 | 185 | 36.21 | 5.11
2495 | Sharp | NU 235W | Sharp : NU 235W | -0.4 | 37 | 8.6 | 235 | 30 | 7.84
2496 | Sharp | NU-180 | Sharp : NU-180 | -0.38 | 30 | 8.37 | 180 | 23.7 | 7.6
2497 | Sharp | NU-180 (E1), NU-S0 (E3E) 180Wp | Sharp : NU-180 (E1), NU-S0 (E3E) 180Wp | -0.35 | 30 | 8.37 | 180 | 23.7 | 7.6
2498 | Sharp | NU-185 (E1), NU-S5 (E3E) 185Wp | Sharp : NU-185 (E1), NU-S5 (E3E) 185Wp | -0.344 | 30.2 | 8.54 | 185 | 24 | 7.71
2499 | Sharp | NU-E245J5 | Sharp : NU-E245J5 | -0.34667 | 37.5 | 8.73 | 245 | 30.5 | 8.04
2500 | Sharp | NU-R0 (E3E) 170Wp | Sharp : NU-R0 (E3E) 170Wp | -0.354 | 29.4 | 8.37 | 170 | 22.4 | 7.6
2501 | Sharp | NU-R5 (E3Z) 175Wp | Sharp : NU-R5 (E3Z) 175Wp | -0.349 | 29.8 | 8.29 | 175 | 23.2 | 7.55
2502 | Sharp | PE 90-16 | Sharp : PE 90-16 | -0.35 | 21.2 | 5.9 | 90 | 16.4 | 5.5
2503 | Sharp | SB-160 | Sharp : SB-160 | -0.4 | 28.4 | 8.04 | 160 | 22.8 | 7.02
2504 | Sharp | SG2R 115W RoofTop | Sharp : SG2R 115W RoofTop | -0.3 | 59.5 | 3.24 | 115 | 43.5 | 2.644
2505 | Sharp | SG2R 121W RoofTop | Sharp : SG2R 121W RoofTop | -0.3 | 59.5 | 3.32 | 121 | 45 | 2.692
2506 | Sharp | SG2R 128W RoofTop | Sharp : SG2R 128W RoofTop | -0.3 | 59.5 | 3.384 | 128 | 46.5 | 2.752
2507 | Sharp | Sharp ND-Q0E6B - 160Wp | Sharp : Sharp ND-Q0E6B - 160Wp | -0.338 | 28.4 | 8.04 | 160 | 22.8 | 7.02
2508 | Sharp | Sharp NE-Q5E2B - 165Wp | Sharp : Sharp NE-Q5E2B - 165Wp | -0.332 | 43.1 | 5.46 | 165 | 34.6 | 4.77
2509 | Sharp | NU-E235 (E2) | Sharp : NU-E235 (E2) | -0.35135 | 37 | 8.6 | 235 | 30 | 7.84
2510 | Sharp | NU-E240 (J5) | Sharp : NU-E240 (J5) | -0.34853 | 37.3 | 8.63 | 240 | 30.2 | 7.95
2511 | Sharp | NU-E245 (J5) | Sharp : NU-E245 (J5) | -0.34667 | 37.5 | 8.73 | 245 | 30.5 | 8.04
2512 | Shell Solar | IRS 110 MA | Shell Solar : IRS 110 MA | -0.4 | 32.3 | 4.6 | 109 | 26 | 4.2
2513 | Shell Solar | Powermax Plus 150 | Shell Solar : Powermax Plus 150 | -0.35 | 42.6 | 5.1 | 150 | 33 | 4.55
2514 | Shell Solar | Powermax Plus 160 | Shell Solar : Powermax Plus 160 | -0.34 | 43.1 | 5.2 | 160 | 34 | 4.71
2515 | Shell Solar | Powermax Ultra 165 | Shell Solar : Powermax Ultra 165 | -0.33 | 44.5 | 5.4 | 165 | 35 | 4.72
2516 | Shell Solar | Powermax Ultra 175 | Shell Solar : Powermax Ultra 175 | -0.32 | 44.6 | 5.43 | 175 | 35.4 | 4.95
2517 | Shell Solar | RSM 100 | Shell Solar : RSM 100 | -0.4 | 43 | 3.1 | 98 | 34 | 2.9
2518 | Shell Solar | RSM 115 | Shell Solar : RSM 115 | -0.4 | 32.8 | 4.7 | 113 | 26.6 | 4.25
2519 | Shell Solar | RSM100 | Shell Solar : RSM100 | -0.332 | 43.4 | 3.1 | 98 | 34 | 2.8
2520 | Shell Solar | RSM95 | Shell Solar : RSM95 | -0.45 | 42.4 | 3.1 | 95 | 33 | 3
2521 | Shell Solar | S105 | Shell Solar : S105 | -0.348 | 31.8 | 4.5 | 105 | 25.5 | 4.12
2522 | Shell Solar | S115 | Shell Solar : S115 | -0.366 | 32.8 | 4.7 | 115 | 26.8 | 4.29
2523 | Shell Solar | S25 | Shell Solar : S25 | -0.358 | 21.4 | 1.5 | 24 | 16.5 | 1.45
2524 | Shell Solar | S65 | Shell Solar : S65 | -0.371 | 20.9 | 4.3 | 65 | 16.5 | 3.64
2525 | Shell Solar | S70 | Shell Solar : S70 | -0.366 | 21.2 | 4.5 | 70 | 17 | 4.12
2526 | Shell Solar | S75 | Shell Solar : S75 | -0.364 | 21.6 | 4.7 | 75 | 17.6 | 4.26
2527 | Shell Solar | SM110-12 | Shell Solar : SM110-12 | -0.332 | 21.7 | 6.9 | 110 | 17.5 | 6.29
2528 | Shell Solar | SM110-24 | Shell Solar : SM110-24 | -0.332 | 43.5 | 3.45 | 110 | 35 | 3.14
2529 | Shell Solar | SM50-H | Shell Solar : SM50-H | -0.36 | 19.8 | 3.35 | 50 | 15.9 | 3.14
2530 | Shell Solar | SM55 | Shell Solar : SM55 | -0.355 | 21.7 | 3.45 | 55 | 17.4 | 3.16
2531 | Shell Solar | SP 130 | Shell Solar : SP 130 | -0.35 | 42.8 | 4.5 | 130 | 33 | 3.95
2532 | Shell Solar | SP 140-C | Shell Solar : SP 140-C | -0.376 | 42.8 | 4.7 | 140 | 33 | 4.25
2533 | Shell Solar | SP140 | Shell Solar : SP140 | -0.336 | 42.8 | 4.7 | 140 | 33 | 4.24
2534 | Shell Solar | SP150 | Shell Solar : SP150 | -0.332 | 43.4 | 4.8 | 150 | 34 | 4.41
2535 | Shell Solar | SP70 | Shell Solar : SP70 | -0.336 | 21.4 | 4.7 | 70 | 16.5 | 4.24
2536 | Shell Solar | SP75 | Shell Solar : SP75 | -0.332 | 21.7 | 4.8 | 75 | 17 | 4.4
2537 | Shell Solar | SQ 140-C | Shell Solar : SQ 140-C | -0.376 | 42.8 | 4.7 | 140 | 33 | 4.25
2538 | Shell Solar | SQ 140-PC | Shell Solar : SQ 140-PC | -0.376 | 42.8 | 4.7 | 140 | 33 | 4.25
2539 | Shell Solar | SQ 150-PC | Shell Solar : SQ 150-PC | -0.371 | 43.4 | 4.8 | 150 | 34 | 4.4
2540 | Shell Solar | SQ 160-PC | Shell Solar : SQ 160-PC | -0.37 | 43.5 | 4.9 | 160 | 35 | 4.58
2541 | Shell Solar | SQ 70 | Shell Solar : SQ 70 | -0.379 | 21.4 | 4.7 | 70 | 16.5 | 4.25
2542 | Shell Solar | SQ 75 | Shell Solar : SQ 75 | -0.373 | 21.7 | 4.8 | 75 | 17 | 4.4
2543 | Shell Solar | SQ 80 | Shell Solar : SQ 80 | -0.371 | 21.8 | 4.85 | 80 | 17.5 | 4.58
2544 | Shell Solar | ST10 | Shell Solar : ST10 | -0.476 | 22.9 | 0.77 | 10 | 15.6 | 0.64
2545 | Shell Solar | ST20 | Shell Solar : ST20 | -0.476 | 22.9 | 1.54 | 20 | 15.6 | 1.29
2546 | Shell Solar | ST36 | Shell Solar : ST36 | -0.45 | 22.9 | 2.68 | 36 | 15.8 | 2.28
2547 | Shell Solar | ST40 | Shell Solar : ST40 | -0.45 | 23.3 | 2.68 | 40 | 16.6 | 2.41
2548 | Shell Solar | ST5 | Shell Solar : ST5 | -0.476 | 22.9 | 0.39 | 5 | 15.6 | 0.32
2549 | SHUNDA | SDM-170/X-72M 150Wp | SHUNDA : SDM-170/X-72M 150Wp | -0.355 | 44 | 4.69 | 150 | 34.6 | 4.34
2550 | SHUNDA | SDM-170/X-72M 155Wp | SHUNDA : SDM-170/X-72M 155Wp | -0.355 | 44 | 4.84 | 155 | 34.6 | 4.48
2551 | SHUNDA | SDM-170/X-72M 160Wp | SHUNDA : SDM-170/X-72M 160Wp | -0.355 | 44 | 5 | 160 | 34.6 | 4.62
2552 | SHUNDA | SDM-170/X-72M 165Wp | SHUNDA : SDM-170/X-72M 165Wp | -0.355 | 44 | 5.16 | 165 | 34.6 | 4.77
2553 | SHUNDA | SDM-170/X-72M 170Wp | SHUNDA : SDM-170/X-72M 170Wp | -0.355 | 44 | 5.31 | 170 | 34.6 | 4.92
2554 | SHUNDA | SDM-170/X-72M 175Wp | SHUNDA : SDM-170/X-72M 175Wp | -0.355 | 44 | 5.47 | 175 | 34.6 | 5.06
2555 | SHUNDA | SDM-170/X-72M 180Wp | SHUNDA : SDM-170/X-72M 180Wp | -0.355 | 44 | 5.64 | 180 | 34.6 | 5.2
2556 | SHUNDA | SDM-170/X-72M 185Wp | SHUNDA : SDM-170/X-72M 185Wp | -0.355 | 44 | 5.8 | 185 | 34.6 | 5.35
2557 | Siemens | M55 53Wp | Siemens : M55 53Wp | -0.38 | 21.7 | 3.35 | 53 | 17.4 | 3.05
2558 | SIG Solar Gmbh | 150Wp mono | SIG Solar Gmbh : 150Wp mono | -0.305 | 43.2 | 5.1 | 150 | 34.2 | 4.39
2559 | SIG Solar Gmbh | 160Wp mono | SIG Solar Gmbh : 160Wp mono | -0.305 | 43.4 | 5.19 | 160 | 34.8 | 4.63
2560 | SIG Solar Gmbh | Sunearth Mono 150Wp | SIG Solar Gmbh : Sunearth Mono 150Wp | -0.35 | 43.4 | 4.86 | 150 | 35.2 | 4.26
2561 | SIG Solar Gmbh | Sunearth Mono 155Wp | SIG Solar Gmbh : Sunearth Mono 155Wp | -0.35 | 43.6 | 4.93 | 155 | 35.4 | 4.38
2562 | SIG Solar Gmbh | Sunearth Mono 160Wp | SIG Solar Gmbh : Sunearth Mono 160Wp | -0.35 | 43.8 | 5 | 160 | 35.6 | 4.5
2563 | SIG Solar Gmbh | Sunearth Mono 165Wp | SIG Solar Gmbh : Sunearth Mono 165Wp | -0.35 | 44 | 5.07 | 165 | 35.8 | 4.61
2564 | SIG Solar Gmbh | Sunearth Mono 170Wp | SIG Solar Gmbh : Sunearth Mono 170Wp | -0.35 | 44.2 | 5.14 | 170 | 36 | 4.72
2565 | SIG Solar Gmbh | Sunearth Mono 175Wp | SIG Solar Gmbh : Sunearth Mono 175Wp | -0.35 | 44.4 | 5.21 | 175 | 36.2 | 4.84
2566 | SIG Solar Gmbh | Sunearth Mono 180Wp | SIG Solar Gmbh : Sunearth Mono 180Wp | -0.35 | 44.6 | 5.28 | 180 | 36.4 | 4.95
2567 | SIG Solar Gmbh | Sunearth Mono 200Wp | SIG Solar Gmbh : Sunearth Mono 200Wp | -0.35 | 57.8 | 4.87 | 200 | 45.8 | 4.37
2568 | SIG Solar Gmbh | Sunearth Mono 210Wp | SIG Solar Gmbh : Sunearth Mono 210Wp | -0.35 | 58.3 | 4.96 | 210 | 47.4 | 4.43
2569 | SIG Solar Gmbh | Sunearth Mono 220Wp | SIG Solar Gmbh : Sunearth Mono 220Wp | -0.35 | 58.7 | 5.07 | 220 | 47.8 | 4.61
2570 | SIG Solar Gmbh | Sunearth Mono 230Wp | SIG Solar Gmbh : Sunearth Mono 230Wp | -0.35 | 59.1 | 5.17 | 230 | 48.2 | 4.77
2571 | SIG Solar Gmbh | Sunearth Mono 240Wp | SIG Solar Gmbh : Sunearth Mono 240Wp | -0.35 | 59.5 | 5.28 | 240 | 48.6 | 4.95
2572 | SIG Solar Gmbh | Sunearth Poly 150Wp | SIG Solar Gmbh : Sunearth Poly 150Wp | -0.35 | 43.3 | 4.9 | 150 | 35.1 | 4.28
2573 | SIG Solar Gmbh | Sunearth Poly 155Wp | SIG Solar Gmbh : Sunearth Poly 155Wp | -0.35 | 43.5 | 4.97 | 155 | 35.3 | 4.39
2574 | SIG Solar Gmbh | Sunearth Poly 160Wp | SIG Solar Gmbh : Sunearth Poly 160Wp | -0.35 | 43.7 | 5.03 | 160 | 35.5 | 4.51
2575 | SIG Solar Gmbh | Sunearth Poly 165Wp | SIG Solar Gmbh : Sunearth Poly 165Wp | -0.35 | 43.9 | 5.1 | 165 | 35.7 | 4.63
2576 | SIG Solar Gmbh | Sunearth Poly 170Wp | SIG Solar Gmbh : Sunearth Poly 170Wp | -0.35 | 44.1 | 5.17 | 170 | 35.9 | 4.74
2577 | SIG Solar Gmbh | Sunearth Poly 175Wp | SIG Solar Gmbh : Sunearth Poly 175Wp | -0.35 | 44.3 | 5.24 | 175 | 36.1 | 4.85
2578 | SIG Solar Gmbh | Sunearth Poly 180Wp | SIG Solar Gmbh : Sunearth Poly 180Wp | -0.35 | 44.5 | 5.31 | 180 | 36.3 | 4.96
2579 | SIG Solar Gmbh | Sunearth Poly 210Wp | SIG Solar Gmbh : Sunearth Poly 210Wp | -0.35 | 58.2 | 5 | 210 | 47.2 | 4.45
2580 | SIG Solar Gmbh | Sunearth Poly 220Wp | SIG Solar Gmbh : Sunearth Poly 220Wp | -0.35 | 58.6 | 5.1 | 220 | 47.6 | 4.63
2581 | SIG Solar Gmbh | Sunearth Poly 230Wp | SIG Solar Gmbh : Sunearth Poly 230Wp | -0.35 | 59 | 5.2 | 230 | 48 | 4.8
2582 | SIG Solar Gmbh | Sunearth Poly 240Wp | SIG Solar Gmbh : Sunearth Poly 240Wp | -0.35 | 59.4 | 5.31 | 240 | 48.4 | 4.96
2583 | SIG Solar Gmbh | Sunearth Poly 285Wp | SIG Solar Gmbh : Sunearth Poly 285Wp | -0.35 | 44.1 | 8.51 | 285 | 35.1 | 8.12
2584 | Sig Solar Gmbh | Sunearth-Mono-TDB 170W | Sig Solar Gmbh : Sunearth-Mono-TDB 170W | -0.35 | 44 | 5.36 | 170 | 35 | 4.86
2585 | Sig Solar Gmbh | Sunearth-Mono-TDB 175W | Sig Solar Gmbh : Sunearth-Mono-TDB 175W | -0.35 | 44 | 5.48 | 175 | 35.2 | 4.96
2586 | Sig Solar Gmbh | Sunearth-Mono-TDB 180W | Sig Solar Gmbh : Sunearth-Mono-TDB 180W | -0.35 | 44.2 | 5.53 | 180 | 35.4 | 5.08
2587 | Sig Solar Gmbh | Sunearth-Poly-TPB 170W | Sig Solar Gmbh : Sunearth-Poly-TPB 170W | -0.35 | 43.6 | 5.17 | 170 | 35.2 | 4.83
2588 | Sig Solar Gmbh | Sunearth-Poly-TPB 175W | Sig Solar Gmbh : Sunearth-Poly-TPB 175W | -0.35 | 43.8 | 5.26 | 175 | 35.4 | 4.95
2589 | Sig Solar Gmbh | Sunearth-Poly-TPB 180W | Sig Solar Gmbh : Sunearth-Poly-TPB 180W | -0.35 | 44 | 5.34 | 180 | 35.6 | 5.06
2590 | Sig Solar Gmbh | Sunearth-Poly-TPB 220W | Sig Solar Gmbh : Sunearth-Poly-TPB 220W | -0.35 | 58.2 | 5.18 | 220 | 46.4 | 4.74
2591 | Signet Solar | SI-S1-X-Ax-344 | Signet Solar : SI-S1-X-Ax-344 | -0.3 | 186.4 | 2.96 | 344 | 144.6 | 2.38
2592 | Signet Solar | SI-S1-X-Ax-360 | Signet Solar : SI-S1-X-Ax-360 | -0.3 | 187.6 | 3 | 360 | 146.4 | 2.46
2593 | Signet Solar | SI-S1-X-Ax-380 | Signet Solar : SI-S1-X-Ax-380 | -0.3 | 189.1 | 3.05 | 380 | 148.7 | 2.53
2594 | Signet Solar | SI-S1-X-Ax-400 | Signet Solar : SI-S1-X-Ax-400 | -0.3 | 190.6 | 3.1 | 400 | 151 | 2.63
2595 | Signet Solar | SI-S2-X-Ax-172 | Signet Solar : SI-S2-X-Ax-172 | -0.3 | 186.4 | 1.48 | 172 | 144.6 | 1.19
2596 | Signet Solar | SI-S2-X-Ax-180 | Signet Solar : SI-S2-X-Ax-180 | -0.3 | 187.6 | 1.5 | 180 | 146.4 | 1.23
2597 | Signet Solar | SI-S2-X-Ax-190 | Signet Solar : SI-S2-X-Ax-190 | -0.3 | 189.1 | 1.54 | 190 | 148.4 | 1.23
2598 | Signet Solar | SI-S2-X-Ax-200 | Signet Solar : SI-S2-X-Ax-200 | -0.3 | 190.6 | 1.58 | 200 | 150.4 | 1.33
2599 | Signet Solar | SI-S3-X-Ax-172 | Signet Solar : SI-S3-X-Ax-172 | -0.3 | 93.2 | 2.96 | 172 | 72.3 | 2.38
2600 | Signet Solar | SI-S3-X-Ax-180 | Signet Solar : SI-S3-X-Ax-180 | -0.3 | 93.8 | 3 | 180 | 73.2 | 2.46
2601 | Signet Solar | SI-S3-X-Ax-190 | Signet Solar : SI-S3-X-Ax-190 | -0.3 | 94.5 | 3.08 | 190 | 74.2 | 2.56
2602 | Signet Solar | SI-S3-X-Ax-200 | Signet Solar : SI-S3-X-Ax-200 | -0.3 | 95 | 3.16 | 200 | 75.2 | 2.66
2603 | Signet Solar | SI-S4-X-Ax-100 | Signet Solar : SI-S4-X-Ax-100 | -0.3 | 95.5 | 1.58 | 100 | 75.2 | 1.33
2604 | Signet Solar | SI-S4-X-Ax-86 | Signet Solar : SI-S4-X-Ax-86 | -0.3 | 93.2 | 1.48 | 86 | 72.2 | 1.18
2605 | Signet Solar | SI-S4-X-Ax-90 | Signet Solar : SI-S4-X-Ax-90 | -0.3 | 94.5 | 1.5 | 90 | 73.2 | 1.23
2606 | Signet Solar | SI-S4-X-Ax-95 | Signet Solar : SI-S4-X-Ax-95 | -0.3 | 95 | 1.54 | 95 | 74.2 | 1.28
2607 | SILIKEN | SLK36P4-50Wp-12V | SILIKEN : SLK36P4-50Wp-12V | -0.37 | 21.4 | 3.2 | 50 | 17.7 | 2.82
2608 | SILIKEN | SLK36P5-80Wp-12V | SILIKEN : SLK36P5-80Wp-12V | -0.332 | 21.7 | 4.82 | 80 | 18 | 4.45
2609 | SILIKEN | SLK36P5-85Wp-12V | SILIKEN : SLK36P5-85Wp-12V | -0.329 | 21.9 | 4.98 | 85 | 18.2 | 4.67
2610 | SILIKEN | SLK36P6L 126Wp | SILIKEN : SLK36P6L 126Wp | -0.345 | 22.1 | 7.6 | 126 | 17.8 | 7.08
2611 | SILIKEN | SLK36P6L 130Wp | SILIKEN : SLK36P6L 130Wp | -0.344 | 22.2 | 7.8 | 130 | 17.9 | 7.26
2612 | SILIKEN | SLK36P6L 133Wp | SILIKEN : SLK36P6L 133Wp | -0.342 | 22.3 | 7.92 | 133 | 18 | 7.39
2613 | SILIKEN | SLK36P6L-130Wp-12V | SILIKEN : SLK36P6L-130Wp-12V | -0.342 | 22.3 | 7.83 | 130 | 17.8 | 7.46
2614 | SILIKEN | SLK60M6L 223Wp | SILIKEN : SLK60M6L 223Wp | -0.344 | 36.9 | 8.04 | 223 | 29.9 | 7.47
2615 | SILIKEN | SLK60M6L 225Wp | SILIKEN : SLK60M6L 225Wp | -0.343 | 37.1 | 8.08 | 225 | 30 | 7.5
2616 | SILIKEN | SLK60M6L 228Wp | SILIKEN : SLK60M6L 228Wp | -0.343 | 37.1 | 8.14 | 228 | 30.1 | 7.57
2617 | SILIKEN | SLK60M6L 230Wp | SILIKEN : SLK60M6L 230Wp | -0.342 | 37.2 | 8.24 | 230 | 30.2 | 7.62
2618 | SILIKEN | SLK60M6L 232Wp | SILIKEN : SLK60M6L 232Wp | -0.342 | 37.2 | 8.29 | 232 | 30.3 | 7.66
2619 | SILIKEN | SLK60P6L | SILIKEN : SLK60P6L | -0.34 | 37 | 7.8 | 215 | 30.3 | 7.1
2620 | SILIKEN | SLK60P6L 209Wp | SILIKEN : SLK60P6L 209Wp | -0.349 | 36.4 | 7.61 | 209 | 29.5 | 7.08
2621 | SILIKEN | SLK60P6L 212Wp | SILIKEN : SLK60P6L 212Wp | -0.348 | 36.5 | 7.71 | 212 | 29.5 | 7.19
2622 | SILIKEN | SLK60P6L 215Wp | SILIKEN : SLK60P6L 215Wp | -0.348 | 36.6 | 7.8 | 215 | 29.6 | 7.26
2623 | SILIKEN | SLK60P6L 218Wp | SILIKEN : SLK60P6L 218Wp | -0.347 | 36.7 | 7.88 | 218 | 29.6 | 7.36
2624 | SILIKEN | SLK60P6L 221Wp | SILIKEN : SLK60P6L 221Wp | -0.346 | 36.8 | 7.94 | 221 | 29.7 | 7.44
2625 | SILIKEN | SLK60P6L 224Wp | SILIKEN : SLK60P6L 224Wp | -0.345 | 36.9 | 8.04 | 224 | 29.8 | 7.52
2626 | SILIKEN | SLK60P6L 227Wp | SILIKEN : SLK60P6L 227Wp | -0.344 | 37 | 8.16 | 227 | 29.8 | 7.62
2627 | SILIKEN | SLK60P6L 230Wp | SILIKEN : SLK60P6L 230Wp | -0.343 | 37.1 | 8.24 | 230 | 29.9 | 7.8
2628 | SILIKEN | SLK60P6L 233Wp | SILIKEN : SLK60P6L 233Wp | -0.342 | 37.2 | 8.34 | 233 | 29.9 | 7.8
2629 | SILIKEN | SLK66P5-150Wp-33V | SILIKEN : SLK66P5-150Wp-33V | -0.325 | 40.6 | 4.79 | 150 | 33.2 | 4.52
2630 | SILIKEN | SLK72M5-176Wp-24V | SILIKEN : SLK72M5-176Wp-24V | -0.357 | 44.4 | 5.48 | 176 | 36.6 | 4.81
2631 | SILIKEN | SLK72M5-180Wp-24V | SILIKEN : SLK72M5-180Wp-24V | -0.357 | 44.4 | 5.48 | 180 | 36.8 | 4.49
2632 | SILIKEN | SLK72M5-184Wp-24V | SILIKEN : SLK72M5-184Wp-24V | -0.356 | 44.5 | 5.49 | 184 | 36.9 | 4.99
2633 | SILIKEN | SLK72P4-100Wp-24V | SILIKEN : SLK72P4-100Wp-24V | -0.377 | 42 | 3.15 | 100 | 35.1 | 2.85
2634 | SILIKEN | SLK72P5-160Wp-24V | SILIKEN : SLK72P5-160Wp-24V | -0.33 | 43.6 | 4.79 | 160 | 36.2 | 4.42
2635 | SILIKEN | SLK72P5-165Wp-24V | SILIKEN : SLK72P5-165Wp-24V | -0.328 | 43.9 | 4.84 | 165 | 36.4 | 4.53
2636 | SILIKEN | SLK72P5-170Wp-24V | SILIKEN : SLK72P5-170Wp-24V | -0.325 | 44.3 | 4.86 | 170 | 36.6 | 4.64
2637 | SILIKEN | SLK80P5-185Wp-40Vmpp | SILIKEN : SLK80P5-185Wp-40Vmpp | -0.324 | 49.3 | 4.83 | 185 | 40.4 | 4.58
2638 | SILLIA energie | SeT225P-40 205Wp | SILLIA energie : SeT225P-40 205Wp | -0.363 | 35.82 | 7.58 | 205 | 30.14 | 6.8
2639 | SILLIA energie | SeT225P-40 215Wp | SILLIA energie : SeT225P-40 215Wp | -0.361 | 36.06 | 7.71 | 215 | 30.2 | 7.11
2640 | SILLIA energie | SeT225P-40 225Wp | SILLIA energie : SeT225P-40 225Wp | -0.357 | 36.48 | 7.88 | 225 | 30.2 | 7.45
2641 | SILLIA energie | SeT225P-40 235Wp | SILLIA energie : SeT225P-40 235Wp | -0.355 | 36.72 | 8.03 | 235 | 30.7 | 7.65
2642 | SILLIA energie | SeT225P-40 245Wp | SILLIA energie : SeT225P-40 245Wp | -0.355 | 36.72 | 8.23 | 245 | 31.2 | 7.84
2643 | SILLIA energie | SeT2xxp-40 200Wp | SILLIA energie : SeT2xxp-40 200Wp | -0.4 | 35.3 | 7.8 | 200 | 28.8 | 6.95
2644 | SILLIA energie | SeT2xxp-40 210Wp | SILLIA energie : SeT2xxp-40 210Wp | -0.4 | 35.5 | 7.9 | 210 | 28.95 | 7.25
2645 | SILLIA energie | SeT2xxp-40 215Wp | SILLIA energie : SeT2xxp-40 215Wp | -0.4 | 35.7 | 8 | 215 | 28.97 | 7.4
2646 | SILLIA energie | SeT2xxp-40 225Wp | SILLIA energie : SeT2xxp-40 225Wp | -0.4 | 36.1 | 8.2 | 225 | 29 | 7.75
2647 | SILLIA energie | SeT2xxp-40 235Wp | SILLIA energie : SeT2xxp-40 235Wp | -0.4 | 36.35 | 8.35 | 235 | 29.8 | 7.95
2648 | Sinepower | SP120-72A | Sinepower : SP120-72A | -0.37 | 44.28 | 3.5 | 120 | 36.72 | 3.33
2649 | Sinepower | SP160-72B | Sinepower : SP160-72B | -0.37 | 43.2 | 4.93 | 160 | 35.7 | 4.49
2650 | Sinepower | SP180-72A | Sinepower : SP180-72A | -0.25 | 44.35 | 5.35 | 180 | 36.96 | 4.87
2651 | Sinepower | SP200-54A | Sinepower : SP200-54A | -0.25 | 32.4 | 8.1 | 200 | 27 | 7.43
2652 | Sinepower | SP200-54B | Sinepower : SP200-54B | -0.25 | 32.4 | 8.14 | 200 | 27 | 7.41
2653 | Sinodeu | 160-16P | Sinodeu : 160-16P | -0.37 | 28.7 | 7.98 | 160 | 22.5 | 7.12
2654 | Sinodeu | 165-16P | Sinodeu : 165-16P | -0.37 | 28.8 | 8.05 | 165 | 22.8 | 7.25
2655 | Sinodeu | 165-25M | Sinodeu : 165-25M | -0.37 | 44.2 | 5.21 | 165 | 35 | 4.72
2656 | Sinodeu | 170-16P | Sinodeu : 170-16P | -0.37 | 28.9 | 8.13 | 170 | 23 | 7.4
2657 | Sinodeu | 170-25M | Sinodeu : 170-25M | -0.37 | 44.4 | 5.29 | 170 | 35.2 | 4.83
2658 | Sinodeu | 175-16P | Sinodeu : 175-16P | -0.37 | 29 | 8.26 | 175 | 23.2 | 7.55
2659 | Sinodeu | 175-25M | Sinodeu : 175-25M | -0.37 | 44.5 | 5.34 | 175 | 35.3 | 4.96
2660 | Sinodeu | 180-16P | Sinodeu : 180-16P | -0.37 | 29.2 | 8.43 | 180 | 23.4 | 7.7
2661 | Sinodeu | 180-18P | Sinodeu : 180-18P | -0.37 | 32.2 | 7.98 | 180 | 25.3 | 7.11
2662 | Sinodeu | 180-25M | Sinodeu : 180-25M | -0.37 | 44.6 | 5.4 | 180 | 35.4 | 5.09
2663 | Sinodeu | 185-16P | Sinodeu : 185-16P | -0.37 | 29.4 | 8.57 | 185 | 23.6 | 7.85
2664 | Sinodeu | 185-18P | Sinodeu : 185-18P | -0.37 | 32.4 | 8.02 | 185 | 25.7 | 7.2
2665 | Sinodeu | 185-25M | Sinodeu : 185-25M | -0.37 | 44.8 | 5.48 | 185 | 35.8 | 5.17
2666 | Sinodeu | 190-18P | Sinodeu : 190-18P | -0.37 | 32.5 | 8.12 | 190 | 25.8 | 7.36
2667 | Sinodeu | 190-25M | Sinodeu : 190-25M | -0.37 | 45 | 5.5 | 190 | 36.2 | 5.25
2668 | Sinodeu | 195-18P | Sinodeu : 195-18P | -0.37 | 32,6 | 8.21 | 195 | 26 | 7.5
2669 | Sinodeu | 200-18P | Sinodeu : 200-18P | -0.37 | 32.8 | 8.36 | 200 | 26.2 | 7.63
2670 | Sinodeu | 205-18P | Sinodeu : 205-18P | -0.37 | 33 | 8.48 | 205 | 26.4 | 7.77
2671 | Sinodeu | 205-20P | Sinodeu : 205-20P | -0.37 | 35.9 | 8.05 | 205 | 28.4 | 7.22
2672 | Sinodeu | 210-18P | Sinodeu : 210-18P | -0.37 | 33.2 | 8.54 | 210 | 26.7 | 7.87
2673 | Sinodeu | 210-20P | Sinodeu : 210-20P | -0.37 | 36.1 | 8.11 | 210 | 28.5 | 7.37
2674 | Sinodeu | 215-20P | Sinodeu : 215-20P | -0.37 | 36.3 | 8.18 | 215 | 28.8 | 7.47
2675 | Sinodeu | 220-20P | Sinodeu : 220-20P | -0.37 | 36.4 | 8.32 | 220 | 29 | 7.59
2676 | Sinodeu | 225-20M | Sinodeu : 225-20M | -0.37 | 36.7 | 8.36 | 225 | 29.3 | 7.68
2677 | Sinodeu | 225-20P | Sinodeu : 225-20P | -0.37 | 36.6 | 8.46 | 225 | 29.2 | 7.71
2678 | Sinodeu | 230-20M | Sinodeu : 230-20M | -0.37 | 36.8 | 8.45 | 230 | 29.5 | 7.8
2679 | Sinodeu | 230-20P | Sinodeu : 230-20P | -0.37 | 36.7 | 8.54 | 230 | 29.4 | 7.83
2680 | Sinodeu | 235-20M | Sinodeu : 235-20M | -0.37 | 36.8 | 8.54 | 235 | 29.6 | 7.94
2681 | Sinodeu | 240-20M | Sinodeu : 240-20M | -0.37 | 37 | 8.62 | 240 | 29.8 | 8.06
2682 | Sinodeu | 245-20M | Sinodeu : 245-20M | -0.37 | 37.2 | 8.69 | 245 | 30 | 8.17
2683 | Sinodeu | 250-20M | Sinodeu : 250-20M | -0.37 | 37.3 | 8.78 | 250 | 30.1 | 8.31
2684 | Sinodeu | 275-24M | Sinodeu : 275-24M | -0.37 | 44.1 | 8.46 | 275 | 35.3 | 7.8
2685 | Sinodeu | 280-24M | Sinodeu : 280-24M | -0.37 | 44.2 | 8.53 | 280 | 35.5 | 7.89
2686 | Sinodeu | 285-24M | Sinodeu : 285-24M | -0.37 | 44.4 | 8.59 | 285 | 35.7 | 7.99
2687 | Sinodeu | 290-24M | Sinodeu : 290-24M | -0.37 | 44.5 | 8.68 | 290 | 35.8 | 8.11
2688 | Sinodeu | 295-24M | Sinodeu : 295-24M | -0.37 | 44.6 | 8.73 | 295 | 35.9 | 8.22
2689 | Sinodeu | 300-24M | Sinodeu : 300-24M | -0.37 | 44.8 | 8.8 | 300 | 36.1 | 8.32
2690 | Sinonar | PVS 50-12F | Sinonar : PVS 50-12F | -0.4 | 25 | 3.4 | 50 | 17 | 3
2691 | Sinosol | CS170 | Sinosol : CS170 | -0.37 | 44.1 | 5.2 | 170 | 35.5 | 4.79
2692 | Sinosol | CS175 | Sinosol : CS175 | -0.37 | 44.3 | 5.3 | 175 | 35.8 | 4.89
2693 | Sinosol | CS180 | Sinosol : CS180 | -0.37 | 44.5 | 5.4 | 180 | 36.1 | 4.99
2694 | Sinosol | CS185 | Sinosol : CS185 | -0.37 | 44.7 | 5.5 | 185 | 36.4 | 5.09
2695 | Sinosol | CS190 | Sinosol : CS190 | -0.37 | 44.9 | 5.6 | 190 | 36.6 | 5.18
2696 | Solaire | SD410 140Wp | Solaire : SD410 140Wp | -0.35 | 22.6 | 7.8 | 140 | 18.8 | 7.45
2697 | Solaire | SD410 145Wp | Solaire : SD410 145Wp | -0.35 | 23 | 7.9 | 145 | 19.2 | 7.55
2698 | Solaire | SD410 150Wp | Solaire : SD410 150Wp | -0.35 | 23.5 | 8 | 150 | 19.6 | 7.65
2699 | Solaire | SD410 155Wp | Solaire : SD410 155Wp | -0.35 | 23.9 | 8.2 | 155 | 19.9 | 7.8
2700 | Solaire | SD410 160Wp | Solaire : SD410 160Wp | -0.35 | 24.4 | 8.3 | 160 | 20.3 | 7.9
2701 | Solaire | SD410 165Wp | Solaire : SD410 165Wp | -0.35 | 24.8 | 8.43 | 165 | 20.7 | 8.02
2702 | Solaire | SD510 185Wp | Solaire : SD510 185Wp | -0.35 | 30.3 | 8.4 | 185 | 23.7 | 7.8
2703 | Solaire | SD510 190Wp | Solaire : SD510 190Wp | -0.35 | 30.6 | 8.55 | 190 | 23.9 | 7.95
2704 | Solaire | SD510 195Wp | Solaire : SD510 195Wp | -0.35 | 30.8 | 8.65 | 195 | 24.1 | 8.1
2705 | Solaire | SD510 200Wp | Solaire : SD510 200Wp | -0.35 | 31.1 | 8.8 | 200 | 24.3 | 8.25
2706 | Solaire | SD510 205Wp | Solaire : SD510 205Wp | -0.35 | 31.4 | 9 | 205 | 24.4 | 8.4
2707 | Solaire | SD610 225Wp | Solaire : SD610 225Wp | -0.35 | 36.6 | 8.4 | 225 | 28.9 | 7.82
2708 | Solaire | SD610 230Wp | Solaire : SD610 230Wp | -0.35 | 36.7 | 8.55 | 230 | 29.3 | 7.95
2709 | Solaire | SD610 235Wp | Solaire : SD610 235Wp | -0.35 | 36.9 | 8.65 | 235 | 29.4 | 8.04
2710 | Solaire | SD610 240Wp | Solaire : SD610 240Wp | -0.35 | 37.03 | 8.78 | 240 | 29.7 | 8.16
2711 | Solaire | SD610 245Wp | Solaire : SD610 245Wp | -0.35 | 37.18 | 8.91 | 245 | 29.95 | 8.27
2712 | Solaire | SD610 250Wp | Solaire : SD610 250Wp | -0.35 | 37.33 | 9.03 | 250 | 30.2 | 8.38
2713 | Solar Cells | SM 106 | Solar Cells : SM 106 | -0.4 | 22.5 | 0.17 | 2 | 14.5 | 0.14
2714 | Solar Cells | SM 112 | Solar Cells : SM 112 | -0.4 | 22.5 | 0.33 | 4 | 14.5 | 0.28
2715 | Solar Cells | SM 118 | Solar Cells : SM 118 | -0.4 | 22.5 | 0.49 | 6 | 14.5 | 0.41
2716 | Solar Cells | SM 136 | Solar Cells : SM 136 | -0.4 | 22.5 | 1 | 12 | 14.5 | 0.83
2717 | Solar Enertech | SE-140M | Solar Enertech : SE-140M | -0.37 | 42.7 | 4.65 | 140 | 34.2 | 4.09
2718 | Solar Enertech | SE-145M | Solar Enertech : SE-145M | -0.37 | 42.9 | 4.74 | 145 | 34.4 | 4.22
2719 | Solar Enertech | SE-150M | Solar Enertech : SE-150M | -0.37 | 43.2 | 4.83 | 150 | 34.6 | 4.34
2720 | Solar Enertech | SE-155M | Solar Enertech : SE-155M | -0.37 | 43.4 | 4.91 | 155 | 34.8 | 4.45
2721 | Solar Enertech | SE-160M | Solar Enertech : SE-160M | -0.37 | 43.7 | 4.99 | 160 | 35.1 | 4.56
2722 | Solar Enertech | SE-165M | Solar Enertech : SE-165M | -0.37 | 44.1 | 5.08 | 165 | 35.3 | 4.67
2723 | Solar Enertech | SE-170M | Solar Enertech : SE-170M | -0.37 | 44.3 | 5.15 | 170 | 35.5 | 4.79
2724 | Solar Enertech | SE-175M | Solar Enertech : SE-175M | -0.37 | 44.5 | 5.21 | 175 | 35.7 | 4.9
2725 | Solar Enertech | SE-180M | Solar Enertech : SE-180M | -0.37 | 44.7 | 5.3 | 180 | 35.9 | 5.01
2726 | Solar for People | SfP 152 | Solar for People : SfP 152 | -0.37 | 43.2 | 4.99 | 145 | 34.8 | 4.38
2727 | SOLAR Integrated | SI-G2 512 | SOLAR Integrated : SI-G2 512 | -0.38 | 190 | 4.8 | 512 | 132 | 3.88
2728 | SOLAR Integrated | SI-G2 544 | SOLAR Integrated : SI-G2 544 | -0.38 | 185 | 5.1 | 544 | 132 | 4.13
2729 | SOLAR Integrated | SI-G2 576 | SOLAR Integrated : SI-G2 576 | -0.38 | 185 | 5.3 | 576 | 132 | 4.37
2730 | SOLAR Integrated | SI-M2 288 | SOLAR Integrated : SI-M2 288 | -0.38 | 92.4 | 5.3 | 288 | 66 | 4.37
2731 | SOLAR Integrated | SI-T2- 544 D | SOLAR Integrated : SI-T2- 544 D | -0.38 | 185 | 5.1 | 544 | 132 | 4.13
2732 | SOLAR Integrated | SI-T2- 576 D | SOLAR Integrated : SI-T2- 576 D | -0.38 | 185 | 5.3 | 576 | 132 | 4.37
2733 | Solar Mittermeier | TSM-175D | Solar Mittermeier : TSM-175D | -0.34 | 44.2 | 5.25 | 175 | 35.8 | 4.89
2734 | Solar Modules Nederland | TC220-MU | Solar Modules Nederland : TC220-MU | -0.36 | 36.3 | 8.3 | 220 | 28.4 | 7.8
2735 | Solar Modules Nederland | TC225-MU | Solar Modules Nederland : TC225-MU | -0.36 | 36.4 | 8.35 | 225 | 28.6 | 7.9
2736 | Solar Modules Nederland | TC230-MU | Solar Modules Nederland : TC230-MU | -0.36 | 36.6 | 8.4 | 230 | 28.8 | 8
2737 | Solar Modules Nederland | TC235-MU | Solar Modules Nederland : TC235-MU | -0.36 | 36.8 | 8.5 | 235 | 29.1 | 8.1
2738 | Solar Modules Nederland | TC240-MU | Solar Modules Nederland : TC240-MU | -0.36 | 37 | 8.6 | 240 | 29.4 | 8.2
2739 | Solar Nord | N-12-50 | Solar Nord : N-12-50 | -0.4 | 20.8 | 3.2 | 50 | 16.5 | 3
2740 | Solar Nord | N-12-70 | Solar Nord : N-12-70 | -0.4 | 20.2 | 4.6 | 70 | 16.2 | 4.3
2741 | Solar World | SW220 Mono | Solar World : SW220 Mono | -0.33 | 36.6 | 8.18 | 220 | 29.3 | 7.51
2742 | Solar World | SW220 Poly | Solar World : SW220 Poly | -0.34 | 36.6 | 8.08 | 220 | 29.2 | 7.54
2743 | Solar World | SW225 Mono | Solar World : SW225 Mono | -0.33 | 36.8 | 8.3 | 225 | 29.5 | 7.64
2744 | Solar World | SW225 Poly | Solar World : SW225 Poly | -0.34 | 36.8 | 8.17 | 225 | 29.5 | 7.63
2745 | Solar World | SW230 Mono | Solar World : SW230 Mono | -0.33 | 36.9 | 8.42 | 230 | 29.6 | 7.76
2746 | Solar World | SW230 Poly | Solar World : SW230 Poly | -0.34 | 36.9 | 8.25 | 230 | 29.8 | 7.72
2747 | Solar World | SW235 Mono | Solar World : SW235 Mono | -0.33 | 37 | 8.54 | 235 | 29.8 | 7.89
2748 | Solar World | SW235 Poly | Solar World : SW235 Poly | -0.34 | 37 | 8.35 | 235 | 30 | 7.85
2749 | Solar World | SW240 Mono | Solar World : SW240 Mono | -0.33 | 37.1 | 8.66 | 240 | 30 | 8.02
2750 | Solar World | SW245 Mono | Solar World : SW245 Mono | -0.33 | 37.3 | 8.78 | 245 | 30.1 | 8.14
2751 | Solara AG | S 800 TI / 130Wp | Solara AG : S 800 TI / 130Wp | -0.355 | 41.75 | 4.12 | 130 | 34.2 | 3.8
2752 | Solara AG | S 810 TI / 140Wp | Solara AG : S 810 TI / 140Wp | -0.355 | 42.6 | 4.01 | 140 | 34.9 | 4.58
2753 | Solara AG | S 820 TI / 146Wp | Solara AG : S 820 TI / 146Wp | -0.33 | 42.48 | 4.56 | 146 | 35.21 | 4.15
2754 | Solara AG | S 830 TI / 156Wp | Solara AG : S 830 TI / 156Wp | -0.33 | 42.8 | 4.65 | 156 | 35.79 | 4.36
2755 | Solara AG | S 836 TI / 140Wp | Solara AG : S 836 TI / 140Wp | -0.33 | 29.3 | 6.5 | 140 | 23.7 | 5.91
2756 | Solara AG | S 840 TI / 166Wp | Solara AG : S 840 TI / 166Wp | -0.33 | 43.56 | 4.9 | 166 | 36.5 | 4.55
2757 | Solara AG | S 845 TI -6L / 145Wp Q6L | Solara AG : S 845 TI -6L / 145Wp Q6L | -0.32 | 30.2 | 6.67 | 145 | 23.6 | 6.15
2758 | Solara AG | S 846 TI / 150Wp | Solara AG : S 846 TI / 150Wp | -0.36 | 29.5 | 6.95 | 150 | 23.9 | 6.28
2759 | Solara AG | S 850 TI (1) / 160Wp | Solara AG : S 850 TI (1) / 160Wp | -0.39 | 43.2 | 4.9 | 160 | 35.2 | 4.54
2760 | Solara AG | S 850 TI / 150Wp | Solara AG : S 850 TI / 150Wp | -0.38 | 42.5 | 4.68 | 150 | 35.6 | 4.23
2761 | Solara AG | S 851 TI / 151Wp Q6L | Solara AG : S 851 TI / 151Wp Q6L | -0.32 | 29.6 | 7 | 151 | 24 | 6.3
2762 | Solara AG | S 855 TI / 155Wp | Solara AG : S 855 TI / 155Wp | -0.38 | 43 | 4.75 | 155 | 35.8 | 4.34
2763 | Solara AG | S 855 TI / 160Wp / 24V | Solara AG : S 855 TI / 160Wp / 24V | -0.38 | 43.2 | 4.85 | 160 | 35.9 | 4.46
2764 | Solara AG | S 856 TI / 160Wp | Solara AG : S 856 TI / 160Wp | -0.358 | 29.65 | 7 | 160 | 24 | 6.67
2765 | Solara AG | S 860 TI / 170Wp | Solara AG : S 860 TI / 170Wp | -0.33 | 43.6 | 4.9 | 170 | 37.3 | 4.56
2766 | Solara AG | S 861 TI / 161Wp Q6L | Solara AG : S 861 TI / 161Wp Q6L | -0.32 | 29.7 | 7.35 | 161 | 24.4 | 6.6
2767 | Solara AG | S 865 TI / 165Wp Q6L | Solara AG : S 865 TI / 165Wp Q6L | -0.32 | 29.7 | 7.35 | 165 | 24.6 | 6.71
2768 | Solara AG | S 866 TI / 166Wp | Solara AG : S 866 TI / 166Wp | -0.355 | 29.85 | 7.2 | 166 | 25 | 6.64
2769 | Solara AG | S 870 TI / 170Wp Q6L | Solara AG : S 870 TI / 170Wp Q6L | -0.35 | 29.82 | 7.45 | 170 | 24.7 | 6.88
2770 | Solara AG | S 875 TI / 175Wp Q6L | Solara AG : S 875 TI / 175Wp Q6L | -0.355 | 29.85 | 7.65 | 175 | 24.8 | 7.06
2771 | Solara AG | S 875 TI M / 175Wp | Solara AG : S 875 TI M / 175Wp | -0.38 | 44.42 | 5.48 | 175 | 36.5 | 4.8
2772 | Solara AG | S 880 TI / 180 Wp Q6L | Solara AG : S 880 TI / 180 Wp Q6L | -0.354 | 29.95 | 7.73 | 180 | 24.9 | 7.23
2773 | Solara AG | S 880 TI M / 180Wp | Solara AG : S 880 TI M / 180Wp | -0.38 | 44.75 | 5.58 | 180 | 36.5 | 4.93
2774 | Solara AG | S 885 TI / 185Wp Q6L | Solara AG : S 885 TI / 185Wp Q6L | -0.32 | 30.5 | 7.83 | 185 | 24.9 | 7.43
2775 | Solara AG | S 885 TI M / 185Wp | Solara AG : S 885 TI M / 185Wp | -0.38 | 44.8 | 5.7 | 185 | 36.5 | 5.07
2776 | Solara AG | S 890 TI M / 190Wp | Solara AG : S 890 TI M / 190Wp | -0.38 | 44.85 | 5.8 | 190 | 36.5 | 5.2
2777 | Solara AG | SM1000/95 | Solara AG : SM1000/95 | -0.362 | 43.2 | 2.9 | 95 | 34 | 2.8
2778 | Solara AG | SM1000CZ | Solara AG : SM1000CZ | -0.25 | 21.7 | 6.48 | 100 | 17.3 | 5.78
2779 | Solara AG | SM120DZ | Solara AG : SM120DZ | -0.217 | 4.8 | 2.76 | 10.5 | 3.8 | 2.7
2780 | Solara AG | SM2000/12 | Solara AG : SM2000/12 | -0.217 | 21.5 | 6 | 100 | 17.2 | 5.9
2781 | Solara AG | SM2000/24 | Solara AG : SM2000/24 | -0.217 | 43 | 3 | 100 | 34.4 | 2.95
2782 | Solara AG | SM3000/12 | Solara AG : SM3000/12 | -0.217 | 21.5 | 6.3 | 106 | 17.2 | 6.1
2783 | Solara AG | SM3000/24 | Solara AG : SM3000/24 | -0.217 | 43 | 3.15 | 106 | 34.4 | 3.05
2784 | Solara AG | SM300S | Solara AG : SM300S | -0.217 | 21.5 | 4.75 | 75 | 17.2 | 4.45
2785 | Solara AG | SM320S | Solara AG : SM320S | -0.217 | 21.9 | 5 | 80 | 17.3 | 4.6
2786 | Solara AG | SM5000 | Solara AG : SM5000 | -0.33 | 32.3 | 5.46 | 125 | 26 | 4.8
2787 | Solara AG | SM640DS | Solara AG : SM640DS | -0.31 | 23.8 | 4.8 | 64 | 16.5 | 3.88
2788 | Solara AG | SM7000 | Solara AG : SM7000 | -0.37 | 28.4 | 7.82 | 160 | 22.8 | 7.02
2789 | Solara AG | SM7001 | Solara AG : SM7001 | -0.36 | 43.1 | 5.46 | 165 | 34.6 | 4.77
2790 | Solara AG | SM7002 | Solara AG : SM7002 | -0.35 | 44.4 | 5.4 | 175 | 35.4 | 4.95
2791 | Solara AG | SM900CZ | Solara AG : SM900CZ | -0.217 | 21 | 6 | 90 | 16.7 | 5.39
2792 | Solara AG | SM950CZ | Solara AG : SM950CZ | -0.25 | 21.4 | 6.28 | 95 | 17 | 5.59
2793 | Solarc | CSM 36.610 | Solarc : CSM 36.610 | -0.4 | 20.5 | 0.39 | 6 | 17.3 | 0.36
2794 | Solarc | CSM 8,050 | Solarc : CSM 8,050 | -0.383 | 4.7 | 0.135 | 0.48 | 3.9 | 0.123
2795 | Solarc | CSM 8,150 | Solarc : CSM 8,150 | -0.4 | 4.7 | 0.41 | 1.5 | 3.9 | 0.39
2796 | Solarc | CSM 8,600 | Solarc : CSM 8,600 | -0.326 | 4.6 | 1.65 | 6 | 3.8 | 1.55
2797 | Solarc | CSM 9,040 | Solarc : CSM 9,040 | -0.377 | 5.3 | 0.11 | 0.42 | 4.4 | 0.096
2798 | Solarc | CSM 9,1400 | Solarc : CSM 9,1400 | -0.283 | 5.3 | 3.35 | 14 | 4.4 | 3.2
2799 | SolarCompany | SC-L 125 | SolarCompany : SC-L 125 | -0.33 | 22 | 7.6 | 125 | 17.4 | 7.15
2800 | SolarCompany | SC-L 130 | SolarCompany : SC-L 130 | -0.33 | 22.15 | 7.8 | 130 | 17.7 | 7.31
2801 | SolarCompany | SC-L 135 | SolarCompany : SC-L 135 | -0.33 | 22.3 | 7.9 | 135 | 18 | 7.48
2802 | Solarday | PX60-210 | Solarday : PX60-210 | -0.337 | 37.1 | 7.87 | 210 | 28.3 | 7.42
2803 | Solarday | PX60-220 | Solarday : PX60-220 | -0.337 | 37.1 | 8.29 | 220 | 28.5 | 7.72
2804 | Solarday | PX60-230 | Solarday : PX60-230 | -0.337 | 37.7 | 8.54 | 230 | 29 | 7.93
2805 | Solarday | PX60-HT 200 | Solarday : PX60-HT 200 | -0.334 | 37.4 | 7.5 | 200 | 29 | 6.9
2806 | Solarday | PX60-HT 210 | Solarday : PX60-HT 210 | -0.334 | 37.1 | 7.87 | 210 | 28.3 | 7.42
2807 | Solarday | PX60-HT 220 | Solarday : PX60-HT 220 | -0.334 | 37.1 | 8.29 | 220 | 28.5 | 7.72
2808 | Solar-Fabrik | SF 100/2 100Wp | Solar-Fabrik : SF 100/2 100Wp | -0.335 | 28.6 | 4.9 | 100 | 22.8 | 4.4
2809 | Solar-Fabrik | SF 100/3 | Solar-Fabrik : SF 100/3 | -0.335 | 29.2 | 4.88 | 102 | 23.2 | 4.4
2810 | Solar-Fabrik | SF 115 | Solar-Fabrik : SF 115 | -0.397 | 20.9 | 7.6 | 115 | 16.8 | 6.9
2811 | Solar-Fabrik | SF 120 - 115Wp | Solar-Fabrik : SF 120 - 115Wp | -0.35 | 22 | 7.2 | 115 | 17.3 | 6.65
2812 | Solar-Fabrik | SF 125-120 | Solar-Fabrik : SF 125-120 | -0.347 | 21.9 | 7.5 | 120 | 17.2 | 6.98
2813 | Solar-Fabrik | SF 125-125 | Solar-Fabrik : SF 125-125 | -0.35 | 22 | 7.7 | 125 | 17.35 | 7.2
2814 | Solar-Fabrik | SF 125-130 | Solar-Fabrik : SF 125-130 | -0.34 | 22.25 | 7.9 | 130 | 17.5 | 7.43
2815 | Solar-Fabrik | SF 130/2-125 | Solar-Fabrik : SF 130/2-125 | -0.334 | 21.53 | 7.84 | 125 | 17.5 | 7.14
2816 | Solar-Fabrik | SF 130/2-130 | Solar-Fabrik : SF 130/2-130 | -0.332 | 21.69 | 7.96 | 130 | 17.71 | 7.34
2817 | Solar-Fabrik | SF 130/2-135 | Solar-Fabrik : SF 130/2-135 | -0.329 | 21.86 | 8.08 | 135 | 17.94 | 7.52
2818 | Solar-Fabrik | SF 145 A 145Wp | Solar-Fabrik : SF 145 A 145Wp | -0.34 | 42.2 | 4.69 | 145 | 34.1 | 4.24
2819 | Solar-Fabrik | SF 150/10A-155 | Solar-Fabrik : SF 150/10A-155 | -0.355 | 43.5 | 4.97 | 155 | 35 | 4.43
2820 | Solar-Fabrik | SF 150/10A-160 | Solar-Fabrik : SF 150/10A-160 | -0.35 | 43.9 | 5.02 | 160 | 35.5 | 4.51
2821 | Solar-Fabrik | SF 150/10A-165 | Solar-Fabrik : SF 150/10A-165 | -0.348 | 44.3 | 5.07 | 165 | 36 | 4.59
2822 | Solar-Fabrik | SF 150/10A-170 | Solar-Fabrik : SF 150/10A-170 | -0.345 | 44.7 | 5.12 | 170 | 36.5 | 4.67
2823 | Solar-Fabrik | SF 150/2A-146 | Solar-Fabrik : SF 150/2A-146 | -0.353 | 36.9 | 5 | 146 | 32.4 | 4.5
2824 | Solar-Fabrik | SF 150/2A-150 | Solar-Fabrik : SF 150/2A-150 | -0.351 | 40.2 | 5.1 | 150 | 32.6 | 4.6
2825 | Solar-Fabrik | SF 150/2A-154 | Solar-Fabrik : SF 150/2A-154 | -0.348 | 40.5 | 5.21 | 154 | 32.8 | 4.69
2826 | Solar-Fabrik | SF 150H (185W) | Solar-Fabrik : SF 150H (185W) | -0.34 | 45 | 5.4 | 185 | 36 | 5.14
2827 | Solar-Fabrik | SF 150H (190W) | Solar-Fabrik : SF 150H (190W) | -0.34 | 44.2 | 5.65 | 190 | 36.5 | 5.21
2828 | Solar-Fabrik | SF 150H (195W) | Solar-Fabrik : SF 150H (195W) | -0.34 | 45.28 | 5.58 | 195 | 35.94 | 5.28
2829 | Solar-Fabrik | SF 165A-155 | Solar-Fabrik : SF 165A-155 | -0.341 | 43.4 | 4.75 | 155 | 37.2 | 4.17
2830 | Solar-Fabrik | SF 165A-165 | Solar-Fabrik : SF 165A-165 | -0.339 | 43.6 | 4.95 | 165 | 37.3 | 4.42
2831 | Solar-Fabrik | SF 170 | Solar-Fabrik : SF 170 | -0.4 | 30.8 | 7.6 | 170 | 25 | 6.8
2832 | Solar-Fabrik | SF 200A-200 | Solar-Fabrik : SF 200A-200 | -0.343 | 35 | 7.77 | 200 | 27.6 | 7.27
2833 | Solar-Fabrik | SF 200A-210 | Solar-Fabrik : SF 200A-210 | -0.335 | 35.8 | 7.96 | 210 | 27.9 | 7.48
2834 | Solar-Fabrik | SF 200A-220 | Solar-Fabrik : SF 200A-220 | -0.33 | 36.4 | 8.15 | 220 | 28.6 | 7.7
2835 | Solar-Fabrik | SF 340 | Solar-Fabrik : SF 340 | -0.4 | 61.5 | 7.6 | 340 | 50 | 6.8
2836 | Solar-Fabrik | SF 52 A | Solar-Fabrik : SF 52 A | -0.428 | 21.5 | 3.3 | 52 | 16.7 | 3.1
2837 | Solar-Fabrik | SF 75 | Solar-Fabrik : SF 75 | -0.395 | 21 | 4.8 | 75 | 17 | 4.4
2838 | Solar-Fabrik | SF 75A | Solar-Fabrik : SF 75A | -0.395 | 21 | 4.8 | 75 | 17 | 4.4
2839 | Solar-Fabrik | Premium L poly 215W | Solar-Fabrik : Premium L poly 215W | -0.33 | 36 | 8.1 | 215 | 28.3 | 7.6
2840 | Solar-Fabrik | Premium L poly 220W | Solar-Fabrik : Premium L poly 220W | -0.33 | 36.4 | 8.15 | 220 | 28.6 | 7.7
2841 | Solar-Fabrik | Premium L poly 225W | Solar-Fabrik : Premium L poly 225W | -0.33 | 36.9 | 8.3 | 225 | 29.1 | 7.75
2842 | Solar-Fabrik | Premium L poly 230W | Solar-Fabrik : Premium L poly 230W | -0.33 | 37.4 | 8.4 | 230 | 29.6 | 7.8
2843 | Solar-Fabrik | Premium L poly 235W | Solar-Fabrik : Premium L poly 235W | -0.33 | 37.4 | 8.5 | 235 | 29.7 | 7.94
2844 | Solarfun | SF160m 5'' 150Wp | Solarfun : SF160m 5'' 150Wp | -0.37 | 43.4 | 4.88 | 150 | 34.8 | 4.31
2845 | Solarfun | SF160m 5'' 155Wp | Solarfun : SF160m 5'' 155Wp | -0.37 | 43.5 | 4.9 | 155 | 35.4 | 4.38
2846 | Solarfun | SF160m 5'' 160Wp | Solarfun : SF160m 5'' 160Wp | -0.37 | 43.5 | 5 | 160 | 35.6 | 4.5
2847 | Solarfun | SF160m 5'' 165Wp | Solarfun : SF160m 5'' 165Wp | -0.37 | 44 | 5.1 | 165 | 35.8 | 4.61
2848 | Solarfun | SF160m 5'' 170Wp | Solarfun : SF160m 5'' 170Wp | -0.37 | 44.5 | 5.12 | 170 | 35.9 | 4.74
2849 | Solarfun | SF160m 5'' 175Wp | Solarfun : SF160m 5'' 175Wp | -0.37 | 44.8 | 5.17 | 175 | 36 | 4.86
2850 | Solarfun | SF160m 5'' 180Wp | Solarfun : SF160m 5'' 180Wp | -0.37 | 45 | 5.2 | 180 | 36 | 5
2851 | Solarfun | SF190m 6'' 170Wp | Solarfun : SF190m 6'' 170Wp | -0.37 | 32.4 | 7.49 | 170 | 26.1 | 6.51
2852 | Solarfun | SF190m 6'' 175Wp | Solarfun : SF190m 6'' 175Wp | -0.37 | 32.5 | 7.69 | 175 | 26.2 | 6.68
2853 | Solarfun | SF190m 6'' 180Wp | Solarfun : SF190m 6'' 180Wp | -0.37 | 32.6 | 7.78 | 180 | 26.3 | 6.84
2854 | Solarfun | SF190m 6'' 185Wp | Solarfun : SF190m 6'' 185Wp | -0.37 | 32.7 | 7.86 | 185 | 26.4 | 7
2855 | Solarfun | SF190m 6'' 190Wp | Solarfun : SF190m 6'' 190Wp | -0.37 | 32.8 | 7.93 | 190 | 26.5 | 7.17
2856 | Solarfun | SF190m 6'' 195Wp | Solarfun : SF190m 6'' 195Wp | -0.37 | 32.9 | 8.12 | 195 | 26.6 | 7.33
2857 | Solarfun | SF190m 6'' 200Wp | Solarfun : SF190m 6'' 200Wp | -0.37 | 33 | 8.19 | 200 | 26.7 | 7.49
2858 | Solarfun | SF190p 6'' 170Wp | Solarfun : SF190p 6'' 170Wp | -0.37 | 32.2 | 7.54 | 170 | 26.3 | 6.47
2859 | Solarfun | SF190p 6'' 175Wp | Solarfun : SF190p 6'' 175Wp | -0.37 | 32.3 | 7.64 | 175 | 26.4 | 6.63
2860 | Solarfun | SF190p 6'' 180Wp | Solarfun : SF190p 6'' 180Wp | -0.37 | 32.4 | 7.72 | 180 | 26.5 | 6.8
2861 | Solarfun | SF190p 6'' 185Wp | Solarfun : SF190p 6'' 185Wp | -0.37 | 32.5 | 7.8 | 185 | 26.6 | 6.96
2862 | Solarfun | SF190p 6'' 190Wp | Solarfun : SF190p 6'' 190Wp | -0.37 | 32.6 | 7.98 | 190 | 26.7 | 7.12
2863 | Solarfun | SF190p 6'' 195Wp | Solarfun : SF190p 6'' 195Wp | -0.37 | 32.7 | 8.06 | 195 | 26.8 | 7.28
2864 | Solarfun | SF190p 6'' 200Wp | Solarfun : SF190p 6'' 200Wp | -0.37 | 32.8 | 8.24 | 200 | 26.9 | 7.44
2865 | Solaris | M 05-300 | Solaris : M 05-300 | -0.316 | 0.57 | 0.33 | 0.139 | 0.46 | 0.31
2866 | Solaris | M 05-600 | Solaris : M 05-600 | -0.316 | 0.57 | 0.66 | 0.279 | 0.46 | 0.61
2867 | Solaris | M 15-300 | Solaris : M 15-300 | -0.314 | 1.72 | 0.33 | 0.417 | 1.37 | 0.31
2868 | Solaris | M 25-150 | Solaris : M 25-150 | -0.321 | 2.87 | 0.17 | 0.35 | 2.29 | 0.15
2869 | Solaris | M 25-300 | Solaris : M 25-300 | -0.317 | 2.87 | 0.33 | 0.695 | 2.29 | 0.31
2870 | Solaris | M 3-600 | Solaris : M 3-600 | -0.32 | 3.44 | 0.66 | 1.674 | 2.74 | 0.61
2871 | Solaris | M 5-300 | Solaris : M 5-300 | -0.314 | 5.73 | 0.33 | 1.39 | 4.57 | 0.31
2872 | Solaris | S 36 KL | Solaris : S 36 KL | -0.365 | 20.3 | 1.8 | 25 | 16 | 1.5
2873 | Solaris | S 56 KL | Solaris : S 56 KL | -0.365 | 20.3 | 3.3 | 50 | 16 | 3.1
2874 | Solaris | S 68 GT | Solaris : S 68 GT | -0.294 | 21.4 | 3.3 | 50 | 16.5 | 3.1
2875 | SolarModules NL | TC230-MO | SolarModules NL : TC230-MO | -0.34 | 36.3 | 8.3 | 230 | 28.9 | 8
2876 | SolarModules NL | TC235-MO | SolarModules NL : TC235-MO | -0.34 | 36.4 | 8.5 | 235 | 28.9 | 8.2
2877 | SolarModules NL | TC240-MO | SolarModules NL : TC240-MO | -0.34 | 36.6 | 8.6 | 240 | 29 | 8.3
2878 | SolarModules NL | TC245-MO | SolarModules NL : TC245-MO | -0.34 | 36.8 | 8.8 | 245 | 29.2 | 8.4
2879 | SolarModules NL | TC250-MO | SolarModules NL : TC250-MO | -0.34 | 37 | 8.8 | 250 | 29.4 | 8.5
2880 | SolarModules NL | TC255-MO | SolarModules NL : TC255-MO | -0.34 | 37.2 | 8.9 | 255 | 29.6 | 8.6
2881 | Solarnova | SOL 100 D-L | Solarnova : SOL 100 D-L | -0.4 | 41.4 | 3.2 | 100 | 34 | 2.94
2882 | Solarnova | SOL 55 D | Solarnova : SOL 55 D | -0.4 | 23 | 3.2 | 55 | 19.1 | 2.9
2883 | Solarnova | SOL 55 K | Solarnova : SOL 55 K | -0.4 | 23 | 3.2 | 55 | 19.1 | 2.9
2884 | Solarnova | SOL 96 AC | Solarnova : SOL 96 AC | -0.4 | 41.4 | 3.1 | 96 | 34 | 2.8
2885 | Solarnova | SOL 96 D-L | Solarnova : SOL 96 D-L | -0.4 | 41.4 | 3.1 | 96 | 34 | 2.8
2886 | Solarnova® | SOL 100 AC | Solarnova® : SOL 100 AC | -0.4 | 41.4 | 3.2 | 100 | 34.2 | 2.92
2887 | Solarnova® | SOL 100 K-L | Solarnova® : SOL 100 K-L | -0.4 | 43.2 | 3.2 | 100 | 34.2 | 2.98
2888 | Solarnova® | SOL 12 K | Solarnova® : SOL 12 K | -0.4 | 29.9 | 0.72 | 12 | 17.5 | 0.65
2889 | Solarnova® | SOL 24 K | Solarnova® : SOL 24 K | -0.4 | 23.1 | 1.43 | 24 | 18.5 | 1.3
2890 | Solarnova® | SOL 48 D | Solarnova® : SOL 48 D | -0.4 | 20.7 | 3.1 | 48 | 17 | 2.8
2891 | Solarnova® | SOL 48 K | Solarnova® : SOL 48 K | -0.4 | 20.7 | 3.1 | 48 | 17 | 2.8
2892 | Solarnova® | SOL 50 D | Solarnova® : SOL 50 D | -0.4 | 20.7 | 3.2 | 50 | 17.1 | 2.9
2893 | Solarnova® | SOL 50 K | Solarnova® : SOL 50 K | -0.4 | 20.7 | 3.2 | 50 | 17.2 | 2.94
2894 | Solarnova® | SOL 53 D | Solarnova® : SOL 53 D | -0.4 | 23 | 3.1 | 53 | 19.1 | 2.8
2895 | Solarnova® | SOL 53 K | Solarnova® : SOL 53 K | -0.4 | 23 | 3.1 | 53 | 19.1 | 2.8
2896 | Solarnova® | SOL 56 D | Solarnova® : SOL 56 D | -0.4 | 23 | 3.2 | 56 | 19.1 | 2.92
2897 | Solarnova® | SOL 96 K-L | Solarnova® : SOL 96 K-L | -0.4 | 41.4 | 3.1 | 96 | 34 | 2.8
2898 | SolarPark | SPP 220 | SolarPark : SPP 220 | -0.35 | 36.5 | 8.09 | 220 | 29.2 | 7.55
2899 | SolarPark | SPP 225 | SolarPark : SPP 225 | -0.35 | 36.8 | 8.17 | 225 | 29.6 | 7.62
2900 | SolarPark | SPP 230 | SolarPark : SPP 230 | -0.35 | 36.9 | 8.26 | 230 | 29.8 | 7.73
2901 | SolarPark | SPP 235 | SolarPark : SPP 235 | -0.35 | 37 | 8.35 | 235 | 30.1 | 7.84
2902 | SolarPark | SPP 240 | SolarPark : SPP 240 | -0.35 | 37.2 | 8.44 | 240 | 30.3 | 7.93
2903 | Solartec | SG36-054 | Solartec : SG36-054 | -0.358 | 21.5 | 3.49 | 54 | 17.1 | 3.14
2904 | Solartec | SG36-056 | Solartec : SG36-056 | -0.363 | 21.5 | 3.52 | 56 | 17.4 | 3.21
2905 | Solartec | SG36-058 | Solartec : SG36-058 | -0.366 | 21.6 | 3.55 | 58 | 17.6 | 3.27
2906 | Solartec | SG72-108 | Solartec : SG72-108 | -0.358 | 21.5 | 6.98 | 108 | 17.1 | 6.29
2907 | Solartec | SG72-112 | Solartec : SG72-112 | -0.363 | 21.5 | 7.04 | 112 | 17.4 | 6.41
2908 | Solartec | SG72-116 | Solartec : SG72-116 | -0.366 | 21.6 | 7.1 | 116 | 17.6 | 6.53
2909 | Solartec | SG72-118 | Solartec : SG72-118 | -0.37 | 21.6 | 7.18 | 118 | 17.7 | 6.65
2910 | Solartec | SSW36-54 (Radix36-054) | Solartec : SSW36-54 (Radix36-054) | -0.358 | 21.5 | 3.49 | 54 | 17.1 | 3.14
2911 | Solartec | SSW36-56 (Radix36-056) | Solartec : SSW36-56 (Radix36-056) | -0.363 | 21.5 | 3.52 | 56 | 17.4 | 3.21
2912 | Solartec | SSW36-58 (Radix36-058) | Solartec : SSW36-58 (Radix36-058) | -0.366 | 21.6 | 3.55 | 58 | 17.6 | 3.27
2913 | Solartec | SSW72-08 (Radix72-108) | Solartec : SSW72-08 (Radix72-108) | -0.358 | 21.5 | 7.98 | 108 | 17.1 | 6.29
2914 | Solartec | SSW72-12 (Radix72-112) | Solartec : SSW72-12 (Radix72-112) | -0.363 | 21.5 | 7.04 | 112 | 17.4 | 6.41
2915 | Solartec | SSW72-16 (Radix72-116) | Solartec : SSW72-16 (Radix72-116) | -0.366 | 21.6 | 7.1 | 116 | 17.6 | 6.53
2916 | Solartec | SSW72-18 (Radix72-118) | Solartec : SSW72-18 (Radix72-118) | -0.37 | 21.6 | 7.18 | 118 | 17.7 | 6.65
2917 | Solarwatt | A10-15 GET AK | Solarwatt : A10-15 GET AK | -0.331 | 24.5 | 0.75 | 10.3 | 18 | 0.57
2918 | Solarwatt | A10-30 GET AK | Solarwatt : A10-30 GET AK | -0.331 | 49 | 0.37 | 10 | 36 | 0.28
2919 | Solarwatt | A15-30 GET AK | Solarwatt : A15-30 GET AK | -0.331 | 49 | 0.56 | 15.3 | 36 | 0.44
2920 | Solarwatt | A5-15 GET AK | Solarwatt : A5-15 GET AK | -0.331 | 24.5 | 0.37 | 5 | 18 | 0.24
2921 | Solarwatt | E25-36 GET AK Laminat | Solarwatt : E25-36 GET AK Laminat | -0.362 | 21 | 1.63 | 25.56 | 17.3 | 1.5
2922 | Solarwatt | E25-36 GET AK Rahmen | Solarwatt : E25-36 GET AK Rahmen | -0.36 | 21.1 | 1.63 | 25.56 | 17.3 | 1.5
2923 | Solarwatt | E51-36 GET AK | Solarwatt : E51-36 GET AK | -0.36 | 21.1 | 3.25 | 51.12 | 17.3 | 3
2924 | Solarwatt | E51-36 TEA LK | Solarwatt : E51-36 TEA LK | -0.36 | 21.1 | 3.25 | 51.12 | 17.3 | 3
2925 | Solarwatt | EP 100-48GET LK | Solarwatt : EP 100-48GET LK | -0.33 | 29.2 | 4.92 | 105 | 24 | 4.38
2926 | Solarwatt | EP 100-72 GEG LK, 100 W | Solarwatt : EP 100-72 GEG LK, 100 W | -0.33 | 42.6 | 3.2 | 100 | 34.6 | 2.9
2927 | Solarwatt | EP 100-72 GEG LK, 105 W | Solarwatt : EP 100-72 GEG LK, 105 W | -0.33 | 43.9 | 3.28 | 105 | 36 | 2.92
2928 | Solarwatt | EP 100-72 GEG LK, 110 W | Solarwatt : EP 100-72 GEG LK, 110 W | -0.33 | 44.1 | 3.31 | 110 | 36 | 3.06
2929 | Solarwatt | EP 115-54 GET AK | Solarwatt : EP 115-54 GET AK | -0.328 | 32.6 | 4.88 | 115 | 27 | 4.26
2930 | Solarwatt | EP 14-36 GET AK | Solarwatt : EP 14-36 GET AK | -0.661 | 22 | 0.82 | 14 | 18 | 0.76
2931 | Solarwatt | EP 28-36 GET AK | Solarwatt : EP 28-36 GET AK | -0.661 | 22 | 1.65 | 28 | 18 | 1.53
2932 | Solarwatt | EP 55-36 GET AK | Solarwatt : EP 55-36 GET AK | -0.661 | 22 | 3.31 | 55 | 18 | 3.06
2933 | Solarwatt | M 120-72 GET LK 112 W | Solarwatt : M 120-72 GET LK 112 W | -0.404 | 43.9 | 3.36 | 112 | 36.3 | 3.08
2934 | Solarwatt | M1,3-17 PRK EK | Solarwatt : M1,3-17 PRK EK | -0.402 | 10.2 | 0.19 | 1.3 | 8.4 | 0.16
2935 | Solarwatt | M110-32 GEG-opak LK 110Wp | Solarwatt : M110-32 GEG-opak LK 110Wp | -0.47 | 19.6 | 7.45 | 110 | 16 | 6.88
2936 | Solarwatt | M115-50 GEG-opak LK 115Wp | Solarwatt : M115-50 GEG-opak LK 115Wp | -0.47 | 31 | 5 | 115 | 24.8 | 4.67
2937 | Solarwatt | M120-72 GEG LK, 110 W | Solarwatt : M120-72 GEG LK, 110 W | -0.404 | 43.9 | 3.36 | 112 | 36.3 | 3.08
2938 | Solarwatt | M120-72 GEG LK, 115 W | Solarwatt : M120-72 GEG LK, 115 W | -0.405 | 43.9 | 3.46 | 115 | 36.3 | 3.17
2939 | Solarwatt | M120-72 GEG LK, 120 W | Solarwatt : M120-72 GEG LK, 120 W | -0.406 | 44 | 3.51 | 120 | 36.4 | 3.29
2940 | Solarwatt | M135-55 GEG LK 125Wp | Solarwatt : M135-55 GEG LK 125Wp | -0.47 | 33.7 | 5.02 | 125 | 27.3 | 4.63
2941 | Solarwatt | M135-55 GEG LK 130Wp | Solarwatt : M135-55 GEG LK 130Wp | -0.47 | 33.7 | 5.28 | 130 | 27.4 | 4.81
2942 | Solarwatt | M135-55 GEG LK 135Wp | Solarwatt : M135-55 GEG LK 135Wp | -0.47 | 33.8 | 5.49 | 135 | 27.5 | 5.01
2943 | Solarwatt | M15-36 GET AK | Solarwatt : M15-36 GET AK | -0.4 | 22 | 0.95 | 15 | 17.1 | 0.87
2944 | Solarwatt | M15-36 TEA LK | Solarwatt : M15-36 TEA LK | -0.4 | 22 | 0.95 | 15 | 17.1 | 0.87
2945 | Solarwatt | M180-48 GET AK 175Wp | Solarwatt : M180-48 GET AK 175Wp | -0.47 | 28.9 | 8.22 | 175 | 23 | 7.71
2946 | Solarwatt | M180-48 GET AK 180Wp | Solarwatt : M180-48 GET AK 180Wp | -0.47 | 29 | 8.27 | 180 | 23.3 | 7.78
2947 | Solarwatt | M180-48 GET AK 185Wp | Solarwatt : M180-48 GET AK 185Wp | -0.47 | 29.1 | 8.35 | 185 | 23.4 | 7.89
2948 | Solarwatt | M180-48 GET AK 190Wp | Solarwatt : M180-48 GET AK 190Wp | -0.47 | 29.3 | 8.55 | 190 | 23.7 | 8.05
2949 | Solarwatt | M180-48 GET AK 195Wp | Solarwatt : M180-48 GET AK 195Wp | -0.47 | 29.6 | 8.62 | 195 | 23.9 | 8.17
2950 | Solarwatt | M2,6-34 PRK EK | Solarwatt : M2,6-34 PRK EK | -0.402 | 20.4 | 0.19 | 2.6 | 16.8 | 0.16
2951 | Solarwatt | M220-60 GET AK 210Wp | Solarwatt : M220-60 GET AK 210Wp | -0.47 | 35.37 | 7.99 | 210 | 28.2 | 7.45
2952 | Solarwatt | M220-60 GET AK 215Wp | Solarwatt : M220-60 GET AK 215Wp | -0.47 | 35.9 | 8.12 | 215 | 28.4 | 7.58
2953 | Solarwatt | M220-60 GET AK 220Wp | Solarwatt : M220-60 GET AK 220Wp | -0.47 | 36 | 8.25 | 220 | 28.6 | 7.71
2954 | Solarwatt | M220-60 GET AK 225Wp | Solarwatt : M220-60 GET AK 225Wp | -0.47 | 36.1 | 8.32 | 225 | 28.8 | 7.82
2955 | Solarwatt | M220-60 GET AK 230Wp | Solarwatt : M220-60 GET AK 230Wp | -0.47 | 36.3 | 8.48 | 230 | 29.1 | 7.92
2956 | Solarwatt | M220-60 GET AK 235Wp | Solarwatt : M220-60 GET AK 235Wp | -0.47 | 36.5 | 9.62 | 235 | 29.3 | 8.03
2957 | Solarwatt | M220-60 GET AK 240Wp | Solarwatt : M220-60 GET AK 240Wp | -0.47 | 36.7 | 8.76 | 240 | 29.5 | 8.15
2958 | Solarwatt | M230-96 GET AK 215Wp | Solarwatt : M230-96 GET AK 215Wp | -0.47 | 58.3 | 5.07 | 215 | 47 | 4.58
2959 | Solarwatt | M230-96 GET AK 220Wp | Solarwatt : M230-96 GET AK 220Wp | -0.47 | 58.5 | 5.13 | 220 | 47.4 | 4.65
2960 | Solarwatt | M230-96 GET AK 225Wp | Solarwatt : M230-96 GET AK 225Wp | -0.47 | 58.7 | 5.21 | 225 | 47.6 | 4.74
2961 | Solarwatt | M230-96 GET AK 230Wp | Solarwatt : M230-96 GET AK 230Wp | -0.47 | 58.9 | 5.28 | 230 | 47.7 | 4.83
2962 | Solarwatt | M230-96 GET AK 235Wp | Solarwatt : M230-96 GET AK 235Wp | -0.47 | 59.1 | 5.4 | 235 | 47.8 | 4.92
2963 | Solarwatt | M230-96 GET AK 240Wp | Solarwatt : M230-96 GET AK 240Wp | -0.47 | 59.2 | 5.5 | 240 | 48 | 5.01
2964 | Solarwatt | M230-96 GET AK 245Wp | Solarwatt : M230-96 GET AK 245Wp | -0.47 | 59.3 | 5.6 | 245 | 48.1 | 5.1
2965 | Solarwatt | M230-96 GET AK 250Wp | Solarwatt : M230-96 GET AK 250Wp | -0.47 | 59.4 | 5.65 | 250 | 48.3 | 5.18
2966 | Solarwatt | M30-18 GEG K | Solarwatt : M30-18 GEG K | -0.359 | 11 | 3.46 | 28 | 9.07 | 3.17
2967 | Solarwatt | M30-36 GET AK Laminat | Solarwatt : M30-36 GET AK Laminat | -0.401 | 22.2 | 1.88 | 30 | 18 | 1.68
2968 | Solarwatt | M30-36 GET AK Rahmen | Solarwatt : M30-36 GET AK Rahmen | -0.4 | 22 | 1.9 | 30 | 17.1 | 1.75
2969 | Solarwatt | M30-36 TEA LK | Solarwatt : M30-36 TEA LK | -0.398 | 22.1 | 1.9 | 30 | 17.1 | 1.75
2970 | Solarwatt | M60-36 GET AK | Solarwatt : M60-36 GET AK | -0.4 | 22 | 3.81 | 60 | 17.1 | 3.51
2971 | Solarwatt | M60-36 TEA LK | Solarwatt : M60-36 TEA LK | -0.4 | 22 | 3.81 | 60 | 17.1 | 3.51
2972 | Solarwatt | M96-50 GEG LK 96Wp | Solarwatt : M96-50 GEG LK 96Wp | -0.47 | 29.6 | 4.43 | 96 | 24.5 | 3.9
2973 | Solarwatt | P 100-72 GEG LK 100 W | Solarwatt : P 100-72 GEG LK 100 W | -0.36 | 42.6 | 3.2 | 100 | 34.6 | 2.92
2974 | Solarwatt | P 100-72 GEG LK 105 W | Solarwatt : P 100-72 GEG LK 105 W | -0.36 | 43.9 | 3.28 | 105 | 36 | 2.92
2975 | Solarwatt | P 100-72 GET AK 100 W | Solarwatt : P 100-72 GET AK 100 W | -0.36 | 42.6 | 3.2 | 100 | 34.6 | 2.9
2976 | Solarwatt | P 100-72 GET AK 105 W | Solarwatt : P 100-72 GET AK 105 W | -0.36 | 43.9 | 3.28 | 105 | 36 | 2.92
2977 | Solarwatt | P 100-72 GET LK 100 W | Solarwatt : P 100-72 GET LK 100 W | -0.36 | 42.6 | 3.2 | 100 | 34.6 | 2.9
2978 | Solarwatt | P 100-72 GET LK 105 W | Solarwatt : P 100-72 GET LK 105 W | -0.36 | 43.9 | 3.28 | 105 | 36 | 2.92
2979 | Solarwatt | P11-36 GET AK Laminat | Solarwatt : P11-36 GET AK Laminat | -0.402 | 21.4 | 0.77 | 11.88 | 16.8 | 0.71
2980 | Solarwatt | P11-36 GET AK Rahmen | Solarwatt : P11-36 GET AK Rahmen | -0.402 | 21.4 | 0.77 | 11.88 | 16.8 | 0.71
2981 | Solarwatt | P160-72 GET AK 160W | Solarwatt : P160-72 GET AK 160W | -0.39 | 43.2 | 5 | 160 | 34.9 | 4.6
2982 | Solarwatt | P160-72 GET AK 165Wp | Solarwatt : P160-72 GET AK 165Wp | -0.39 | 43.3 | 5.1 | 165 | 35.4 | 4.7
2983 | Solarwatt | P160-72 GET AK 170Wp | Solarwatt : P160-72 GET AK 170Wp | -0.39 | 43.7 | 5.1 | 170 | 35.7 | 4.8
2984 | Solarwatt | P210-30 GET AK 225Wp | Solarwatt : P210-30 GET AK 225Wp | -0.35 | 36.7 | 8.42 | 225 | 28.6 | 7.87
2985 | Solarwatt | P210-30 GET AK 230Wp | Solarwatt : P210-30 GET AK 230Wp | -0.35 | 36.9 | 8.5 | 230 | 29.4 | 8
2986 | Solarwatt | P210-60 GET AK 185Wp | Solarwatt : P210-60 GET AK 185Wp | -0.32 | 36.4 | 8.03 | 185 | 27.7 | 6.68
2987 | Solarwatt | P210-60 GET AK 190Wp | Solarwatt : P210-60 GET AK 190Wp | -0.32 | 36.4 | 8.1 | 190 | 27.7 | 6.86
2988 | Solarwatt | P210-60 GET AK 195Wp | Solarwatt : P210-60 GET AK 195Wp | -0.32 | 36.5 | 8.16 | 195 | 27.7 | 7.04
2989 | Solarwatt | P210-60 GET AK 200Wp | Solarwatt : P210-60 GET AK 200Wp | -0.32 | 36.6 | 8.2 | 200 | 27.8 | 7.19
2990 | Solarwatt | P210-60 GET AK 205Wp | Solarwatt : P210-60 GET AK 205Wp | -0.32 | 36.7 | 8.24 | 205 | 28 | 7.32
2991 | Solarwatt | P210-60 GET AK 210Wp | Solarwatt : P210-60 GET AK 210Wp | -0.32 | 36.8 | 8.28 | 210 | 28.2 | 7.45
2992 | Solarwatt | P210-60 GET AK 215Wp | Solarwatt : P210-60 GET AK 215Wp | -0.32 | 37 | 8.33 | 215 | 28.3 | 7.6
2993 | Solarwatt | P210-60 GET AK 220Wp | Solarwatt : P210-60 GET AK 220Wp | -0.32 | 37.2 | 8.38 | 220 | 28.4 | 7.75
2994 | Solarwatt | P23-36 GET AK Laminat | Solarwatt : P23-36 GET AK Laminat | -0.402 | 21.4 | 1.54 | 11.88 | 16.8 | 1.42
2995 | Solarwatt | P23-36 GET AK Rahmen | Solarwatt : P23-36 GET AK Rahmen | -0.402 | 21.4 | 1.54 | 11.88 | 16.8 | 1.42
2996 | Solarwatt | P47-36 GET AK | Solarwatt : P47-36 GET AK | -0.402 | 21.4 | 3.07 | 47.52 | 16.8 | 2.83
2997 | Solarwatt | P47-36 TEA LK | Solarwatt : P47-36 TEA LK | -0.402 | 21.4 | 3.07 | 47.52 | 16.8 | 2.83
2998 | Solarwatt | Power 70-72 GEG LK 100 W | Solarwatt : Power 70-72 GEG LK 100 W | -0.36 | 42.6 | 3.2 | 100 | 34.6 | 2.9
2999 | Solarwatt | Power 70-72 GEG LK 65 W | Solarwatt : Power 70-72 GEG LK 65 W | -0.4 | 40 | 2.89 | 65 | 28 | 2.32
3000 | Solarwatt | Power 70-72 GEG LK 70 W | Solarwatt : Power 70-72 GEG LK 70 W | -0.4 | 41.8 | 2.93 | 70 | 29.2 | 2.4
3001 | SolarWatt | P220-60 GET AK 210Wp | SolarWatt : P220-60 GET AK 210Wp | -0.37 | 35.7 | 7.99 | 210 | 28.2 | 7.45
3002 | SolarWatt | P220-60 GET AK 215Wp | SolarWatt : P220-60 GET AK 215Wp | -0.37 | 35.9 | 8.12 | 215 | 28.4 | 7.58
3003 | SolarWatt | P220-60 GET AK 220Wp | SolarWatt : P220-60 GET AK 220Wp | -0.37 | 36 | 8.25 | 220 | 28.6 | 7.71
3004 | SolarWatt | P220-60 GET AK 225Wp | SolarWatt : P220-60 GET AK 225Wp | -0.37 | 36.1 | 8.32 | 225 | 28.8 | 7.82
3005 | SolarWatt | P220-60 GET AK 230Wp | SolarWatt : P220-60 GET AK 230Wp | -0.37 | 36.3 | 8.48 | 230 | 29.1 | 7.92
3006 | SolarWatt | P220-60 GET AK 235Wp | SolarWatt : P220-60 GET AK 235Wp | -0.37 | 36.5 | 8.62 | 235 | 29.3 | 8.03
3007 | SolarWatt | P220-60 GET AK 240Wp | SolarWatt : P220-60 GET AK 240Wp | -0.37 | 36.7 | 8.76 | 240 | 28.5 | 8.15
3008 | SolarWatt | P230-96 GET AK 215Wp | SolarWatt : P230-96 GET AK 215Wp | -0.37 | 58.3 | 5.07 | 215 | 47 | 4.58
3009 | SolarWatt | P230-96 GET AK 220Wp | SolarWatt : P230-96 GET AK 220Wp | -0.37 | 58.5 | 5.13 | 220 | 47.4 | 4.65
3010 | SolarWatt | P230-96 GET AK 225Wp | SolarWatt : P230-96 GET AK 225Wp | -0.37 | 58.7 | 5.21 | 225 | 47.6 | 4.74
3011 | SolarWatt | P230-96 GET AK 230Wp | SolarWatt : P230-96 GET AK 230Wp | -0.37 | 58.9 | 5.28 | 230 | 47.7 | 4.83
3012 | SolarWatt | P230-96 GET AK 235Wp | SolarWatt : P230-96 GET AK 235Wp | -0.37 | 59.1 | 5.4 | 235 | 47.8 | 4.92
3013 | SolarWatt | P230-96 GET AK 240Wp | SolarWatt : P230-96 GET AK 240Wp | -0.37 | 59.2 | 5.5 | 240 | 48 | 5.01
3014 | SolarWatt | P230-96 GET AK 245Wp | SolarWatt : P230-96 GET AK 245Wp | -0.37 | 59.3 | 5.6 | 245 | 48.1 | 5.1
3015 | SolarWatt | P230-96 GET AK 250Wp | SolarWatt : P230-96 GET AK 250Wp | -0.37 | 59.4 | 5.65 | 250 | 48.3 | 5.18
3016 | SolarWorld | GPV 150 P | SolarWorld : GPV 150 P | -0.388 | 43 | 4.7 | 150 | 34 | 4.4
3017 | SolarWorld | GPV 51 P | SolarWorld : GPV 51 P | -0.39 | 21.5 | 3 | 51 | 17 | 3
3018 | SolarWorld | GPV 75 P | SolarWorld : GPV 75 P | -0.39 | 21.5 | 4.7 | 75 | 17 | 4.4
3019 | SolarWorld | SM 150 P-12V-LAM | SolarWorld : SM 150 P-12V-LAM | -0.4 | 21.5 | 9.4 | 150 | 17 | 8.8
3020 | SolarWorld | SM 150-12V | SolarWorld : SM 150-12V | -0.4 | 21.5 | 9.2 | 150 | 17.5 | 8.6
3021 | SolarWorld | SM 150-12V-LAM | SolarWorld : SM 150-12V-LAM | -0.4 | 21.5 | 9.2 | 150 | 17.5 | 8.6
3022 | SolarWorld | SM 165-12 V | SolarWorld : SM 165-12 V | -0.4 | 21.6 | 10.1 | 165 | 17.7 | 9.3
3023 | SolarWorld | SM 165-12V-LAM | SolarWorld : SM 165-12V-LAM | -0.4 | 21.6 | 10.1 | 165 | 17.7 | 9.3
3024 | SolarWorld | SM 51 | SolarWorld : SM 51 | -0.402 | 21.5 | 3.2 | 51 | 17 | 3
3025 | SolarWorld | SW 075-D | SolarWorld : SW 075-D | -0.372 | 21.5 | 4.7 | 75 | 17 | 4.4
3026 | Solarworld | SW 130 Poly | Solarworld : SW 130 Poly | -0.33 | 24.1 | 7.5 | 130 | 18.9 | 6.9
3027 | Solarworld | SW 140 Poly | Solarworld : SW 140 Poly | -0.33 | 24.3 | 7.8 | 140 | 19.5 | 7.2
3028 | Solarworld | SW 150 Poly | Solarworld : SW 150 Poly | -0.33 | 24.5 | 8.1 | 150 | 20.1 | 7.5
3029 | SolarWorld | SW 155-C (12V) | SolarWorld : SW 155-C (12V) | -0.39 | 21.6 | 9.4 | 155 | 17.55 | 8.8
3030 | SolarWorld | SW 155-C (24V) | SolarWorld : SW 155-C (24V) | -0.39 | 43.2 | 4.7 | 155 | 35 | 4.4
3031 | Solarworld | SW 160 mono | Solarworld : SW 160 mono | -0.33 | 43.8 | 5 | 160 | 35 | 4.58
3032 | SolarWorld | SW 160-C (12V) | SolarWorld : SW 160-C (12V) | -0.39 | 21.6 | 9.8 | 160 | 17.6 | 9.1
3033 | SolarWorld | SW 160-C (24V) | SolarWorld : SW 160-C (24V) | -0.39 | 43.2 | 4.9 | 160 | 35.2 | 4.5
3034 | Solarworld | SW 165 mono | Solarworld : SW 165 mono | -0.33 | 44 | 5.1 | 165 | 35.3 | 4.68
3035 | Solarworld | SW 170 mono | Solarworld : SW 170 mono | -0.33 | 44.2 | 5.2 | 170 | 35.5 | 4.79
3036 | Solarworld | SW 175 mono | Solarworld : SW 175 mono | -0.33 | 44.4 | 5.3 | 175 | 35.8 | 4.89
3037 | Solarworld | SW 180 mono | Solarworld : SW 180 mono | -0.33 | 44.6 | 5.4 | 180 | 36 | 5.01
3038 | Solarworld | SW 185 mono | Solarworld : SW 185 mono | -0.33 | 44.8 | 5.5 | 185 | 36.3 | 5.1
3039 | Solarworld | SW 200 Poly | Solarworld : SW 200 Poly | -0.34 | 36.1 | 7.7 | 200 | 28.3 | 7.07
3040 | Solarworld | SW 205 Poly | Solarworld : SW 205 Poly | -0.34 | 36.2 | 7.8 | 205 | 28.5 | 7.2
3041 | Solarworld | SW 210 Poly | Solarworld : SW 210 Poly | -0.34 | 36.4 | 7.9 | 210 | 28.7 | 7.32
3042 | Solarworld | SW 215 Poly | Solarworld : SW 215 Poly | -0.34 | 36.5 | 8 | 215 | 28.9 | 7.44
3043 | Solarworld | SW 220 Poly | Solarworld : SW 220 Poly | -0.34 | 36.6 | 8.08 | 220 | 29.2 | 7.54
3044 | Solarworld | SW 225 Poly | Solarworld : SW 225 Poly | -0.34 | 36.8 | 8.17 | 225 | 29.5 | 7.63
3045 | SolConTec | PS160M-24/F | SolConTec : PS160M-24/F | -0.35 | 43.8 | 5.1 | 160 | 34.6 | 4.6
3046 | SolConTec | PS160P-24/F | SolConTec : PS160P-24/F | -0.35 | 43.8 | 5.1 | 160 | 34.4 | 4.7
3047 | SolConTec | PS165M-24/F | SolConTec : PS165M-24/F | -0.35 | 44 | 5.1 | 165 | 35 | 4.7
3048 | SolConTec | PS165P-24/F | SolConTec : PS165P-24/F | -0.35 | 44 | 5.1 | 165 | 34.8 | 4.8
3049 | SolConTec | PS170M-24/F | SolConTec : PS170M-24/F | -0.35 | 44.2 | 5.2 | 170 | 35.4 | 4.8
3050 | SolConTec | PS170P-24/F | SolConTec : PS170P-24/F | -0.35 | 44.2 | 5.2 | 170 | 35.2 | 4.8
3051 | SolConTec | PS175M-24/F | SolConTec : PS175M-24/F | -0.35 | 44.4 | 5.2 | 175 | 35.8 | 4.9
3052 | SolConTec | PS175P-24/F | SolConTec : PS175P-24/F | -0.35 | 44.4 | 5.2 | 175 | 35.6 | 4.9
3053 | SolConTec | PS180M-24/F | SolConTec : PS180M-24/F | -0.35 | 44.6 | 5.3 | 180 | 36.2 | 5
3054 | SolConTec | PS180P-24/F | SolConTec : PS180P-24/F | -0.35 | 44.6 | 5.3 | 180 | 36 | 5
3055 | SolConTec | PS185M-24/F | SolConTec : PS185M-24/F | -0.35 | 44.8 | 5.3 | 185 | 36.6 | 5.1
3056 | SolConTec | PS185P-24/F | SolConTec : PS185P-24/F | -0.35 | 44.8 | 5.3 | 185 | 36.4 | 5.1
3057 | SolConTec | PS190M-24/F | SolConTec : PS190M-24/F | -0.35 | 45 | 5.4 | 190 | 37 | 5.1
3058 | SolConTec | PS190P-24/F | SolConTec : PS190P-24/F | -0.35 | 45 | 5.4 | 190 | 36.8 | 5.2
3059 | SolConTec | PS210M-20/U | SolConTec : PS210M-20/U | -0.35 | 36.7 | 7.9 | 210 | 28.8 | 7.3
3060 | SolConTec | PS210P-20/U | SolConTec : PS210P-20/U | -0.35 | 36.5 | 7.9 | 210 | 28.6 | 7.4
3061 | SolConTec | PS215M-20/U | SolConTec : PS215M-20/U | -0.35 | 36.9 | 8 | 215 | 29 | 7.4
3062 | SolConTec | PS215P-20/U | SolConTec : PS215P-20/U | -0.35 | 36.7 | 8 | 215 | 28.8 | 7.5
3063 | SolConTec | PS220M-20/U | SolConTec : PS220M-20/U | -0.35 | 37 | 8.1 | 220 | 29.2 | 7.5
3064 | SolConTec | PS220P-20/U | SolConTec : PS220P-20/U | -0.35 | 36.9 | 8.1 | 220 | 29 | 7.6
3065 | SolConTec | PS225M-20/U | SolConTec : PS225M-20/U | -0.35 | 37.1 | 8.2 | 225 | 29.4 | 7.7
3066 | SolConTec | PS225P-20/U | SolConTec : PS225P-20/U | -0.35 | 37 | 8.2 | 225 | 29.2 | 7.7
3067 | SolConTec | PS230M-20/U | SolConTec : PS230M-20/U | -0.35 | 37.3 | 8.3 | 230 | 29.6 | 7.8
3068 | SolConTec | PS230P-20/U | SolConTec : PS230P-20/U | -0.35 | 37.1 | 8.3 | 230 | 29.4 | 7.8
3069 | SolConTec | PS235M-20/U | SolConTec : PS235M-20/U | -0.35 | 37.5 | 8.4 | 235 | 29.8 | 7.9
3070 | SolConTec | PS235P-20/U | SolConTec : PS235P-20/U | -0.35 | 37.3 | 8.4 | 235 | 29.6 | 7.9
3071 | SolConTec | PS240M-20/U | SolConTec : PS240M-20/U | -0.35 | 37.6 | 8.5 | 240 | 30 | 8
3072 | SolConTec | PS240P-20/U | SolConTec : PS240P-20/U | -0.35 | 37.5 | 8.5 | 240 | 29.8 | 8.1
3073 | Solec | S-008 | Solec : S-008 | -0.4 | 21.3 | 0.5 | 8 | 17.1 | 0.47
3074 | Solec | S-012 | Solec : S-012 | -0.4 | 21.3 | 0.75 | 12 | 17.1 | 0.7
3075 | Solec | S-020 | Solec : S-020 | -0.4 | 21.3 | 1.25 | 20 | 17.1 | 1.17
3076 | Solec | S-025 | Solec : S-025 | -0.4 | 21.3 | 1.56 | 25 | 17.1 | 1.46
3077 | Solec | S-055 | Solec : S-055 | -0.4 | 21.3 | 3.44 | 55 | 17.1 | 3.22
3078 | Solec | S-100D 12V | Solec : S-100D 12V | -0.4 | 21.3 | 6.26 | 100 | 17.1 | 5.85
3079 | Solec | S-100D 24V | Solec : S-100D 24V | -0.4 | 42.6 | 3.13 | 100 | 34.2 | 2.92
3080 | Solec | S-110D 12V | Solec : S-110D 12V | -0.4 | 21.3 | 6.89 | 110 | 17.1 | 6.43
3081 | Solec | S-110D 24V | Solec : S-110D 24V | -0.4 | 42.6 | 3.44 | 110 | 34.2 | 3.22
3082 | Solec | SQ-080 | Solec : SQ-080 | -0.4 | 21.3 | 5.01 | 80 | 17.1 | 4.68
3083 | Solec | SQ-090 | Solec : SQ-090 | -0.4 | 21.3 | 5.63 | 90 | 17.1 | 5.26
3084 | SOLIBRO | SL1-65F | SOLIBRO : SL1-65F | -0.36 | 68.5 | 1.57 | 65 | 51.2 | 1.27
3085 | SOLIBRO | SL1-70F | SOLIBRO : SL1-70F | -0.36 | 70.3 | 1.58 | 70 | 53.8 | 1.3
3086 | SOLIBRO | SL1-75F | SOLIBRO : SL1-75F | -0.36 | 71.5 | 1.59 | 75 | 55.6 | 1.35
3087 | SOLIBRO | SL1-80F | SOLIBRO : SL1-80F | -0.36 | 72.5 | 1.6 | 80 | 57.1 | 1.4
3088 | SOLIBRO | SL1-85F | SOLIBRO : SL1-85F | -0.36 | 73.4 | 1.61 | 85 | 59 | 1.44
3089 | SOLON | Black 160/05 (155Wp) | SOLON : Black 160/05 (155Wp) | -0.31 | 43.9 | 4.7 | 155 | 35.8 | 4.35
3090 | SOLON | Black 160/05 (160Wp) | SOLON : Black 160/05 (160Wp) | -0.31 | 44 | 4.8 | 160 | 35.9 | 4.445
3091 | SOLON | Black 160/05 (165Wp) | SOLON : Black 160/05 (165Wp) | -0.31 | 44.15 | 4.95 | 165 | 36 | 4.6
3092 | SOLON | Black 160/05 (170Wp) | SOLON : Black 160/05 (170Wp) | -0.31 | 44.3 | 5.05 | 170 | 36.1 | 4.7
3093 | SOLON | Black 160/05 (170Wp) | SOLON : Black 160/05 (170Wp) | -0.31 | 44.3 | 5.05 | 170 | 36.1 | 4.7
3094 | SOLON | Black 160/05 (175Wp) | SOLON : Black 160/05 (175Wp) | -0.31 | 44.5 | 5.2 | 175 | 36.2 | 4.85
3095 | Solon | Black 230/07 215Wp | Solon : Black 230/07 215Wp | -0.33 | 36.6 | 8.59 | 215 | 27.5 | 7.82
3096 | Solon | Black 230/07 220Wp | Solon : Black 230/07 220Wp | -0.33 | 35.8 | 8.6 | 220 | 28.1 | 7.85
3097 | Solon | Black 230/07 225Wp | Solon : Black 230/07 225Wp | -0.33 | 36 | 8.7 | 225 | 28.3 | 7.95
3098 | Solon | Black 230/07 230Wp | Solon : Black 230/07 230Wp | -0.33 | 36.4 | 8.75 | 230 | 28.8 | 8
3099 | Solon | Black 230/07 235Wp | Solon : Black 230/07 235Wp | -0.33 | 36.5 | 8.75 | 235 | 29.4 | 8
3100 | Solon | Black 230/07 240Wp | Solon : Black 230/07 240Wp | -0.33 | 36.7 | 8.8 | 240 | 29.7 | 8.1
3101 | Solon | Black 280/10 260Wp | Solon : Black 280/10 260Wp | -0.29 | 60.7 | 5.5 | 260 | 52 | 5.04
3102 | Solon | Black 280/10 265Wp | Solon : Black 280/10 265Wp | -0.29 | 61.2 | 5.5 | 265 | 52.4 | 5.1
3103 | Solon | Black 280/10 270Wp | Solon : Black 280/10 270Wp | -0.29 | 61.4 | 5.6 | 270 | 52.7 | 5.13
3104 | Solon | Black 280/10 275Wp | Solon : Black 280/10 275Wp | -0.29 | 61.5 | 5.6 | 275 | 53 | 5.17
3105 | Solon | Black 280/10 280Wp | Solon : Black 280/10 280Wp | -0.29 | 61.8 | 5.7 | 280 | 53.3 | 5.28
3106 | Solon | Black 280/10 285Wp | Solon : Black 280/10 285Wp | -0.29 | 62 | 5.8 | 285 | 53.6 | 5.34
3107 | SOLON | Black 280/11 (260Wp) | SOLON : Black 280/11 (260Wp) | -0.36 | 42.61 | 8.14 | 260 | 34.4 | 7.56
3108 | SOLON | Black 280/11 (265Wp) | SOLON : Black 280/11 (265Wp) | -0.36 | 42.89 | 8.21 | 265 | 34.6 | 7.66
3109 | SOLON | Black 280/11 (270Wp) | SOLON : Black 280/11 (270Wp) | -0.36 | 43.15 | 8.29 | 270 | 34.8 | 7.76
3110 | SOLON | Black 280/11 (275Wp) | SOLON : Black 280/11 (275Wp) | -0.36 | 43.42 | 8.36 | 275 | 35 | 7.86
3111 | SOLON | Black 280/11 (280Wp) | SOLON : Black 280/11 (280Wp) | -0.36 | 43.69 | 8.44 | 280 | 35.2 | 7.96
3112 | SOLON | Black 280/11 (285Wp) | SOLON : Black 280/11 (285Wp) | -0.36 | 43.96 | 8.51 | 285 | 35.4 | 8.06
3113 | SOLON | Black 280/11 (290Wp) | SOLON : Black 280/11 (290Wp) | -0.36 | 44.23 | 8.59 | 290 | 35.6 | 8.16
3114 | Solon | Black 300/10 280Wp | Solon : Black 300/10 280Wp | -0.29 | 63.7 | 6 | 280 | 51.5 | 5.43
3115 | Solon | Black 300/10 280Wp | Solon : Black 300/10 280Wp | -0.29 | 63.7 | 6 | 280 | 51.5 | 5.43
3116 | Solon | Black 300/10 285Wp | Solon : Black 300/10 285Wp | -0.29 | 64.2 | 6.1 | 285 | 52 | 5.51
3117 | Solon | Black 300/10 285Wp | Solon : Black 300/10 285Wp | -0.29 | 64.2 | 6.1 | 285 | 52 | 5.51
3118 | Solon | Black 300/10 290Wp | Solon : Black 300/10 290Wp | -0.29 | 64.2 | 6.1 | 290 | 51.96 | 5.6
3119 | Solon | Black 300/10 290Wp | Solon : Black 300/10 290Wp | -0.29 | 64.2 | 6.1 | 290 | 51.96 | 5.6
3120 | Solon | Black 300/10 295Wp | Solon : Black 300/10 295Wp | -0.29 | 63.8 | 6.1 | 295 | 52.1 | 5.66
3121 | Solon | Black 300/10 295Wp | Solon : Black 300/10 295Wp | -0.29 | 63.8 | 6.1 | 295 | 52.1 | 5.66
3122 | Solon | Black 300/10 300Wp | Solon : Black 300/10 300Wp | -0.29 | 64.2 | 6.1 | 300 | 53.5 | 5.61
3123 | Solon | Black 300/10 300Wp | Solon : Black 300/10 300Wp | -0.29 | 64.2 | 6.1 | 300 | 53.5 | 5.61
3124 | Solon | Black 300/10 305Wp | Solon : Black 300/10 305Wp | -0.29 | 64.5 | 6.2 | 305 | 53 | 5.76
3125 | Solon | Black 300/10 305Wp | Solon : Black 300/10 305Wp | -0.29 | 64.5 | 6.2 | 305 | 53 | 5.76
3126 | Solon | Blue 230/07 240Wp | Solon : Blue 230/07 240Wp | -0.35 | 40 | 8.7 | 240 | 29.4 | 8.1
3127 | Solon | Blue P220/6+ 200Wp | Solon : Blue P220/6+ 200Wp | -0.35 | 35.6 | 7.9 | 200 | 27.8 | 7.2
3128 | Solon | Blue P220/6+ 205Wp | Solon : Blue P220/6+ 205Wp | -0.35 | 35.9 | 8 | 205 | 28.1 | 7.3
3129 | Solon | Blue P220/6+ 210Wp | Solon : Blue P220/6+ 210Wp | -0.35 | 36.1 | 8.1 | 210 | 28.3 | 7.45
3130 | Solon | Blue P220/6+ 215Wp | Solon : Blue P220/6+ 215Wp | -0.35 | 36.3 | 8.2 | 215 | 28.5 | 7.55
3131 | Solon | Blue P220/6+ 220Wp | Solon : Blue P220/6+ 220Wp | -0.35 | 36.4 | 8.3 | 220 | 28.8 | 7.65
3132 | Solon | Blue P220/6+ 225Wp | Solon : Blue P220/6+ 225Wp | -0.35 | 36.6 | 8.4 | 225 | 28.9 | 7.8
3133 | Solon | Blue P220/6+ 230Wp | Solon : Blue P220/6+ 230Wp | -0.35 | 36.7 | 8.55 | 230 | 29 | 7.95
3134 | Solon | Blue P220/6+ 235Wp | Solon : Blue P220/6+ 235Wp | -0.35 | 36.9 | 8.65 | 235 | 29.2 | 8.05
3135 | Solon | M230 200Wp | Solon : M230 200Wp | -0.33 | 34.9 | 8.45 | 200 | 26.3 | 7.65
3136 | Solon | M230 205Wp | Solon : M230 205Wp | -0.33 | 35.1 | 8.5 | 205 | 26.7 | 7.71
3137 | Solon | M230 210Wp | Solon : M230 210Wp | -0.33 | 35.4 | 8.54 | 210 | 27.1 | 7.76
3138 | Solon | M230 215Wp | Solon : M230 215Wp | -0.33 | 35.6 | 8.59 | 215 | 27.5 | 7.82
3139 | Solon | M230 220Wp | Solon : M230 220Wp | -0.33 | 35.8 | 8.6 | 220 | 28.1 | 7.85
3140 | Solon | M230 225Wp | Solon : M230 225Wp | -0.33 | 36 | 8.7 | 225 | 28.3 | 7.95
3141 | Solon | M230 230Wp | Solon : M230 230Wp | -0.33 | 36.4 | 8.75 | 230 | 28.8 | 8
3142 | Solon | M230 235Wp | Solon : M230 235Wp | -0.33 | 36.5 | 8.75 | 235 | 29.4 | 8
3143 | Solon | M230/6+ 205Wp | Solon : M230/6+ 205Wp | -0.33 | 35.4 | 8.35 | 205 | 26.6 | 7.7
3144 | Solon | M230/6+ 210Wp | Solon : M230/6+ 210Wp | -0.33 | 35.7 | 8.4 | 210 | 27.05 | 7.75
3145 | Solon | M230/6+ 215Wp | Solon : M230/6+ 215Wp | -0.33 | 35.9 | 8.45 | 215 | 27.55 | 7.8
3146 | Solon | M230/6+ 220Wp | Solon : M230/6+ 220Wp | -0.33 | 36.1 | 8.55 | 220 | 28.05 | 7.85
3147 | Solon | M230/6+ 225Wp | Solon : M230/6+ 225Wp | -0.33 | 36.35 | 8.6 | 225 | 28.7 | 7.85
3148 | Solon | M230/6+ 230Wp | Solon : M230/6+ 230Wp | -0.33 | 36.6 | 8.7 | 230 | 29.3 | 7.85
3149 | Solon | M230/6+ 235Wp | Solon : M230/6+ 235Wp | -0.33 | 36.85 | 8.8 | 235 | 29.75 | 7.9
3150 | Solon | M230/6+ 240Wp | Solon : M230/6+ 240Wp | -0.33 | 37.1 | 8.9 | 240 | 30.4 | 7.9
3151 | Solon | P130/6+ 120Wp | Solon : P130/6+ 120Wp | -0.35 | 21.4 | 7.9 | 120 | 16.7 | 7.2
3152 | Solon | P130/6+ 125Wp | Solon : P130/6+ 125Wp | -0.35 | 21.7 | 8.15 | 125 | 17 | 7.4
3153 | Solon | P130/6+ 130Wp | Solon : P130/6+ 130Wp | -0.35 | 21.8 | 8.2 | 130 | 17.1 | 7.6
3154 | Solon | P130/6+ 135Wp | Solon : P130/6+ 135Wp | -0.35 | 21.9 | 8.4 | 135 | 17.3 | 7.8
3155 | Solon | P130/6+ 140Wp | Solon : P130/6+ 140Wp | -0.35 | 22.1 | 8.6 | 140 | 17.4 | 8.05
3156 | Solon | P160/6 | Solon : P160/6 | -0.35 | 31.6 | 7.1 | 160 | 25.4 | 6.3
3157 | Solon | P180/6+ 160Wp | Solon : P180/6+ 160Wp | -0.35 | 29.7 | 7.8 | 160 | 22.6 | 7.1
3158 | Solon | P180/6+ 165Wp | Solon : P180/6+ 165Wp | -0.35 | 29.9 | 7.9 | 165 | 22.8 | 7.25
3159 | Solon | P180/6+ 170Wp | Solon : P180/6+ 170Wp | -0.35 | 30 | 8.1 | 170 | 23 | 7.4
3160 | Solon | P180/6+ 175Wp | Solon : P180/6+ 175Wp | -0.35 | 30.1 | 8.2 | 175 | 23.4 | 7.5
3161 | Solon | P180/6+ 180Wp | Solon : P180/6+ 180Wp | -0.35 | 30.2 | 8.3 | 180 | 23.7 | 7.6
3162 | Solon | P180/6+ 185Wp | Solon : P180/6+ 185Wp | -0.35 | 30.3 | 8.4 | 185 | 23.9 | 7.75
3163 | Solon | P180/6+ 190Wp | Solon : P180/6+ 190Wp | -0.35 | 30.5 | 8.6 | 190 | 24.1 | 7.9
3164 | Solon | P180/6+ 195Wp | Solon : P180/6+ 195Wp | -0.35 | 30.7 | 8.7 | 195 | 24.1 | 8.1
3165 | Solon | SOLON M 180 / 6 | Solon : SOLON M 180 / 6 | -0.36 | 34.6 | 7.6 | 180 | 26.8 | 6.7
3166 | Solon | SOLON P 120 / 6 | Solon : SOLON P 120 / 6 | -0.35 | 22 | 7.45 | 120 | 17.4 | 6.9
3167 | Solon | SOLON P 200 / 6 (190 Wp) | Solon : SOLON P 200 / 6 (190 Wp) | -0.35 | 36.5 | 7.3 | 190 | 28.4 | 6.7
3168 | Solon | SOLON P 200 / 6 (200 Wp) | Solon : SOLON P 200 / 6 (200 Wp) | -0.35 | 36.6 | 7.45 | 200 | 29 | 6.9
3169 | SOLSONICA | 608-165 | SOLSONICA : 608-165 | -0.335 | 29.2 | 7.93 | 165 | 22.64 | 7.43
3170 | SOLSONICA | 608-170 | SOLSONICA : 608-170 | -0.337 | 29.79 | 8.12 | 170 | 22.83 | 7.45
3171 | SOLSONICA | 608-175 | SOLSONICA : 608-175 | -0.333 | 30.18 | 8.13 | 175 | 23.3 | 7.51
3172 | SOLSONICA | 608-180 | SOLSONICA : 608-180 | -0.329 | 30.58 | 8.15 | 180 | 23.78 | 7.57
3173 | SOLSONICA | 608-185 | SOLSONICA : 608-185 | -0.324 | 30.98 | 8.16 | 185 | 24.25 | 7.63
3174 | SOLSONICA | 610-210 | SOLSONICA : 610-210 | -0.335 | 36,65 | 7,91 | 210 | 28,38 | 7,41
3175 | SOLSONICA | 610-215 | SOLSONICA : 610-215 | -0.335 | 36,85 | 8,00 | 215 | 28,68 | 7,50
3176 | SOLSONICA | 610-220 | SOLSONICA : 610-220 | -0.335 | 37,05 | 8,09 | 220 | 28,98 | 7,59
3177 | SOLSONICA | 610-225 | SOLSONICA : 610-225 | -0.335 | 37,25 | 8,17 | 225 | 29,29 | 7,68
3178 | SOLSONICA | 610-230 | SOLSONICA : 610-230 | -0.335 | 37,45 | 8,26 | 230 | 29,59 | 7,77
3179 | SOLSONICA | 610-235 | SOLSONICA : 610-235 | -0.335 | 37,65 | 8,35 | 235 | 29,90 | 7,86
3180 | SOLSONICA | 612-250 | SOLSONICA : 612-250 | -0.335 | 43,89 | 7,80 | 250 | 33,79 | 7,30
3181 | SOLSONICA | 612-255 | SOLSONICA : 612-255 | -0.335 | 44,10 | 7,89 | 255 | 34,12 | 7,39
3182 | SOLSONICA | 612-258 | SOLSONICA : 612-258 | -0.34 | 44.82 | 7.88 | 258 | 35.04 | 7.35
3183 | SOLSONICA | 612-260 | SOLSONICA : 612-260 | -0.335 | 44,30 | 7,98 | 260 | 34,44 | 7,48
3184 | SOLSONICA | 612-264 | SOLSONICA : 612-264 | -0.34 | 44.94 | 7.96 | 264 | 35.4 | 7.45
3185 | SOLSONICA | 612-265 | SOLSONICA : 612-265 | -0.335 | 44,50 | 8,07 | 265 | 34,77 | 7,57
3186 | SOLSONICA | 612-270 | SOLSONICA : 612-270 | -0.34 | 45.18 | 8.05 | 270 | 35.76 | 7.54
3187 | SOLSONICA | 612-270 | SOLSONICA : 612-270 | -0.335 | 44,70 | 8,15 | 270 | 35,10 | 7,66
3188 | SOLSONICA | 612-275 | SOLSONICA : 612-275 | -0.335 | 44,90 | 8,24 | 275 | 35,44 | 7,75
3189 | SOLSONICA | 612-276 | SOLSONICA : 612-276 | -0.34 | 45.31 | 8.13 | 276 | 36.13 | 7.63
3190 | SOLSONICA | 612-280 | SOLSONICA : 612-280 | -0.335 | 45,10 | 8,33 | 280 | 35,77 | 7,84
3191 | SOLSONICA | 612-282 | SOLSONICA : 612-282 | -0.34 | 45.43 | 8.21 | 282 | 36.49 | 7.72
3192 | SOLSONICA | 612-288 | SOLSONICA : 612-288 | -0.34 | 45.55 | 8.29 | 288 | 36.85 | 7.81
3193 | Solvis | SV 36-140 | Solvis : SV 36-140 | -0.35 | 22.6 | 8.35 | 140 | 17.9 | 7.82
3194 | Solvis | SV 48-190 | Solvis : SV 48-190 | -0.34 | 31.1 | 8.37 | 190 | 24.4 | 7.79
3195 | Solvis | SV 60-230 | Solvis : SV 60-230 | -0.35 | 37.6 | 8.35 | 230 | 29.6 | 7.77
3196 | Solvis | SV 72-275 | Solvis : SV 72-275 | -0.34 | 45.6 | 8.13 | 275 | 36.4 | 7.56
3197 | SOLYNDRA | SL-001-150 | SOLYNDRA : SL-001-150 | -0.24 | 91.4 | 2.72 | 150 | 65.7 | 2.28
3198 | SOLYNDRA | SL-001-157 | SOLYNDRA : SL-001-157 | -0.24 | 92.5 | 2.73 | 157 | 67.5 | 2.33
3199 | SOLYNDRA | SL-001-165 | SOLYNDRA : SL-001-165 | -0.24 | 93.9 | 2.74 | 165 | 69.6 | 2.37
3200 | SOLYNDRA | SL-001-173 | SOLYNDRA : SL-001-173 | -0.24 | 95.2 | 2.75 | 173 | 71.7 | 2.41
3201 | SOLYNDRA | SL-001-182 | SOLYNDRA : SL-001-182 | -0.24 | 96.7 | 2.76 | 182 | 73.9 | 2.46
3202 | SOLYNDRA | SL-001-191 | SOLYNDRA : SL-001-191 | -0.24 | 98.2 | 2.77 | 191 | 76.1 | 2.51
3203 | SONTOR | SN-125 | SONTOR : SN-125 | -0.39 | 128 | 1.71 | 125 | 96.8 | 1.29
3204 | SONTOR | SN-127.5 | SONTOR : SN-127.5 | -0.39 | 128.1 | 1.71 | 127.5 | 97.8 | 1.3
3205 | SONTOR | SN-130.0 | SONTOR : SN-130.0 | -0.39 | 128.2 | 1.71 | 130 | 98.8 | 1.32
3206 | SONTOR | SN-132,5 | SONTOR : SN-132,5 | -0.39 | 128.3 | 1.71 | 132.5 | 99.8 | 1.33
3207 | SONTOR | SN-135 | SONTOR : SN-135 | -0.39 | 128.4 | 1.71 | 135 | 100.7 | 1.34
3208 | SONTOR | SN-137,5 | SONTOR : SN-137,5 | -0.39 | 128.5 | 1.71 | 137.5 | 101.7 | 1.35
3209 | SONTOR | SN-140.0 | SONTOR : SN-140.0 | -0.39 | 128.6 | 1.71 | 140 | 102.7 | 1.36
3210 | SONTOR | SN-142.5 | SONTOR : SN-142.5 | -0.39 | 128.7 | 1.71 | 142.5 | 103.6 | 1.38
3211 | SONTOR | SN-145.0 | SONTOR : SN-145.0 | -0.39 | 128.8 | 1.71 | 145 | 104.6 | 1.39
3212 | Sony | 190 Wp | Sony : 190 Wp | -0.33025 | 32.4 | 8 | 190 | 26.2 | 7.26
3213 | Sony | 200 Wp | Sony : 200 Wp | -0.32622 | 32.8 | 8.25 | 200 | 26.7 | 7.49
3214 | Sovello | SV-T-180 | Sovello : SV-T-180 | -0.34 | 21.3 | 11.64 | 180 | 17.1 | 10.53
3215 | Sovello | SV-T-185 | Sovello : SV-T-185 | -0.34 | 21.4 | 11.8 | 185 | 17.3 | 10.7
3216 | Sovello | SV-T-190 | Sovello : SV-T-190 | -0.34 | 21.5 | 11.95 | 190 | 17.4 | 10.92
3217 | Sovello | SV-T-195 | Sovello : SV-T-195 | -0.34 | 21.7 | 12.11 | 195 | 17.6 | 11.08
3218 | Sovello | SV-T-200 | Sovello : SV-T-200 | -0.34 | 21.8 | 12.26 | 200 | 17.7 | 11.3
3219 | Sovello | SV-X-195 | Sovello : SV-X-195 | -0.34 | 22.8 | 11.55 | 195 | 18.3 | 10.66
3220 | Sovello | SV-X-200 | Sovello : SV-X-200 | -0.34 | 22.9 | 11.71 | 200 | 18.3 | 10.93
3221 | Sovello | SV-X-205 | Sovello : SV-X-205 | -0.34 | 23 | 11.87 | 205 | 18.4 | 11.15
3222 | Sovello | SV-X-210 | Sovello : SV-X-210 | -0.33 | 23.1 | 12.02 | 210 | 18.5 | 11.36
3223 | Spire Solar | SS75 | Spire Solar : SS75 | -0.4 | 24.2 | 4.8 | 75 | 17 | 4.5
3224 | SPsistem | IS4000P-210P | SPsistem : IS4000P-210P | -0.37 | 32.9 | 9.06 | 210 | 26 | 8.05
3225 | SPsistem | IS4000P-220P | SPsistem : IS4000P-220P | -0.37 | 32.4 | 9.16 | 220 | 26.6 | 8.25
3226 | SPsistem | SPS-120 pc32 Black Ghost | SPsistem : SPS-120 pc32 Black Ghost | -0.34 | 19.81 | 8.05 | 120 | 16.04 | 7.48
3227 | SPsistem | SPS-125 pc32 Black Ghost | SPsistem : SPS-125 pc32 Black Ghost | -0.34 | 19.94 | 8.11 | 125 | 16.45 | 7.6
3228 | SPsistem | SPS-130 pc32 Black Ghost | SPsistem : SPS-130 pc32 Black Ghost | -0.34 | 20.06 | 8.32 | 130 | 16.66 | 7.8
3229 | SPsistem | SPS-175P | SPsistem : SPS-175P | -0.34 | 30.4 | 7.55 | 175 | 25.15 | 7.06
3230 | SPsistem | SPS-185P | SPsistem : SPS-185P | -0.34 | 30.65 | 8.01 | 185 | 24.73 | 7.48
3231 | SPsistem | SPS-185P plus | SPsistem : SPS-185P plus | -0.34 | 30.65 | 8.01 | 185 | 24.73 | 7.48
3232 | SPsistem | SPS-190P | SPsistem : SPS-190P | -0.34 | 30.9 | 8.03 | 190 | 25.3 | 7.51
3233 | SPsistem | SPS-195P | SPsistem : SPS-195P | -0.34 | 31.05 | 8.08 | 195 | 25.8 | 7.56
3234 | SPsistem | SPS-195P plus | SPsistem : SPS-195P plus | -0.34 | 31.05 | 8.08 | 195 | 25.8 | 7.56
3235 | SPsistem | SPS-200P | SPsistem : SPS-200P | -0.34 | 31.12 | 8.28 | 200 | 25.94 | 7.71
3236 | SPsistem | SPS-210P | SPsistem : SPS-210P | -0.34 | 36.48 | 7.55 | 210 | 30.18 | 7.06
3237 | SPsistem | SPS-220P | SPsistem : SPS-220P | -0.34 | 36.84 | 7.82 | 220 | 30.05 | 7.32
3238 | SPsistem | SPS-220P plus | SPsistem : SPS-220P plus | -0.34 | 36.84 | 7.82 | 220 | 30.05 | 7.32
3239 | SPsistem | SPS-230P | SPsistem : SPS-230P | -0.34 | 37.26 | 7.74 | 230 | 30.46 | 7.55
3240 | SPsistem | SPS-235P | SPsistem : SPS-235P | -0.34 | 37.35 | 8.2 | 235 | 31.2 | 7.65
3241 | SPsistem | SPS-240P | SPsistem : SPS-240P | -0.34 | 37.39 | 8.38 | 240 | 30.85 | 7.78
3242 | Stafier Solar | ST90M6+ | Stafier Solar : ST90M6+ | -0.36 | 13.86 | 8.46 | 90 | 11.33 | 8.02
3243 | Star Unity | Sunny Tile, Typ amorph | Star Unity : Sunny Tile, Typ amorph | -0.4 | 22 | 0.15 | 2 | 12 | 0.133
3244 | Star Unity | Sunny Tile, Typ mono | Star Unity : Sunny Tile, Typ mono | -0.4 | 16.3 | 0.53 | 6.5 | 12.8 | 0.5
3245 | Stel Solar | 210W | Stel Solar : 210W | -0.25 | 36.3 | 7.74 | 210 | 29.2 | 7.22
3246 | Stel Solar | 215W | Stel Solar : 215W | -0.25 | 36.5 | 7.79 | 215 | 29.4 | 7.32
3247 | Stel Solar | 220W | Stel Solar : 220W | -0.25 | 36.8 | 7.88 | 220 | 29.7 | 7.45
3248 | Stel Solar | 225W | Stel Solar : 225W | -0.25 | 37 | 7.95 | 225 | 29.9 | 7.55
3249 | Stel Solar | 230W | Stel Solar : 230W | -0.25 | 37.2 | 8.03 | 230 | 31.1 | 7.65
3250 | SULFURCELL | SCG50-HV-RI | SULFURCELL : SCG50-HV-RI | -0.26 | 49.5 | 1.66 | 50 | 36.8 | 1.36
3251 | SULFURCELL | SCG52-HV-RI | SULFURCELL : SCG52-HV-RI | -0.26 | 50.2 | 1.67 | 52.5 | 37.8 | 1.39
3252 | SULFURCELL | SCG55-HV-RI | SULFURCELL : SCG55-HV-RI | -0.26 | 50.9 | 1.69 | 55 | 38.8 | 1.42
3253 | SULFURCELL | SCG57-HV-RI | SULFURCELL : SCG57-HV-RI | -0.26 | 51.4 | 1.71 | 57.5 | 39.7 | 1.45
3254 | SULFURCELL | SCG60-HV-RI | SULFURCELL : SCG60-HV-RI | -0.26 | 52.1 | 1.74 | 60 | 40.3 | 1.49
3255 | Sun Peak | ALP 195 | Sun Peak : ALP 195 | -0.4 | 35.5 | 7.4 | 195 | 28.54 | 6.9
3256 | Sun Peak | ALP 200 | Sun Peak : ALP 200 | -0.4 | 35.98 | 7.58 | 200 | 28.54 | 7
3257 | Sun Peak | ALP 205 | Sun Peak : ALP 205 | -0.4 | 35.9 | 8 | 205 | 28.1 | 7.3
3258 | Sun Peak | ALP 210 | Sun Peak : ALP 210 | -0.4 | 36.1 | 8.1 | 210 | 28.3 | 7.45
3259 | Sun Peak | ALP 215 | Sun Peak : ALP 215 | -0.4 | 36 | 7.83 | 215 | 29.94 | 7.18
3260 | Sun Peak | ALP 220 | Sun Peak : ALP 220 | -0.4 | 36.06 | 7.95 | 220 | 30.12 | 7.3
3261 | Sun Peak | ALP 225 | Sun Peak : ALP 225 | -0.4 | 36.42 | 8.1 | 225 | 30.36 | 7.41
3262 | Sun Peak | ALP 235 | Sun Peak : ALP 235 | -0.405 | 36.27 | 8.23 | 235 | 30.48 | 7.71
3263 | Sun Power | E19/238 | Sun Power : E19/238 | -0.273 | 48.5 | 6.25 | 238 | 40.5 | 5.88
3264 | Sunfilm AG | Model SN2-125 | Sunfilm AG : Model SN2-125 | -0.3 | 125.7 | 1.6 | 125 | 95.7 | 1.31
3265 | Sunfilm AG | Model SN2-127.5 | Sunfilm AG : Model SN2-127.5 | -0.3 | 126.4 | 1.61 | 127.5 | 96.5 | 1.33
3266 | Sunfilm AG | Model SN2-130 | Sunfilm AG : Model SN2-130 | -0.3 | 127.1 | 1.62 | 130 | 97.2 | 1.34
3267 | Sunfilm AG | Model SN2-132.5 | Sunfilm AG : Model SN2-132.5 | -0.3 | 127.8 | 1.63 | 132.5 | 97.9 | 1.36
3268 | Sunfilm AG | Model SN2-135 | Sunfilm AG : Model SN2-135 | -0.3 | 128.5 | 1.64 | 135 | 98.7 | 1.37
3269 | Sunfilm AG | Model SN2-137.5 | Sunfilm AG : Model SN2-137.5 | -0.3 | 129.2 | 1.65 | 137.5 | 99.4 | 1.39
3270 | Sunfilm AG | Model SN2-140 | Sunfilm AG : Model SN2-140 | -0.3 | 129.8 | 1.66 | 140 | 100.2 | 1.41
3271 | Sunfilm AG | Model SN2-142.5 | Sunfilm AG : Model SN2-142.5 | -0.3 | 130.5 | 1.67 | 142.5 | 100.9 | 1.42
3272 | Sunfilm AG | Model SN2-145 | Sunfilm AG : Model SN2-145 | -0.3 | 131.2 | 1.68 | 145 | 101.6 | 1.44
3273 | Sunovation | Sunovation 70 | Sunovation : Sunovation 70 | -0.4 | 21.2 | 4.86 | 140 | 16.2 | 4.4
3274 | SunPower Corp | SPR-200 | SunPower Corp : SPR-200 | -0.287 | 47.8 | 5.4 | 200 | 40 | 5
3275 | SunPower Corp | SPR-210 | SunPower Corp : SPR-210 | -0.287 | 47.8 | 5.65 | 210 | 40 | 5.25
3276 | SunPower Corp | SPR-210-BLK | SunPower Corp : SPR-210-BLK | -0.287 | 47.7 | 5.75 | 210 | 40 | 5.25
3277 | SunPower Corp | SPR-215-WHT | SunPower Corp : SPR-215-WHT | -0.283 | 48.3 | 5.8 | 215 | 39.8 | 5.4
3278 | SunPower Corp | SPR-215-WHT | SunPower Corp : SPR-215-WHT | -0.283 | 48.3 | 5.8 | 215 | 39.8 | 5.4
3279 | SunPower Corp | SPR-225-BLK | SunPower Corp : SPR-225-BLK | -0.273 | 48.5 | 5.87 | 225 | 41 | 5.49
3280 | SunPower Corp | SPR-230-BLK | SunPower Corp : SPR-230-BLK | -0.272 | 48.7 | 5.99 | 230 | 41 | 5.61
3281 | SunPower Corp | SPR-230-WHT | SunPower Corp : SPR-230-WHT | -0.272 | 48.7 | 5.99 | 230 | 41 | 5.61
3282 | SunPower Corp | SPR-305-WHT | SunPower Corp : SPR-305-WHT | -0.275 | 64.2 | 5.96 | 305 | 54.7 | 5.58
3283 | SunPower Corp | SPR-315-WHT | SunPower Corp : SPR-315-WHT | -0.273 | 64.6 | 6.14 | 315 | 54.7 | 5.76
3284 | SunPower Corp | SPR-90 | SunPower Corp : SPR-90 | -0.287 | 21.2 | 5.5 | 90 | 17.7 | 5.1
3285 | Sunpower Corp | Sunpower 230 | Sunpower Corp : Sunpower 230 | -0.272 | 48.7 | 5.99 | 230 | 41 | 5.61
3286 | Sunpower Corp | Sunpower 305 | Sunpower Corp : Sunpower 305 | -0.275 | 64.2 | 5.96 | 305 | 54.7 | 5.58
3287 | SunPower Corp | SUNTILE | SunPower Corp : SUNTILE | -0.25 | 14.6 | 5.65 | 63 | 12 | 5.25
3288 | Sunrise Solartech | SR-M666225 | Sunrise Solartech : SR-M666225 | -0.38 | 35.67 | 8.38 | 225 | 29 | 7.76
3289 | Sunrise Solartech | SR-M666230 | Sunrise Solartech : SR-M666230 | -0.38 | 35.92 | 8.51 | 230 | 29.2 | 7.88
3290 | Sunrise Solartech | SR-M666235 | Sunrise Solartech : SR-M666235 | -0.38 | 36.1 | 8.65 | 235 | 29.35 | 8.01
3291 | Sunrise Solartech | SR-M666240 | Sunrise Solartech : SR-M666240 | -0.38 | 36.28 | 8.79 | 240 | 29.5 | 8.14
3292 | Sunrise Solartech | SR-M666245 | Sunrise Solartech : SR-M666245 | -0.38 | 36.6 | 8.9 | 245 | 29.75 | 8.24
3293 | Sunrise Solartech | SR-M666250 | Sunrise Solartech : SR-M666250 | -0.38 | 36.9 | 9 | 250 | 30 | 8.34
3294 | Sunrise Solartech | SR-M666255 | Sunrise Solartech : SR-M666255 | -0.38 | 37.08 | 9.13 | 255 | 35.15 | 8.46
3295 | Sunrise Solartech | SR-M666260 | Sunrise Solartech : SR-M666260 | -0.38 | 37.4 | 9.24 | 260 | 34.4 | 8.56
3296 | Sunset | AS 1204 E | Sunset : AS 1204 E | -0.35 | 33.1 | 4.64 | 120 | 26.8 | 4.45
3297 | Sunset | AS 1304 E | Sunset : AS 1304 E | -0.35 | 33.9 | 4.88 | 130 | 27.9 | 4.65
3298 | Sunset | AS 160 5'' | Sunset : AS 160 5'' | -0.35 | 43.5 | 5.1 | 160 | 34.5 | 4.6
3299 | Sunset | AS 160 6'' | Sunset : AS 160 6'' | -0.35 | 31.7 | 7.2 | 160 | 25 | 6.4
3300 | Sunset | AS 165 6'' | Sunset : AS 165 6'' | -0.35 | 32 | 7.4 | 165 | 25.4 | 6.5
3301 | Sunset | AS 170 5'' | Sunset : AS 170 5'' | -0.35 | 44.1 | 5.35 | 170 | 35.2 | 4.82
3302 | Sunset | AS 170 6'' | Sunset : AS 170 6'' | -0.35 | 32.3 | 7.6 | 170 | 25.7 | 6.6
3303 | Sunset | AS 180 5'' | Sunset : AS 180 5'' | -0.35 | 44.3 | 5.6 | 180 | 36 | 4.98
3304 | Sunset | AS 6506 | Sunset : AS 6506 | -0.4 | 21.2 | 4.1 | 65 | 17.3 | 3.75
3305 | Sunset | AS 8005 | Sunset : AS 8005 | -0.4 | 21.5 | 4.95 | 80 | 17.3 | 4.6
3306 | Sunset | AS1105 | Sunset : AS1105 | -0.4 | 30 | 4.7 | 110 | 25 | 4.4
3307 | Sunset | AS1205 | Sunset : AS1205 | -0.4 | 31 | 4.85 | 120 | 26.2 | 4.58
3308 | Sunset | AS1305 | Sunset : AS1305 | -0.4 | 32 | 4.98 | 130 | 27.4 | 4.75
3309 | Sunset | KA 60 | Sunset : KA 60 | -0.38 | 92 | 1.19 | 60 | 67 | 0.9
3310 | Sunset | TWIN 130 | Sunset : TWIN 130 | -0.35 | 46.6 | 5 | 130 | 32 | 4.05
3311 | Sunset | TWIN 135 | Sunset : TWIN 135 | -0.35 | 46.7 | 5.1 | 135 | 32.5 | 4.15
3312 | Sunset | TWIN 140 | Sunset : TWIN 140 | -0.35 | 47.1 | 5.2 | 140 | 32.8 | 4.25
3313 | SUNTAICS | STC 100-22 P6 100Wp | SUNTAICS : STC 100-22 P6 100Wp | -0.27 | 22 | 7.1 | 100 | 17.5 | 6.3
3314 | SUNTAICS | STC 110-22 P6 110Wp | SUNTAICS : STC 110-22 P6 110Wp | -0.27 | 22 | 7.14 | 110 | 17.5 | 6.29
3315 | SUNTAICS | STC 140-24 P5 140Wp | SUNTAICS : STC 140-24 P5 140Wp | -0.38 | 44 | 4.3 | 140 | 35 | 4
3316 | SUNTAICS | STC 160-24 P5 140Wp | SUNTAICS : STC 160-24 P5 140Wp | -0.38 | 43.6 | 5.08 | 160 | 35.6 | 4.5
3317 | SUNTAICS | STC 170-35M5-E 170Wp | SUNTAICS : STC 170-35M5-E 170Wp | -0.38 | 44.5 | 5.12 | 170 | 35.9 | 4.74
3318 | Suntech | PLUTO215-Udm | Suntech : PLUTO215-Udm | -0.314 | 33.2 | 8.3 | 215 | 27.4 | 7.85
3319 | Suntech | PLUTO220-Udm | Suntech : PLUTO220-Udm | -0.314 | 33.5 | 8.4 | 220 | 27.8 | 7.92
3320 | Suntech | STP 150 - 12 / A | Suntech : STP 150 - 12 / A | -0.38 | 21.6 | 9.72 | 150 | 17.2 | 8.72
3321 | Suntech | STP 150 - 24 / A | Suntech : STP 150 - 24 / A | -0.38 | 43.2 | 4.87 | 150 | 34.4 | 4.86
3322 | Suntech | STP130-12/Tb | Suntech : STP130-12/Tb | -0.34 | 22 | 8.09 | 130 | 17.4 | 7.47
3323 | Suntech | STP130S-12/Tb | Suntech : STP130S-12/Tb | -0.35 | 22.2 | 8.04 | 130 | 17.5 | 7.43
3324 | Suntech | STP140S-12/Tb | Suntech : STP140S-12/Tb | -0.348 | 22.4 | 8.33 | 140 | 17.6 | 7.95
3325 | Suntech | STP150-24/Aa (150Wp) | Suntech : STP150-24/Aa (150Wp) | -0.301 | 43.2 | 4.87 | 150 | 34.4 | 4.36
3326 | Suntech | STP155-24/Aa/Ac (155Wp) | Suntech : STP155-24/Aa/Ac (155Wp) | -0.301 | 43.2 | 4.9 | 155 | 34.4 | 4.51
3327 | Suntech | STP160-24/Aa (160Wp) | Suntech : STP160-24/Aa (160Wp) | -0.301 | 43.2 | 5 | 160 | 34.4 | 4.65
3328 | Suntech | STP160S-24/Aa/Ac (160Wp) | Suntech : STP160S-24/Aa/Ac (160Wp) | -0.301 | 43.2 | 5 | 160 | 34.4 | 4.65
3329 | Suntech | STP160S-24/Ab-1 | Suntech : STP160S-24/Ab-1 | -0.34 | 43.2 | 5 | 160 | 34.4 | 4.65
3330 | Suntech | STP162S-24/Aa (162Wp) | Suntech : STP162S-24/Aa (162Wp) | -0.298 | 43.6 | 5 | 162 | 34.4 | 4.71
3331 | Suntech | STP165S-24/Aa/Ac (165Wp) | Suntech : STP165S-24/Aa/Ac (165Wp) | -0.298 | 43.6 | 5.04 | 165 | 34.8 | 4.74
3332 | Suntech | STP165S-24/Ab-1 | Suntech : STP165S-24/Ab-1 | -0.34 | 43.6 | 5.04 | 165 | 34.8 | 4.74
3333 | Suntech | STP170-24/Ab | Suntech : STP170-24/Ab | -0.34 | 44.4 | 5.11 | 170 | 35.5 | 4.79
3334 | Suntech | STP170S-18/Ub | Suntech : STP170S-18/Ub | -0.48 | 32.4 | 7.6 | 170 | 25.8 | 6.59
3335 | Suntech | STP170S-24/Aa/Ac (170Wp) | Suntech : STP170S-24/Aa/Ac (170Wp) | -0.297 | 43.8 | 5.14 | 170 | 35.2 | 4.83
3336 | Suntech | STP170S-24/Ab-1 | Suntech : STP170S-24/Ab-1 | -0.34 | 43.8 | 5.14 | 170 | 35.2 | 4.83
3337 | Suntech | STP170S-24/Ac/Ad | Suntech : STP170S-24/Ac/Ad | -0.34 | 44.4 | 5.15 | 170 | 35.6 | 4.8
3338 | Suntech | STP175-24/Ac | Suntech : STP175-24/Ac | -0.34 | 44.7 | 5.18 | 175 | 35.9 | 4.87
3339 | Suntech | STP175S-24/Ab-1 | Suntech : STP175S-24/Ab-1 | -0.34 | 44.2 | 5.2 | 175 | 35.2 | 4.95
3340 | Suntech | STP175S-24/Ac/Ad | Suntech : STP175S-24/Ac/Ad | -0.34 | 44.7 | 5.23 | 175 | 35.8 | 4.9
3341 | Suntech | STP180S-18/Ub | Suntech : STP180S-18/Ub | -0.48 | 32.4 | 7.7 | 180 | 25.8 | 6.98
3342 | Suntech | STP180S-24/Ab-1 | Suntech : STP180S-24/Ab-1 | -0.34 | 44.4 | 5.4 | 180 | 35.6 | 5.05
3343 | Suntech | STP180S-24/Ac | Suntech : STP180S-24/Ac | -0.346 | 44.8 | 5.3 | 180 | 36 | 5
3344 | Suntech | STP180-S-24/Ad | Suntech : STP180-S-24/Ad | -0.34 | 44.8 | 5.29 | 180 | 36 | 5
3345 | Suntech | STP185-S-24/Ad | Suntech : STP185-S-24/Ad | -0.34 | 45 | 5.43 | 185 | 36.4 | 5.09
3346 | Suntech | STP-190-18/Ub/Ud | Suntech : STP-190-18/Ub/Ud | -0.34 | 33 | 7.89 | 190 | 26 | 7.31
3347 | Suntech | STP190S-18/Ub | Suntech : STP190S-18/Ub | -0.349 | 33.2 | 7.84 | 190 | 26.2 | 7.25
3348 | Suntech | STP190S-24/Ad+ | Suntech : STP190S-24/Ad+ | -0.34 | 45.2 | 5.62 | 190 | 36.5 | 5.2
3349 | Suntech | STP195S-24/Ad+ | Suntech : STP195S-24/Ad+ | -0.34 | 45.4 | 5.69 | 195 | 36.6 | 5.33
3350 | Suntech | STP200-18/Ub/Ud | Suntech : STP200-18/Ub/Ud | -0.34 | 33.4 | 8.12 | 200 | 26.2 | 7.63
3351 | Suntech | STP200S-18/Ub | Suntech : STP200S-18/Ub | -0.345 | 33.6 | 8.1 | 200 | 26.2 | 7.63
3352 | Suntech | STP210-18/Ub/Ud | Suntech : STP210-18/Ub/Ud | -0.34 | 33.6 | 8.33 | 210 | 26.4 | 7.95
3353 | Suntech | STP210S-18/Ub | Suntech : STP210S-18/Ub | -0.47 | 33.2 | 8.1 | 210 | 26.6 | 7.89
3354 | Suntech | STP220-20/Wd | Suntech : STP220-20/Wd | -0.34 | 36.6 | 8.05 | 220 | 29.5 | 7.46
3355 | Suntech | STP225-20/Wd | Suntech : STP225-20/Wd | -0.34 | 36.7 | 8.15 | 225 | 29.6 | 7.61
3356 | Suntech | STP260-24/Vd | Suntech : STP260-24/Vd | -0.34 | 44 | 8.09 | 260 | 34.8 | 7.47
3357 | Suntech | STP260S-24/Vb/Vd | Suntech : STP260S-24/Vb/Vd | -0.34 | 44 | 8.09 | 260 | 34.8 | 7.47
3358 | Suntech | STP270-24/Vd | Suntech : STP270-24/Vd | -0.34 | 44.5 | 8.2 | 270 | 35 | 7.71
3359 | Suntech | STP270S-24/Vb/Vd | Suntech : STP270S-24/Vb/Vd | -0.34 | 44.5 | 8.2 | 270 | 35 | 7.71
3360 | Suntech | STP280-24/Vd | Suntech : STP280-24/Vd | -0.34 | 44.8 | 8.33 | 280 | 35.2 | 7.95
3361 | Suntech | STP280S-24/Vb/Vd | Suntech : STP280S-24/Vb/Vd | -0.34 | 44.8 | 8.33 | 280 | 35.2 | 7.95
3362 | SunWare | SunWare 12/1 | SunWare : SunWare 12/1 | -0.4 | 20.3 | 0.8 | 12 | 16.5 | 0.75
3363 | SunWare | SunWare 13/1 | SunWare : SunWare 13/1 | -0.4 | 20.3 | 0.8 | 13 | 18.2 | 0.75
3364 | SunWare | SunWare 17/1 | SunWare : SunWare 17/1 | -0.4 | 20.3 | 1.1 | 17 | 16.5 | 1
3365 | SunWare | SunWare 18/1 | SunWare : SunWare 18/1 | -0.4 | 22.5 | 1.1 | 18 | 18.2 | 1
3366 | SunWare | SunWare 25/1 | SunWare : SunWare 25/1 | -0.4 | 20.3 | 1.65 | 25 | 16.5 | 1.5
3367 | SunWare | SunWare 27/1 | SunWare : SunWare 27/1 | -0.4 | 22.5 | 1.65 | 27 | 18.2 | 1.5
3368 | SunWare | SunWare 27/2 | SunWare : SunWare 27/2 | -0.4 | 22.5 | 1.65 | 27 | 18.2 | 1.5
3369 | SunWare | SunWare 33/1 | SunWare : SunWare 33/1 | -0.4 | 20.3 | 2.2 | 33 | 16.5 | 2
3370 | SunWare | SunWare 35/1 | SunWare : SunWare 35/1 | -0.4 | 22.5 | 2.2 | 35 | 18.2 | 2
3371 | SunWare | SunWare 35/1 24V | SunWare : SunWare 35/1 24V | -0.4 | 23.8 | 1.1 | 35 | 35.1 | 1
3372 | SunWare | SunWare 35/1 SRM 2 | SunWare : SunWare 35/1 SRM 2 | -0.4 | 21.5 | 2.2 | 34 | 17.5 | 2
3373 | SunWare | SunWare 35/2 | SunWare : SunWare 35/2 | -0.4 | 22.5 | 2.2 | 36 | 18.2 | 2
3374 | SunWare | SunWare 50/1 | SunWare : SunWare 50/1 | -0.4 | 20.3 | 3.3 | 52 | 16.5 | 3
3375 | SunWare | SunWare 50/T | SunWare : SunWare 50/T | -0.4 | 20.5 | 3.3 | 50 | 16.5 | 3
3376 | SunWare | SunWare 54/1 | SunWare : SunWare 54/1 | -0.4 | 22.5 | 3.3 | 54 | 18.2 | 3
3377 | SunWare | SunWare 54/1 24V | SunWare : SunWare 54/1 24V | -0.4 | 10.2 | 1.65 | 52 | 33 | 1.5
3378 | SunWare | SunWare 54/1 SRM 2 | SunWare : SunWare 54/1 SRM 2 | -0.4 | 20.5 | 3.3 | 52 | 16.5 | 3
3379 | SunWare | SunWare 54/2 | SunWare : SunWare 54/2 | -0.4 | 22.5 | 3.3 | 54 | 18.2 | 3
3380 | SunWare | SunWare 54/2 SRM 2 | SunWare : SunWare 54/2 SRM 2 | -0.4 | 22.5 | 3.3 | 54 | 18.2 | 3
3381 | Sunways | SM210UA61 210Wp | Sunways : SM210UA61 210Wp | -0.32 | 36.4 | 7.99 | 210 | 28.4 | 7.48
3382 | Sunways | SM210UA62 215Wp | Sunways : SM210UA62 215Wp | -0.32 | 36.5 | 8.1 | 215 | 28.6 | 7.6
3383 | Sunways | SM210UA63 220Wp | Sunways : SM210UA63 220Wp | -0.32 | 36.6 | 8.18 | 220 | 28.9 | 7.68
3384 | Sunways | SM210UA64 225Wp | Sunways : SM210UA64 225Wp | -0.32 | 36.7 | 8.29 | 225 | 29.2 | 7.74
3385 | Sunways | SM210UA65 230Wp | Sunways : SM210UA65 230Wp | -0.32 | 36.8 | 8.38 | 230 | 29.5 | 7.8
3386 | Sunways | SM215MA63 225Wp | Sunways : SM215MA63 225Wp | -0.34 | 36.6 | 7.79 | 225 | 28.9 | 7.79
3387 | Sunways | SM215MA64 230Wp | Sunways : SM215MA64 230Wp | -0.34 | 36.6 | 7.9 | 230 | 29.1 | 7.9
3388 | Sunways | SM215MA65 235Wp | Sunways : SM215MA65 235Wp | -0.34 | 36.7 | 8 | 235 | 29.3 | 8
3389 | Sunways | SM215MA66 240Wp | Sunways : SM215MA66 240Wp | -0.34 | 36.8 | 8.13 | 240 | 29.5 | 8.13
3390 | Sunways | SM230MA03 225Wp | Sunways : SM230MA03 225Wp | -0.32 | 59.2 | 5.08 | 225 | 48.6 | 4.63
3391 | Sunways | SM230MA04 235Wp | Sunways : SM230MA04 235Wp | -0.32 | 59.4 | 5.14 | 235 | 48.8 | 4.82
3392 | Sunways | SM230MA10 220Wp | Sunways : SM230MA10 220Wp | -0.32 | 59.1 | 5.07 | 220 | 48.5 | 4.54
3393 | Sunways | SM230MA11 230Wp | Sunways : SM230MA11 230Wp | -0.32 | 59.3 | 5.1 | 230 | 48.7 | 4.73
3394 | Sunways | SM230MA12 240Wp | Sunways : SM230MA12 240Wp | -0.32 | 59.5 | 5.2 | 240 | 48.9 | 4.91
3395 | SunWell Solar | WD-A-CC-0870 | SunWell Solar : WD-A-CC-0870 | -0.3 | 137.5 | 1.2 | 95 | 100 | 0.96
3396 | SunWell Solar | WD-A-CC-0871 | SunWell Solar : WD-A-CC-0871 | -0.3 | 137 | 1.15 | 90 | 100 | 0.9
3397 | SunWell Solar | WD-A-CC-0872 | SunWell Solar : WD-A-CC-0872 | -0.3 | 136 | 1.13 | 85 | 97 | 0.87
3398 | SunWell Solar | WD-A-CC-0873 | SunWell Solar : WD-A-CC-0873 | -0.3 | 135 | 1.12 | 80 | 95 | 0.85
3399 | SunWell Solar | WD-A-CC-087A | SunWell Solar : WD-A-CC-087A | -0.3 | 138 | 1.24 | 100 | 101 | 1.01
3400 | SunWell Solar | WD-A-GE-0656 | SunWell Solar : WD-A-GE-0656 | -0.34 | 53 | 2.83 | 65 | 33 | 2.05
3401 | SunWell Solar | WD-B-GA-0772 | SunWell Solar : WD-B-GA-0772 | -0.34 | 137 | 1.11 | 85 | 103 | 0.85
3402 | SunWell Solar | WD-B-GA-0773 | SunWell Solar : WD-B-GA-0773 | -0.34 | 136 | 1.09 | 80 | 99 | 0.83
3403 | SunWell Solar | WD-B-GA-0774 | SunWell Solar : WD-B-GA-0774 | -0.34 | 135 | 1.08 | 75 | 95 | 0.81
3404 | SunWell Solar | WD-B-GA-0775 | SunWell Solar : WD-B-GA-0775 | -0.34 | 134 | 1.06 | 70 | 93 | 0.78
3405 | SunWell Solar | WD-C-GF-0902 | SunWell Solar : WD-C-GF-0902 | -0.34 | 137 | 1.11 | 85 | 103 | 0.85
3406 | SunWell Solar | WD-C-GF-0903 | SunWell Solar : WD-C-GF-0903 | -0.34 | 136 | 1.09 | 80 | 99 | 0.83
3407 | SunWell Solar | WD-C-GF-0904 | SunWell Solar : WD-C-GF-0904 | -0.34 | 135 | 1.08 | 75 | 95 | 0.81
3408 | SunWell Solar | WD-C-GF-0905 | SunWell Solar : WD-C-GF-0905 | -0.34 | 134 | 1.06 | 70 | 93 | 0.78
3409 | SunWell Solar | WD-EE-CC125C | SunWell Solar : WD-EE-CC125C | -0.4 | 130 | 1.32 | 110 | 100 | 1.12
3410 | SunWell Solar | WD-EE-CC125D | SunWell Solar : WD-EE-CC125D | -0.4 | 128 | 1.35 | 115 | 103 | 1.14
3411 | SunWell Solar | WD-EE-CC125E | SunWell Solar : WD-EE-CC125E | -0.4 | 129 | 1.39 | 120 | 105 | 1.16
3412 | SunWell Solar | WD-EE-CC125F | SunWell Solar : WD-EE-CC125F | -0.4 | 130 | 1.42 | 125 | 107 | 1.18
3413 | Sunworx | SW230P 205Wp | Sunworx : SW230P 205Wp | -0.32 | 35.94 | 7.47 | 205 | 29.5 | 6.95
3414 | Sunworx | SW230P 210Wp | Sunworx : SW230P 210Wp | -0.32 | 35.94 | 7.47 | 210 | 29.6 | 7.1
3415 | Sunworx | SW230P 215Wp | Sunworx : SW230P 215Wp | -0.32 | 36 | 7.72 | 215 | 29.8 | 7.2
3416 | Sunworx | SW230P 220Wp | Sunworx : SW230P 220Wp | -0.32 | 36.1 | 7.95 | 220 | 30 | 7.34
3417 | Sunworx | SW230P 225Wp | Sunworx : SW230P 225Wp | -0.32 | 36.25 | 8.04 | 225 | 30.2 | 7.45
3418 | Sunworx | SW230P 230Wp | Sunworx : SW230P 230Wp | -0.32 | 36.7 | 8.1 | 230 | 30.5 | 7.55
3419 | Sunworx | SW230P 235Wp | Sunworx : SW230P 235Wp | -0.32 | 36.7 | 8.25 | 235 | 30.6 | 7.7
3420 | Svarun | RTM 200Wp | Svarun : RTM 200Wp | -0.3 | 35 | 8.45 | 200 | 26.3 | 7.65
3421 | SWT-Solar | Sun Earth 150W | SWT-Solar : Sun Earth 150W | -0.35 | 43.2 | 5.1 | 150 | 34.2 | 4.39
3422 | SWT-Solar | Sun Earth 160W | SWT-Solar : Sun Earth 160W | -0.35 | 43.4 | 5.19 | 160 | 34.6 | 4.63
3423 | SWT-Solar | Sun Earth 165W | SWT-Solar : Sun Earth 165W | -0.35 | 43.6 | 5.26 | 165 | 34.6 | 4.77
3424 | SWT-Solar | Sun Earth 170W | SWT-Solar : Sun Earth 170W | -0.35 | 44 | 5.32 | 170 | 35 | 4.86
3425 | Symphony | SE-M100 | Symphony : SE-M100 | -0.35 | 28.8 | 4.73 | 80 | 23.5 | 4.26
3426 | Symphony | SE-M121 | Symphony : SE-M121 | -0.35 | 21.6 | 7.35 | 121 | 18 | 6.73
3427 | Symphony | SE-M126 | Symphony : SE-M126 | -0.35 | 22 | 7.63 | 126 | 18.1 | 6.97
3428 | Symphony | SE-M130 | Symphony : SE-M130 | -0.35 | 22.1 | 7.61 | 130 | 18.2 | 7.16
3429 | Symphony | SE-M150 | Symphony : SE-M150 | -0.35 | 43.2 | 4.73 | 150 | 35.3 | 4.26
3430 | Symphony | SE-M181 | Symphony : SE-M181 | -0.35 | 32.4 | 7.35 | 181 | 26.9 | 6.73
3431 | Symphony | SE-M189 | Symphony : SE-M189 | -0.35 | 33 | 7.63 | 189 | 27.1 | 6.97
3432 | Symphony | SE-M194 | Symphony : SE-M194 | -0.35 | 32.6 | 7.89 | 194 | 26.6 | 7.3
3433 | Symphony | SE-M195 | Symphony : SE-M195 | -0.35 | 33.2 | 7.61 | 195 | 27.2 | 7.16
3434 | Symphony | SE-M200 | Symphony : SE-M200 | -0.35 | 32.8 | 7.99 | 200 | 27 | 7.4
3435 | Symphony | SE-M201 | Symphony : SE-M201 | -0.35 | 32.7 | 8.07 | 201 | 27.1 | 7.41
3436 | Symphony | SE-M205 | Symphony : SE-M205 | -0.35 | 33 | 8.12 | 205 | 27.2 | 7.54
3437 | Symphony | SE-M206 | Symphony : SE-M206 | -0.35 | 35.9 | 7.76 | 206 | 29.1 | 7.09
3438 | Symphony | SE-M210 | Symphony : SE-M210 | -0.35 | 33.2 | 8.25 | 210 | 27.3 | 7.68
3439 | Symphony | SE-M210 | Symphony : SE-M210 | -0.35 | 36 | 7.8 | 210 | 29.1 | 7.21
3440 | Symphony | SE-M216 | Symphony : SE-M216 | -0.35 | 36.2 | 7.89 | 216 | 29.6 | 7.3
3441 | Symphony | SE-M222 | Symphony : SE-M222 | -0.35 | 36.5 | 7.99 | 222 | 30 | 7.4
3442 | Symphony | SE-M225 | Symphony : SE-M225 | -0.35 | 36.6 | 8.06 | 225 | 30.2 | 7.44
3443 | Symphony | SE-M228 | Symphony : SE-M228 | -0.35 | 36.7 | 8.12 | 228 | 30.2 | 7.54
3444 | Symphony | SE-M233 | Symphony : SE-M233 | -0.35 | 36.9 | 8.25 | 233 | 30.4 | 7.68
3445 | Symphony | SE-M240 | Symphony : SE-M240 | -0.35 | 36.6 | 8.71 | 240 | 30 | 8.01
3446 | Symphony | SE-M250 | Symphony : SE-M250 | -0.35 | 37 | 8.87 | 250 | 30.7 | 8.14
3447 | Symphony | SE-M80 | Symphony : SE-M80 | -0.35 | 22 | 4.84 | 80 | 17.8 | 4.44
3448 | Symphony | SE-S115 | Symphony : SE-S115 | -0.34 | 30 | 5.1 | 115 | 24.6 | 4.67
3449 | Symphony | SE-S130 | Symphony : SE-S130 | -0.34 | 33.8 | 5.1 | 130 | 27.8 | 4.67
3450 | Symphony | SE-S165 | Symphony : SE-S165 | -0.34 | 43.8 | 4.96 | 165 | 36 | 4.58
3451 | Symphony | SE-S170 | Symphony : SE-S170 | -0.34 | 43.9 | 5.08 | 170 | 36.3 | 4.68
3452 | Symphony | SE-S173 | Symphony : SE-S173 | -0.34 | 43.9 | 5.13 | 173 | 36.6 | 4.73
3453 | Symphony | SE-S176 | Symphony : SE-S176 | -0.34 | 44 | 5.19 | 176 | 36.7 | 4.79
3454 | Symphony | SE-S181 | Symphony : SE-S181 | -0.34 | 44.1 | 5.33 | 181 | 36.6 | 4.94
3455 | Symphony | SE-S185 | Symphony : SE-S185 | -0.34 | 44.1 | 5.46 | 185 | 36.7 | 5.04
3456 | Symphony | SE-S189 | Symphony : SE-S189 | -0.34 | 44.1 | 5.53 | 189 | 36.9 | 5.12
3457 | Symphony | SE-S210 | Symphony : SE-S210 | -0.34 | 47.8 | 5.65 | 210 | 40 | 5.25
3458 | Symphony | SE-S80 | Symphony : SE-S80 | -0.34 | 22 | 4.9 | 80 | 17.8 | 4.52
3459 | Symphony | SE-S82 | Symphony : SE-S82 | -0.34 | 21.9 | 4.96 | 82 | 17.9 | 4.58
3460 | Symphony | SE-S85 | Symphony : SE-S85 | -0.34 | 22 | 5.08 | 85 | 18.2 | 4.68
3461 | Symphony | SE-S88 | Symphony : SE-S88 | -0.34 | 22 | 5.19 | 88 | 18.4 | 4.79
3462 | Symphony | SE-S91 | Symphony : SE-S91 | -0.34 | 22 | 5.33 | 91 | 18.4 | 4.94
3463 | Symphony Energy | SE-M126 | Symphony Energy : SE-M126 | -0.36 | 21.6 | 7.8 | 126 | 17.5 | 7.21
3464 | Symphony Energy | SE-M130 | Symphony Energy : SE-M130 | -0.36 | 21.7 | 7.89 | 130 | 17.8 | 7.3
3465 | Symphony Energy | SE-M135 | Symphony Energy : SE-M135 | -0.36 | 22 | 8.06 | 135 | 18.4 | 7.44
3466 | Symphony Energy | SE-M140 | Symphony Energy : SE-M140 | -0.36 | 22.1 | 8.25 | 140 | 18.2 | 7.68
3467 | Symphony Energy | SE-M181 | Symphony Energy : SE-M181 | -0.36 | 32.4 | 7.35 | 181 | 26.9 | 6.7.
3468 | Symphony Energy | SE-M189 | Symphony Energy : SE-M189 | -0.36 | 32.4 | 7.8 | 189 | 26.2 | 7.21
3469 | Symphony Energy | SE-M194 | Symphony Energy : SE-M194 | -0.36 | 32.6 | 7.89 | 194 | 26.2 | 7.3
3470 | Symphony Energy | SE-M200 | Symphony Energy : SE-M200 | -0.36 | 32.8 | 7.99 | 200 | 27 | 7.4
3471 | Symphony Energy | SE-M205 | Symphony Energy : SE-M205 | -0.36 | 33 | 8.12 | 205 | 27.2 | 7.54
3472 | Symphony Energy | SE-M210 | Symphony Energy : SE-M210 | -0.36 | 33.2 | 8.25 | 210 | 27.3 | 7.68
3473 | Symphony Energy | SE-M215 | Symphony Energy : SE-M215 | -0.36 | 36.2 | 7.89 | 215 | 29.6 | 7.27
3474 | Symphony Energy | SE-M219 | Symphony Energy : SE-M219 | -0.36 | 36.3 | 7.93 | 219 | 29.8 | 7.34
3475 | Symphony Energy | SE-M220 | Symphony Energy : SE-M220 | -0.36 | 36.3 | 7.95 | 220 | 29.8 | 7.39
3476 | Symphony Energy | SE-M222 | Symphony Energy : SE-M222 | -0.36 | 36.5 | 7.99 | 222 | 30 | 7.4
3477 | Symphony Energy | SE-M225 | Symphony Energy : SE-M225 | -0.36 | 36.6 | 8.06 | 225 | 30.2 | 7.44
3478 | Symphony Energy | SE-M228 | Symphony Energy : SE-M228 | -0.36 | 36.7 | 8.12 | 228 | 30.2 | 7.54
3479 | Symphony Energy | SE-M230 | Symphony Energy : SE-M230 | -0.36 | 36.7 | 8.16 | 230 | 30.2 | 7.61
3480 | Symphony Energy | SE-S165 | Symphony Energy : SE-S165 | -0.36 | 43.8 | 4.94 | 165 | 36.2 | 4.56
3481 | Symphony Energy | SE-S170 | Symphony Energy : SE-S170 | -0.36 | 43.9 | 5.06 | 170 | 36.5 | 4.66
3482 | Symphony Energy | SE-S175 | Symphony Energy : SE-S175 | -0.36 | 44 | 5.17 | 175 | 36.7 | 4.77
3483 | Symphony Energy | SE-S180 | Symphony Energy : SE-S180 | -0.36 | 44.1 | 5.31 | 180 | 36.6 | 4.92
3484 | Symphony Energy | SE-S219 | Symphony Energy : SE-S219 | -0.36 | 37 | 8.13 | 219 | 29.2 | 7.5
3485 | Symphony Energy | SE-S222 | Symphony Energy : SE-S222 | -0.36 | 37 | 8.19 | 222 | 29.3 | 7.56
3486 | Symphony Energy | SE-S225 | Symphony Energy : SE-S225 | -0.36 | 37.1 | 8.26 | 225 | 29.6 | 7.6
3487 | Symphony Energy | SE-S228 | Symphony Energy : SE-S228 | -0.36 | 37.1 | 8.32 | 228 | 29.7 | 7.68
3488 | TBEA | 475 | TBEA : 475 | -0.36697 | 21.8 | 4.7 | 75 | 17.4 | 4.3
3489 | TBEA | 480 | TBEA : 480 | -0.36364 | 22 | 5.1 | 80 | 17.2 | 4.7
3490 | TBEA | 485 | TBEA : 485 | -0.36036 | 22.2 | 5.1 | 85 | 17.8 | 4.78
3491 | TBEA | 3210 | TBEA : 3210 | -0.36 | 36.6 | 8.3 | 225 | 29.1 | 7.7
3492 | TBEA | 3220 | TBEA : 3220 | -0.36 | 36.6 | 8.2 | 220 | 28.9 | 7.6
3493 | TBEA | 3225 | TBEA : 3225 | -0.36 | 36.1 | 8.2 | 210 | 28.9 | 7.3
3494 | TBEA | 3230 | TBEA : 3230 | -0.36 | 36.7 | 8.5 | 240 | 29.6 | 8.1
3495 | TBEA | 3235 | TBEA : 3235 | -0.36 | 36.7 | 8.4 | 235 | 29.4 | 8
3496 | TBEA | 3240 | TBEA : 3240 | -0.36 | 36.7 | 8.4 | 230 | 29.1 | 7.9
3497 | TBEA | 4160 | TBEA : 4160 | -0.36 | 44 | 5.1 | 160 | 35.4 | 4.8
3498 | TBEA | 4165 | TBEA : 4165 | -0.36 | 43.7 | 5.4 | 165 | 34.3 | 4.8
3499 | TBEA | 4170 | TBEA : 4170 | -0.36 | 44 | 5.3 | 170 | 35.6 | 4.8
3500 | TBEA | 4175 | TBEA : 4175 | -0.36 | 43.6 | 5.5 | 175 | 35.4 | 4.94
3501 | TBEA | 4180 | TBEA : 4180 | -0.36 | 43.6 | 5.5 | 180 | 35.8 | 5
3502 | TBEA | 4185 | TBEA : 4185 | -0.36 | 44.2 | 5.4 | 185 | 36 | 5.14
3503 | TBEA | 4190 | TBEA : 4190 | -0.36 | 44.8 | 5.5 | 190 | 36.6 | 5.2
3504 | TechnoTherm | TT101 | TechnoTherm : TT101 | -0.144 | 41.2 | 3.4 | 100 | 33.1 | 3.02
3505 | TechnoTherm | TT151 | TechnoTherm : TT151 | -0.152 | 42.2 | 4.95 | 150 | 32.8 | 4.57
3506 | Tegreon | 220P | Tegreon : 220P | -0.33 | 35.9 | 8.13 | 220 | 29.14 | 7.65
3507 | Tegreon | 225P | Tegreon : 225P | -0.33 | 36.21 | 8.22 | 225 | 29.5 | 7.72
3508 | Tegreon | 230P | Tegreon : 230P | -0.33 | 36.4 | 8.33 | 230 | 29.7 | 7.82
3509 | Tegron | Tegron 220P | Tegron : Tegron 220P | -0.34 | 36.23 | 8.15 | 220 | 29.01 | 7.65
3510 | Tegron | Tegron 225P | Tegron : Tegron 225P | -0.34 | 36.43 | 8.24 | 225 | 29.23 | 7.74
3511 | Tegron | Tegron 230P | Tegron : Tegron 230P | -0.34 | 36.66 | 8.34 | 230 | 29.54 | 7.82
3512 | Telecom-STV | TSM-50 | Telecom-STV : TSM-50 | -0.372 | 21.5 | 3.2 | 50 | 17.2 | 3
3513 | Tenesol | TE1300 115Wp Multi | Tenesol : TE1300 115Wp Multi | -0.35 | 21.7 | 7.7 | 115 | 17.5 | 6.7
3514 | Tenesol | TE1300 120Wp Multi | Tenesol : TE1300 120Wp Multi | -0.35 | 21.8 | 7.8 | 120 | 17.6 | 6.9
3515 | Tenesol | TE1300 125Wp Multi | Tenesol : TE1300 125Wp Multi | -0.347 | 21.9 | 7.9 | 125 | 17.7 | 7.2
3516 | Tenesol | TE1300 130Wp Multi | Tenesol : TE1300 130Wp Multi | -0.344 | 22 | 8 | 130 | 17.8 | 7.4
3517 | Tenesol | TE1300 135Wp Multi | Tenesol : TE1300 135Wp Multi | -0.342 | 22.1 | 8.1 | 135 | 17.9 | 7.6
3518 | Tenesol | TE1300 140Wp Multi | Tenesol : TE1300 140Wp Multi | -0.341 | 22.2 | 8.2 | 140 | 18 | 7.8
3519 | Tenesol | TE1700 140Wp Multi | Tenesol : TE1700 140Wp Multi | -0.363 | 42 | 4.5 | 140 | 33.2 | 4.2
3520 | Tenesol | TE1700 150Wp Multi | Tenesol : TE1700 150Wp Multi | -0.358 | 42.6 | 4.7 | 150 | 33.9 | 4.4
3521 | Tenesol | TE1700 160Wp Multi | Tenesol : TE1700 160Wp Multi | -0.353 | 43.2 | 5 | 160 | 34.7 | 4.6
3522 | Tenesol | TE1700 170Wp Multi | Tenesol : TE1700 170Wp Multi | -0.348 | 43.8 | 5.2 | 170 | 35.5 | 4.8
3523 | Tenesol | TE1700 180Wp Multi | Tenesol : TE1700 180Wp Multi | -0.344 | 44.4 | 5.4 | 180 | 36.2 | 5
3524 | Tenesol | TE2000 180Wp Multi | Tenesol : TE2000 180Wp Multi | -0.358 | 32.5 | 7.6 | 180 | 26.3 | 6.9
3525 | Tenesol | TE2000 190Wp Multi | Tenesol : TE2000 190Wp Multi | -0.346 | 32.7 | 7.8 | 190 | 26.5 | 7.2
3526 | Tenesol | TE2000 200Wp Multi | Tenesol : TE2000 200Wp Multi | -0.342 | 32.9 | 8 | 200 | 26.7 | 7.5
3527 | Tenesol | TE2000 210Wp Multi | Tenesol : TE2000 210Wp Multi | -0.341 | 33.1 | 8.2 | 210 | 26.9 | 7.8
3528 | TENESOL | TE2200 (210Wp) | TENESOL : TE2200 (210Wp) | -0.35 | 36.2 | 7.8 | 210 | 29.5 | 7.2
3529 | TENESOL | TE2200 (220Wp) | TENESOL : TE2200 (220Wp) | -0.35 | 36.5 | 8 | 220 | 29.7 | 7.5
3530 | TENESOL | TE2200 (230Wp) | TENESOL : TE2200 (230Wp) | -0.35 | 36.8 | 8.2 | 230 | 29.9 | 7.8
3531 | TENESOL | TE2200 (240Wp) | TENESOL : TE2200 (240Wp) | -0.35 | 37 | 8.3 | 240 | 30.1 | 8
3532 | Tenesol | TE2200 200Wp Multi | Tenesol : TE2200 200Wp Multi | -0.359 | 35.9 | 7.6 | 200 | 29.3 | 6.9
3533 | Tenesol | TE2200 210Wp Multi | Tenesol : TE2200 210Wp Multi | -0.356 | 36.2 | 7.8 | 210 | 29.5 | 7.2
3534 | Tenesol | TE2200 220Wp Multi | Tenesol : TE2200 220Wp Multi | -0.353 | 36.5 | 8 | 220 | 29.7 | 7.5
3535 | Tenesol | TE2200 230Wp Multi | Tenesol : TE2200 230Wp Multi | -0.35 | 36.8 | 8.2 | 230 | 29.9 | 7.8
3536 | Tenesol | TE2200 240Wp Multi | Tenesol : TE2200 240Wp Multi | -0.349 | 37 | 8.3 | 240 | 30.1 | 8
3537 | TerraSolar | DS40 | TerraSolar : DS40 | -0.201 | 62.2 | 1.15 | 40 | 44.8 | 0.9
3538 | TGSolar | HSTAF12-190M48 | TGSolar : HSTAF12-190M48 | -0.36 | 30 | 8.49 | 190 | 24.2 | 7.85
3539 | TGSolar | HSTAF12-195M48 | TGSolar : HSTAF12-195M48 | -0.36 | 30 | 8.49 | 195 | 24.4 | 8
3540 | TGSolar | HSTAF12-210M54 | TGSolar : HSTAF12-210M54 | -0.36 | 33.6 | 8.45 | 210 | 27 | 7.78
3541 | TGSolar | HSTAF12-215M54 | TGSolar : HSTAF12-215M54 | -0.36 | 33.8 | 8.49 | 215 | 27.3 | 7.9
3542 | TGSolar | HSTAF12-220M54 | TGSolar : HSTAF12-220M54 | -0.36 | 33.795 | 8.49 | 220 | 27.5 | 8
3543 | TGSolar | HSTAF24-235M60 | TGSolar : HSTAF24-235M60 | -0.36 | 37.25 | 8.42 | 235 | 30.15 | 7.8
3544 | TGSolar | HSTAF24-240M60 | TGSolar : HSTAF24-240M60 | -0.36 | 37.38 | 8.49 | 240 | 30.6 | 7.85
3545 | TGSolar | HSTAF24-245M60 | TGSolar : HSTAF24-245M60 | -0.36 | 37.55 | 8.6 | 245 | 30.65 | 8
3546 | TGSolar | HSTAF24-280M72 | TGSolar : HSTAF24-280M72 | -0.36 | 44.4 | 8.35 | 280 | 35.8 | 7.83
3547 | TGSolar | HSTAF24-285M72 | TGSolar : HSTAF24-285M72 | -0.36 | 44.5 | 8.49 | 285 | 36 | 7.92
3548 | TGSolar | HSTAF24-290M72 | TGSolar : HSTAF24-290M72 | -0.36 | 44.6 | 8.49 | 290 | 36.5 | 7.95
3549 | TGSolar | HSTAF24-295M72 | TGSolar : HSTAF24-295M72 | -0.36 | 44.6 | 8.49 | 295 | 36.85 | 8.01
3550 | The Sun Factory | TSF115 Black Line | The Sun Factory : TSF115 Black Line | -0.36 | 43.9 | 3.46 | 115 | 36.3 | 3.17
3551 | Thyssen | Solartec 128 W | Thyssen : Solartec 128 W | -0.4 | 47.6 | 4.8 | 128 | 33 | 3.88
3552 | Thyssen | Solartec 28 W | Thyssen : Solartec 28 W | -0.4 | 43.2 | 1.15 | 28 | 30 | 0.93
3553 | Thyssen | Solartec 32 W | Thyssen : Solartec 32 W | -0.4 | 23.8 | 2.4 | 32 | 16.5 | 1.94
3554 | Thyssen | Solartec 64 W, 64 W vertikal | Thyssen : Solartec 64 W, 64 W vertikal | -0.4 | 23.8 | 4.8 | 64 | 16.5 | 3.88
3555 | Thyssen | Solartec-H 1999 | Thyssen : Solartec-H 1999 | -0.4 | 15 | 2.7 | 25 | 11 | 2.7
3556 | Thyssen | Solartec-L 1,40 | Thyssen : Solartec-L 1,40 | -0.4 | 10 | 5.6 | 32 | 7 | 4.6
3557 | Thyssen | Solartec-L 2,60 | Thyssen : Solartec-L 2,60 | -0.4 | 20 | 5.6 | 64 | 14 | 4.6
3558 | TITAN-energy | 160Wp | TITAN-energy : 160Wp | -0.44 | 43 | 5.22 | 160 | 34.2 | 4.71
3559 | TITAN-energy | 170Wp | TITAN-energy : 170Wp | -0.43 | 44.35 | 5.07 | 170 | 36 | 4.73
3560 | TITAN-energy | 180Wp | TITAN-energy : 180Wp | -0.43 | 44.5 | 5.6 | 180 | 36 | 5
3561 | TITAN-energy | 190Wp | TITAN-energy : 190Wp | -0.43 | 44.65 | 5.9 | 190 | 36 | 5.28
3562 | TITAN-energy | 200Wp | TITAN-energy : 200Wp | -0.42 | 44.8 | 6.22 | 200 | 36 | 5.56
3563 | TITAN-energy | 210Wp | TITAN-energy : 210Wp | -0.42 | 45.5 | 6.5 | 210 | 36.5 | 5.75
3564 | TITAN-energy | 220Wp | TITAN-energy : 220Wp | -0.42 | 45.8 | 6.8 | 220 | 37 | 5.94
3565 | TITAN-energy | TITAN-12-100 | TITAN-energy : TITAN-12-100 | -0.38 | 21.3 | 6.4 | 100 | 17.2 | 5.8
3566 | TITAN-energy | TITAN-12-120 | TITAN-energy : TITAN-12-120 | -0.38 | 21.3 | 7.9 | 120 | 17.2 | 6.9
3567 | TITAN-energy | TITAN-12-50 | TITAN-energy : TITAN-12-50 | -0.38 | 21 | 3.2 | 50 | 17.2 | 2.9
3568 | TITAN-energy | TITAN-12-75 | TITAN-energy : TITAN-12-75 | -0.38 | 21 | 4.7 | 75 | 17.2 | 4.3
3569 | TITAN-energy | TITAN-24-100 | TITAN-energy : TITAN-24-100 | -0.38 | 42.5 | 3.2 | 100 | 34.5 | 2.9
3570 | TITAN-energy | TITAN-24-120 | TITAN-energy : TITAN-24-120 | -0.38 | 42.5 | 3.9 | 120 | 34.5 | 3.47
3571 | TITAN-energy | TITAN-TF 32/12 | TITAN-energy : TITAN-TF 32/12 | -0.33 | 22.8 | 2.5 | 32 | 16.8 | 1.92
3572 | TITAN-energy | TITAN-TF 37/12 | TITAN-energy : TITAN-TF 37/12 | -0.33 | 22.8 | 2.5 | 37 | 16.8 | 2.2
3573 | Topray Solar | TPS-113 (40) | Topray Solar : TPS-113 (40) | -0.32 | 61 | 1 | 40 | 46 | 0.87
3574 | Topray Solar | TPS-113 (45) | Topray Solar : TPS-113 (45) | -0.32 | 61 | 1.12 | 45 | 48.9 | 0.92
3575 | Topray Solar | TPS-113 (50) | Topray Solar : TPS-113 (50) | -0.32 | 61 | 1.2 | 50 | 49 | 1.02
3576 | Topray Solar | TPS-113 (55) | Topray Solar : TPS-113 (55) | -0.32 | 61 | 1.24 | 55 | 48.2 | 1.14
3577 | Topray Solar | TPS-113 (60) | Topray Solar : TPS-113 (60) | -0.32 | 61 | 1.26 | 60 | 49.18 | 1.22
3578 | TopSola | TSM96-125M-210Wp | TopSola : TSM96-125M-210Wp | -0.34 | 57.35 | 4.95 | 210 | 45.95 | 4.57
3579 | TopSola | TSM96-125M-220Wp | TopSola : TSM96-125M-220Wp | -0.34 | 57.85 | 5.25 | 220 | 46.35 | 4.75
3580 | TopSola | TSM96-125M-230Wp | TopSola : TSM96-125M-230Wp | -0.34 | 58.05 | 5.4 | 230 | 46.75 | 4.92
3581 | TopSola | TSM96-125M-240Wp | TopSola : TSM96-125M-240Wp | -0.34 | 58.4 | 5.56 | 240 | 47.05 | 5.1
3582 | Total-Energie | TE 1200 (110 W) | Total-Energie : TE 1200 (110 W) | -0.386 | 20.7 | 7.5 | 110 | 16.7 | 6.6
3583 | Total-Energie | TE 1200 (120 W) | Total-Energie : TE 1200 (120 W) | -0.386 | 20.7 | 7.5 | 120 | 16.9 | 7.1
3584 | Total-Energie | TE 1250 Q6/115 | Total-Energie : TE 1250 Q6/115 | -0.344 | 21.9 | 7.1 | 115 | 17.5 | 6.5
3585 | Total-Energie | TE 1250 Q6/120 | Total-Energie : TE 1250 Q6/120 | -0.344 | 22 | 7.3 | 120 | 17.6 | 6.8
3586 | Total-Energie | TE 1250 Q6/125 | Total-Energie : TE 1250 Q6/125 | -0.344 | 22.1 | 7.5 | 125 | 17.8 | 7
3587 | Total-Energie | TE 1250 Q6/130 | Total-Energie : TE 1250 Q6/130 | -0.344 | 22.2 | 7.7 | 130 | 18 | 7.2
3588 | Total-Energie | TE 1300/120 | Total-Energie : TE 1300/120 | -0.34 | 21.8 | 7.5 | 120 | 17.8 | 6.8
3589 | Total-Energie | TE 1300/125 | Total-Energie : TE 1300/125 | -0.34 | 22 | 7.6 | 125 | 17.9 | 7
3590 | Total-Energie | TE 1300/130 | Total-Energie : TE 1300/130 | -0.33 | 22.1 | 7.8 | 130 | 18 | 7.3
3591 | Total-Energie | TE 1300/135 | Total-Energie : TE 1300/135 | -0.33 | 22.3 | 7.9 | 135 | 18.1 | 7.5
3592 | Total-Energie | TE 1300/140 | Total-Energie : TE 1300/140 | -0.33 | 22.4 | 8 | 140 | 18.3 | 7.8
3593 | Total-Energie | TE 1500 (140 W) | Total-Energie : TE 1500 (140 W) | -0.379 | 42.2 | 4.4 | 140 | 33.2 | 4.2
3594 | Total-Energie | TE 1500 (150 W) | Total-Energie : TE 1500 (150 W) | -0.377 | 42.4 | 4.6 | 150 | 33.8 | 4.4
3595 | Total-Energie | TE 1500 (160 W) | Total-Energie : TE 1500 (160 W) | -0.374 | 42.8 | 5.01 | 160 | 34.6 | 4.6
3596 | Total-Energie | TE 1700A1 (180Wp) | Total-Energie : TE 1700A1 (180Wp) | -0.35 | 44.4 | 5.4 | 180 | 36.2 | 5
3597 | Total-Energie | TE 1700A2 (170Wp) | Total-Energie : TE 1700A2 (170Wp) | -0.35 | 43.8 | 5.2 | 170 | 35.5 | 4.8
3598 | Total-Energie | TE 1700A3 (160Wp) | Total-Energie : TE 1700A3 (160Wp) | -0.35 | 43.2 | 5 | 160 | 34.7 | 4.6
3599 | Total-Energie | TE 1800/180 | Total-Energie : TE 1800/180 | -0.35 | 33 | 7.3 | 180 | 26.8 | 6.8
3600 | Total-Energie | TE 1800/190 | Total-Energie : TE 1800/190 | -0.35 | 33.2 | 7.6 | 190 | 27 | 7.1
3601 | Total-Energie | TE 1800/200 | Total-Energie : TE 1800/200 | -0.344 | 33.4 | 7.9 | 200 | 27.2 | 7.4
3602 | Total-Energie | TE 1800/210 | Total-Energie : TE 1800/210 | -0.34 | 33.6 | 8.1 | 210 | 27.3 | 7.7
3603 | Total-Energie | TE 1800A1 (190Wp) | Total-Energie : TE 1800A1 (190Wp) | -0.35 | 33.2 | 7.6 | 190 | 27 | 7.1
3604 | Total-Energie | TE 1800A2 (180Wp) | Total-Energie : TE 1800A2 (180Wp) | -0.35 | 33 | 7.3 | 180 | 26.8 | 6.8
3605 | Total-Energie | TE 1800A3 (170Wp) | Total-Energie : TE 1800A3 (170Wp) | -0.35 | 32.8 | 7 | 170 | 26.6 | 6.4
3606 | Total-Energie | TE 2000/170 Polykristallin | Total-Energie : TE 2000/170 Polykristallin | -0.35 | 32.6 | 7.4 | 170 | 16.4 | 6.5
3607 | Total-Energie | TE 2000/180 Polykristallin | Total-Energie : TE 2000/180 Polykristallin | -0.35 | 32.8 | 7.6 | 180 | 26.6 | 6.8
3608 | Total-Energie | TE 2000/190 Monokristallin | Total-Energie : TE 2000/190 Monokristallin | -0.34 | 33.4 | 7.8 | 190 | 27 | 7.2
3609 | Total-Energie | TE 2000/190 Polykristallin | Total-Energie : TE 2000/190 Polykristallin | -0.346 | 33.1 | 7.7 | 190 | 26.8 | 7.1
3610 | Total-Energie | TE 2000/200 Monokristallin | Total-Energie : TE 2000/200 Monokristallin | -0.34 | 33.5 | 8 | 200 | 27.2 | 7.5
3611 | Total-Energie | TE 2000/200 Polykristallin | Total-Energie : TE 2000/200 Polykristallin | -0.346 | 33.4 | 7.9 | 200 | 27.1 | 7.4
3612 | Total-Energie | TE 2000/210 Monokristallin | Total-Energie : TE 2000/210 Monokristallin | -0.34 | 33.6 | 8.1 | 210 | 27.4 | 7.8
3613 | Total-Energie | TE 2000-210 Polykristallin | Total-Energie : TE 2000-210 Polykristallin | -0.346 | 33.6 | 8 | 210 | 27.3 | 7.7
3614 | Total-Energie | TE 500/60 | Total-Energie : TE 500/60 | -0.35 | 22.5 | 3.7 | 60 | 17.9 | 3.35
3615 | Total-Energie | TE 750 (70 W) | Total-Energie : TE 750 (70 W) | -0.379 | 21.1 | 4.4 | 70 | 16.6 | 4.2
3616 | Total-Energie | TE 750 (75 W) | Total-Energie : TE 750 (75 W) | -0.379 | 21.1 | 4.55 | 75 | 16.9 | 4.4
3617 | Total-Energie | TE 750 (80 W) | Total-Energie : TE 750 (80 W) | -0.374 | 21.4 | 5 | 80 | 17.3 | 4.6
3618 | Total-Energie | TE 850/80 | Total-Energie : TE 850/80 | -0.349 | 21.8 | 5 | 80 | 17.3 | 4.6
3619 | Total-Energie | TE 850/85 | Total-Energie : TE 850/85 | -0.349 | 22 | 5.2 | 85 | 17.7 | 4.8
3620 | Total-Energie | TE1500 Q/165 | Total-Energie : TE1500 Q/165 | -0.352 | 43.2 | 5.1 | 165 | 34.9 | 4.7
3621 | Total-Energie | TE1500 Q/170 | Total-Energie : TE1500 Q/170 | -0.352 | 43.5 | 5.3 | 170 | 35.3 | 4.8
3622 | Total-Energie | TE1500 Q/175 | Total-Energie : TE1500 Q/175 | -0.352 | 43.8 | 5.3 | 175 | 35.7 | 4.9
3623 | Total-Energie | TE1500 Q/180 | Total-Energie : TE1500 Q/180 | -0.352 | 44.1 | 5.4 | 180 | 36.1 | 5
3624 | Traxle | TXL120 (120Wp) | Traxle : TXL120 (120Wp) | -0.38 | 22 | 7.8 | 120 | 17.5 | 6.9
3625 | Traxle | TXL160 (160Wp) | Traxle : TXL160 (160Wp) | -0.38 | 43.8 | 5.08 | 160 | 35.6 | 4.5
3626 | Trienergia | COE-170M | Trienergia : COE-170M | -0.21 | 43.2 | 5.4 | 170 | 35.41 | 4.8
3627 | Trienergia | COE-180M | Trienergia : COE-180M | -0.21 | 44.28 | 5.6 | 180 | 35.65 | 4.8
3628 | Trienergia | COE-85M | Trienergia : COE-85M | -0.11 | 21.6 | 5.4 | 85 | 17.71 | 4.8
3629 | Trienergia | COE-90M | Trienergia : COE-90M | -0.11 | 22.14 | 5.6 | 90 | 17.83 | 5.05
3630 | Trina Solar | TSM-160D | Trina Solar : TSM-160D | -0.34 | 44.2 | 4.76 | 160 | 36.3 | 4.41
3631 | Trina Solar | TSM-160P | Trina Solar : TSM-160P | -0.38 | 43.2 | 4.91 | 160 | 35.55 | 4.5
3632 | Trina Solar | TSM-165D 48 Cells | Trina Solar : TSM-165D 48 Cells | -0.34 | 29 | 7.79 | 165 | 23.5 | 7.02
3633 | Trina Solar | TSM-165D 72Cells | Trina Solar : TSM-165D 72Cells | -0.34 | 43.34 | 4.8 | 165 | 36.3 | 4.55
3634 | Trina Solar | TSM-165P 48 Cells | Trina Solar : TSM-165P 48 Cells | -0.38 | 28.5 | 7.75 | 165 | 23.6 | 6.99
3635 | Trina Solar | TSM-165P 72 Cells | Trina Solar : TSM-165P 72 Cells | -0.38 | 43.34 | 5 | 165 | 36 | 4.58
3636 | Trina Solar | TSM-170D 48 Cells | Trina Solar : TSM-170D 48 Cells | -0.34 | 29 | 7.88 | 170 | 23.5 | 7.23
3637 | Trina Solar | TSM-170D 72Cells | Trina Solar : TSM-170D 72Cells | -0.34 | 44.42 | 4.88 | 170 | 37.02 | 4.59
3638 | Trina Solar | TSM-170P 48 Cells | Trina Solar : TSM-170P 48 Cells | -0.38 | 28.5 | 7.86 | 170 | 23.6 | 7.2
3639 | Trina Solar | TSM-170P 72 Cells | Trina Solar : TSM-170P 72 Cells | -0.38 | 43.48 | 5.07 | 170 | 36.14 | 4.7
3640 | Trina Solar | TSM-175D | Trina Solar : TSM-175D | -0.34 | 43.58 | 4.97 | 175 | 37.02 | 4.73
3641 | Trina Solar | TSM-175P | Trina Solar : TSM-175P | -0.38 | 43.58 | 5.15 | 175 | 36.5 | 4.79
3642 | Trina Solar | TSM-180D | Trina Solar : TSM-180D | -0.34 | 44.06 | 5.08 | 180 | 37.02 | 4.86
3643 | Trina Solar | TSM-75D | Trina Solar : TSM-75D | -0.34 | 21.72 | 4.62 | 75 | 17.8 | 4.21
3644 | Trina Solar | TSM-75P | Trina Solar : TSM-75P | -0.38 | 21.56 | 4.82 | 75 | 17.75 | 4.23
3645 | Trina Solar | TSM-80D | Trina Solar : TSM-80D | -0.34 | 22.1 | 4.76 | 80 | 18.15 | 4.41
3646 | Trina Solar | TSM-80P | Trina Solar : TSM-80P | -0.38 | 22.6 | 4.91 | 80 | 17.75 | 4.51
3647 | Trina Solar | TSM-85D | Trina Solar : TSM-85D | -0.34 | 22.21 | 4.88 | 85 | 18.51 | 4.59
3648 | Trina Solar | TSM-85P | Trina Solar : TSM-85P | -0.38 | 21.74 | 5.07 | 85 | 18.07 | 4.7
3649 | Trina Solar | TSM-DC01 165Wp | Trina Solar : TSM-DC01 165Wp | -0.35 | 43.2 | 5.2 | 165 | 35.6 | 4.65
3650 | Trina Solar | TSM-DC01 170Wp | Trina Solar : TSM-DC01 170Wp | -0.35 | 43.6 | 5.25 | 170 | 35.8 | 4.76
3651 | Trina Solar | TSM-DC01 175Wp | Trina Solar : TSM-DC01 175Wp | -0.35 | 43.9 | 5.3 | 175 | 36.2 | 4.85
3652 | Trina Solar | TSM-DC01 180Wp | Trina Solar : TSM-DC01 180Wp | -0.35 | 44.2 | 5.35 | 180 | 36.8 | 4.9
3653 | Trina Solar | TSM-DC01 Black 170Wp | Trina Solar : TSM-DC01 Black 170Wp | -0.35 | 43.6 | 5.25 | 170 | 35.8 | 4.76
3654 | Trina Solar | TSM-DC01 Black 175Wp | Trina Solar : TSM-DC01 Black 175Wp | -0.35 | 43.9 | 5.3 | 175 | 36.2 | 4.85
3655 | Trina Solar | TSM-DC01 Black 180Wp | Trina Solar : TSM-DC01 Black 180Wp | -0.35 | 44.2 | 5.35 | 180 | 36.8 | 4.9
3656 | Trina Solar | TSM-DC01 Black 185Wp | Trina Solar : TSM-DC01 Black 185Wp | -0.35 | 44.5 | 5.4 | 185 | 37.5 | 4.95
3657 | Trina Solar | TSM-DC03/PC03 165Wp | Trina Solar : TSM-DC03/PC03 165Wp | -0.35 | 29 | 7.6 | 165 | 23.8 | 6.95
3658 | Trina Solar | TSM-DC03/PC03 170Wp | Trina Solar : TSM-DC03/PC03 170Wp | -0.35 | 29.2 | 7.72 | 170 | 24 | 7.1
3659 | Trina Solar | TSM-DC03/PC03 175Wp | Trina Solar : TSM-DC03/PC03 175Wp | -0.35 | 29.4 | 7.82 | 175 | 24.2 | 7.25
3660 | Trina Solar | TSM-DC03/PC03 180Wp | Trina Solar : TSM-DC03/PC03 180Wp | -0.35 | 29.6 | 7.95 | 180 | 24.4 | 7.38
3661 | Trina Solar | TSM-DC03/PC03 185Wp | Trina Solar : TSM-DC03/PC03 185Wp | -0.35 | 29.8 | 8.08 | 185 | 24.7 | 7.5
3662 | Trina Solar | TSM-DC05/PC05 200Wp | Trina Solar : TSM-DC05/PC05 200Wp | -0.35 | 36 | 7.75 | 200 | 28.7 | 6.97
3663 | Trina Solar | TSM-DC05/PC05 210Wp | Trina Solar : TSM-DC05/PC05 210Wp | -0.35 | 36.4 | 7.86 | 210 | 29.2 | 7.19
3664 | Trina Solar | TSM-DC05/PC05 220Wp | Trina Solar : TSM-DC05/PC05 220Wp | -0.35 | 36.8 | 8 | 220 | 29.8 | 7.39
3665 | Trina Solar | TSM-DC05/PC05 230Wp | Trina Solar : TSM-DC05/PC05 230Wp | -0.35 | 37 | 8.18 | 230 | 30 | 7.66
3666 | Trina Solar | TSM-DC05/PC05 240Wp | Trina Solar : TSM-DC05/PC05 240Wp | -0.35 | 37.5 | 8.38 | 240 | 30.6 | 7.84
3667 | Trina Solar | TSM-PC05 Black 215Wp | Trina Solar : TSM-PC05 Black 215Wp | -0.35 | 36.4 | 8.13 | 215 | 28.5 | 7.55
3668 | Trina Solar | TSM-PC05 Black 220Wp | Trina Solar : TSM-PC05 Black 220Wp | -0.35 | 36.8 | 8.15 | 220 | 29 | 7.6
3669 | Trina Solar | TSM-PC05 Black 225Wp | Trina Solar : TSM-PC05 Black 225Wp | -0.35 | 36.9 | 8.2 | 225 | 29.4 | 7.66
3670 | Trina Solar | TSM-PC05 Black 230Wp | Trina Solar : TSM-PC05 Black 230Wp | -0.35 | 37 | 8.26 | 230 | 29.8 | 7.72
3671 | Trina Solar | TSM-PC05 Black 235Wp | Trina Solar : TSM-PC05 Black 235Wp | -0.35 | 37.1 | 8.31 | 235 | 30.1 | 7.81
3672 | Trina Solar | TSM-PC14 265Wp | Trina Solar : TSM-PC14 265Wp | -0.35 | 44.2 | 8.2 | 265 | 35.33 | 7.5
3673 | Trina Solar | TSM-PC14 270Wp | Trina Solar : TSM-PC14 270Wp | -0.35 | 44.34 | 8.29 | 270 | 35.52 | 7.6
3674 | Trina Solar | TSM-PC14 275Wp | Trina Solar : TSM-PC14 275Wp | -0.35 | 44.4 | 8.39 | 275 | 35.85 | 7.68
3675 | Trina Solar | TSM-PC14 280Wp | Trina Solar : TSM-PC14 280Wp | -0.35 | 44.44 | 8.45 | 280 | 36.01 | 7.78
3676 | Trina Solar | TSM-PC14 285Wp | Trina Solar : TSM-PC14 285Wp | -0.35 | 44.5 | 8.49 | 285 | 36.25 | 7.86
3677 | Trina Solar | TSM-PC14 290Wp | Trina Solar : TSM-PC14 290Wp | -0.35 | 44.55 | 8.52 | 290 | 36.48 | 7.95
3678 | Tynsolar | TYN-126P6 120W | Tynsolar : TYN-126P6 120W | -0.37 | 21.53 | 7.35 | 120 | 17.57 | 6.83
3679 | Tynsolar | TYN-126P6 125W | Tynsolar : TYN-126P6 125W | -0.37 | 21.56 | 7.6 | 125 | 17.78 | 7.03
3680 | Tynsolar | TYN-126P6 130W | Tynsolar : TYN-126P6 130W | -0.37 | 21.6 | 7.83 | 130 | 17.96 | 7.24
3681 | Tynsolar | TYN-126P6 135W | Tynsolar : TYN-126P6 135W | -0.37 | 21.74 | 8.04 | 135 | 18.14 | 7.44
3682 | Tynsolar | TYN-126P6 140W | Tynsolar : TYN-126P6 140W | -0.37 | 22.03 | 8.23 | 140 | 18.36 | 7.63
3683 | Tynsolar | TYN-168P6 155W | Tynsolar : TYN-168P6 155W | -0.37 | 28.7 | 7.24 | 155 | 22.94 | 6.76
3684 | Tynsolar | TYN-168P6 160W | Tynsolar : TYN-168P6 160W | -0.37 | 28.7 | 7.35 | 160 | 23.42 | 6.83
3685 | Tynsolar | TYN-168P6 165W | Tynsolar : TYN-168P6 165W | -0.37 | 28.75 | 7.47 | 165 | 23.66 | 6.97
3686 | Tynsolar | TYN-168P6 170W | Tynsolar : TYN-168P6 170W | -0.37 | 28.8 | 7.72 | 170 | 23.8 | 7.14
3687 | Tynsolar | TYN-170P5 160Wp | Tynsolar : TYN-170P5 160Wp | -0.37 | 42.91 | 4.93 | 160 | 35.5 | 4.51
3688 | Tynsolar | TYN-170P5 165Wp | Tynsolar : TYN-170P5 165Wp | -0.37 | 43.49 | 5.03 | 165 | 35.93 | 4.59
3689 | Tynsolar | TYN-170P5 170Wp | Tynsolar : TYN-170P5 170Wp | -0.37 | 43.56 | 5.07 | 170 | 36.14 | 4.7
3690 | Tynsolar | TYN-170P5 175Wp | Tynsolar : TYN-170P5 175Wp | -0.37 | 43.63 | 5.15 | 175 | 36.43 | 4.8
3691 | Tynsolar | TYN-170P5 180Wp | Tynsolar : TYN-170P5 180Wp | -0.37 | 43.78 | 5.23 | 180 | 36.86 | 4.88
3692 | Tynsolar | TYN-170S5 150Wp | Tynsolar : TYN-170S5 150Wp | -0.37 | 43.49 | 4.79 | 150 | 35.42 | 4.24
3693 | Tynsolar | TYN-170S5 155Wp | Tynsolar : TYN-170S5 155Wp | -0.37 | 43.49 | 4.79 | 155 | 35.42 | 4.38
3694 | Tynsolar | TYN-170S5 160Wp | Tynsolar : TYN-170S5 160Wp | -0.37 | 43.63 | 4.84 | 160 | 35.86 | 4.46
3695 | Tynsolar | TYN-170S5 165Wp | Tynsolar : TYN-170S5 165Wp | -0.37 | 43.78 | 4.94 | 165 | 36.14 | 4.57
3696 | Tynsolar | TYN-170S5 170Wp | Tynsolar : TYN-170S5 170Wp | -0.37 | 43.92 | 5.06 | 170 | 36.43 | 4.67
3697 | Tynsolar | TYN-180P6 175Wp | Tynsolar : TYN-180P6 175Wp | -0.37 | 28.85 | 7.95 | 175 | 24.1 | 7.26
3698 | Tynsolar | TYN-180P6 180Wp | Tynsolar : TYN-180P6 180Wp | -0.37 | 29.14 | 8.1 | 180 | 24.29 | 7.41
3699 | Tynsolar | TYN-180P6 185Wp | Tynsolar : TYN-180P6 185Wp | -0.37 | 29.38 | 8.23 | 185 | 24.48 | 7.56
3700 | Tynsolar | TYN-180P6 190Wp | Tynsolar : TYN-180P6 190Wp | -0.37 | 29.47 | 8.32 | 190 | 24.53 | 7.75
3701 | Tynsolar | TYN-180S5 175Wp | Tynsolar : TYN-180S5 175Wp | -0.37 | 43.99 | 5.17 | 175 | 36.72 | 4.77
3702 | Tynsolar | TYN-180S5 180Wp | Tynsolar : TYN-180S5 180Wp | -0.37 | 44.06 | 5.31 | 180 | 36.72 | 4.9
3703 | Tynsolar | TYN-180S5 185Wp | Tynsolar : TYN-180S5 185Wp | -0.37 | 44.14 | 5.43 | 185 | 36.79 | 5.03
3704 | Tynsolar | TYN-220P6 205Wp | Tynsolar : TYN-220P6 205Wp | -0.37 | 35.94 | 7.47 | 205 | 29.58 | 6.93
3705 | Tynsolar | TYN-220P6 210Wp | Tynsolar : TYN-220P6 210Wp | -0.37 | 35.94 | 7.6 | 210 | 29.64 | 7.09
3706 | Tynsolar | TYN-220P6 215Wp | Tynsolar : TYN-220P6 215Wp | -0.37 | 36 | 7.83 | 215 | 29.94 | 7.18
3707 | Tynsolar | TYN-220P6 220Wp | Tynsolar : TYN-220P6 220Wp | -0.37 | 36.06 | 7.95 | 220 | 30.12 | 7.3
3708 | Tynsolar | TYN-220P6 225Wp | Tynsolar : TYN-220P6 225Wp | -0.37 | 36.42 | 8.1 | 225 | 30.36 | 7.41
3709 | Tynsolar | TYN-220P6 230Wp | Tynsolar : TYN-220P6 230Wp | -0.37 | 36.6 | 8.17 | 230 | 30.48 | 7.55
3710 | Tynsolar | TYN-220P6 235Wp | Tynsolar : TYN-220P6 235Wp | -0.37 | 36.72 | 8.23 | 235 | 30.6 | 7.68
3711 | Tynsolar | TYN-270P6 260Wp | Tynsolar : TYN-270P6 260Wp | -0.37 | 43.2 | 7.83 | 260 | 35.93 | 7.24
3712 | Tynsolar | TYN-270P6 265Wp | Tynsolar : TYN-270P6 265Wp | -0.37 | 43.27 | 7.95 | 265 | 36.14 | 7.33
3713 | Tynsolar | TYN-270P6 270Wp | Tynsolar : TYN-270P6 270Wp | -0.37 | 43.7 | 8.1 | 270 | 36.43 | 7.41
3714 | Tynsolar | TYN-270P6 275Wp | Tynsolar : TYN-270P6 275Wp | -0.37 | 43.92 | 8.17 | 275 | 36.58 | 7.52
3715 | Tynsolar | TYN-85S5 75W | Tynsolar : TYN-85S5 75W | -0.37 | 21.74 | 4.79 | 75 | 17.71 | 4.24
3716 | Tynsolar | TYN-85S5 80W | Tynsolar : TYN-85S5 80W | -0.37 | 21.82 | 4.84 | 80 | 17.93 | 4.46
3717 | Tynsolar | TYN-85S5 85W | Tynsolar : TYN-85S5 85W | -0.37 | 21.96 | 5.06 | 85 | 18.22 | 4.67
3718 | Tynsolar | TYN-85S5 90W | Tynsolar : TYN-85S5 90W | -0.37 | 22.03 | 5.31 | 90 | 18.36 | 4.9
3719 | UBBINK Solar | Atdium 150WP | UBBINK Solar : Atdium 150WP | -0.35 | 29.9 | 7.7 | 150 | 21.8 | 6.9
3720 | UBBINK Solar | Atdium 155WP | UBBINK Solar : Atdium 155WP | -0.35 | 29.9 | 7.75 | 155 | 21.8 | 7.1
3721 | UBBINK Solar | Atdium 160WP | UBBINK Solar : Atdium 160WP | -0.35 | 30 | 7.8 | 160 | 21.9 | 7.3
3722 | UBBINK Solar | Atrium 165Wp | UBBINK Solar : Atrium 165Wp | -0.35 | 30 | 7.85 | 165 | 22.5 | 7.4
3723 | UBBINK Solar | Atrium 170Wp | UBBINK Solar : Atrium 170Wp | -0.349 | 30.1 | 7.9 | 170 | 22.6 | 7.5
3724 | UBBINK Solar | Atrium 175Wp | UBBINK Solar : Atrium 175Wp | -0.348 | 30.2 | 7.95 | 175 | 22.8 | 7.7
3725 | UBBINK Solar | Atrium 180Wp | UBBINK Solar : Atrium 180Wp | -0.347 | 30.3 | 8 | 180 | 23.1 | 7.8
3726 | UBBINK Solar | Atrium 185Wp | UBBINK Solar : Atrium 185Wp | -0.345 | 30.4 | 8.05 | 185 | 23.3 | 7.94
3727 | UBBINK Solar | Atrium 190Wp | UBBINK Solar : Atrium 190Wp | -0.344 | 30.5 | 8.15 | 190 | 23.7 | 8
3728 | UBBINK Solar | Atrium 200Wp | UBBINK Solar : Atrium 200Wp | -0.3219 | 35.8 | 7.9 | 200 | 28 | 7.2
3729 | UBBINK Solar | Atrium 205Wp | UBBINK Solar : Atrium 205Wp | -0.349 | 36.1 | 8 | 205 | 28.7 | 7.3
3730 | UBBINK Solar | Atrium 210Wp | UBBINK Solar : Atrium 210Wp | -0.348 | 36.2 | 8.1 | 210 | 28.8 | 7.3
3731 | UBBINK Solar | Atrium 215Wp | UBBINK Solar : Atrium 215Wp | -0.347 | 36.3 | 8.2 | 215 | 28.9 | 7.45
3732 | UBBINK Solar | Atrium 220Wp | UBBINK Solar : Atrium 220Wp | -0.347 | 36.3 | 8.3 | 220 | 28.8 | 7.65
3733 | UBBINK Solar | Atrium 225Wp | UBBINK Solar : Atrium 225Wp | -0.346 | 36.4 | 8.3 | 225 | 28.9 | 7.8
3734 | UBBINK Solar | Atrium 230Wp | UBBINK Solar : Atrium 230Wp | -0.344 | 36.6 | 8.4 | 230 | 28.9 | 8
3735 | UBBINK Solar | Atrium 235Wp | UBBINK Solar : Atrium 235Wp | -0.342 | 36.8 | 8.5 | 235 | 28.9 | 8.2
3736 | UBBINK Solar | Atrium 240Wp | UBBINK Solar : Atrium 240Wp | -0.341 | 37 | 8.7 | 240 | 28.9 | 8.3
3737 | Uni-Solar | PVL-144 | Uni-Solar : PVL-144 | -0.38 | 46.2 | 5.3 | 144 | 33 | 4.36
3738 | Unisolar / Bekaert | ASR-120 | Unisolar / Bekaert : ASR-120 | -0.4 | 47.6 | 4.5 | 120 | 33 | 3.6
3739 | Unisolar / Bekaert | ASR-128 | Unisolar / Bekaert : ASR-128 | -0.4 | 47.6 | 4.8 | 128 | 33 | 3.9
3740 | Unisolar / Bekaert | ASR-60 | Unisolar / Bekaert : ASR-60 | -0.4 | 23.8 | 4.5 | 60 | 16.5 | 3.6
3741 | Unisolar / Bekaert | ASR-64 | Unisolar / Bekaert : ASR-64 | -0.4 | 23.8 | 4.8 | 64 | 16.5 | 3.9
3742 | Unisolar / Bekaert | LM-21 | Unisolar / Bekaert : LM-21 | -0.4 | 23.8 | 1.59 | 21 | 16.5 | 1.27
3743 | Unisolar / Bekaert | LM-3 | Unisolar / Bekaert : LM-3 | -0.4 | 12 | 0.35 | 2.5 | 9 | 0.28
3744 | Unisolar / Bekaert | LM-5 | Unisolar / Bekaert : LM-5 | -0.4 | 23.8 | 0.37 | 5 | 16.5 | 0.3
3745 | Unisolar / Bekaert | PVL-116T | Unisolar / Bekaert : PVL-116T | -0.4 | 43.2 | 4.8 | 116 | 30 | 3.88
3746 | Unisolar / Bekaert | PVL-128T | Unisolar / Bekaert : PVL-128T | -0.4 | 47.6 | 4.8 | 128 | 33 | 3.88
3747 | Unisolar / Bekaert | PVL-136 | Unisolar / Bekaert : PVL-136 | -0.39 | 46.2 | 5.1 | 136 | 33 | 4.13
3748 | Unisolar / Bekaert | PVL-29T | Unisolar / Bekaert : PVL-29T | -0.4 | 10.8 | 4.8 | 29 | 6 | 3.88
3749 | Unisolar / Bekaert | PVL-58T | Unisolar / Bekaert : PVL-58T | -0.4 | 21.6 | 4.8 | 58 | 15 | 3.88
3750 | Unisolar / Bekaert | PVL-64T | Unisolar / Bekaert : PVL-64T | -0.4 | 23.8 | 4.8 | 64 | 16.5 | 3.88
3751 | Unisolar / Bekaert | PVL-68 | Unisolar / Bekaert : PVL-68 | -0.39 | 23.1 | 5.1 | 68 | 16.5 | 4.13
3752 | Unisolar / Bekaert | PVL-87T | Unisolar / Bekaert : PVL-87T | -0.4 | 32.4 | 4.8 | 87 | 22.5 | 3.88
3753 | Unisolar / Bekaert | S4 LM3 | Unisolar / Bekaert : S4 LM3 | -0.4 | 24 | 0.8 | 10.7 | 16.2 | 0.66
3754 | Unisolar / Bekaert | SSR-120 | Unisolar / Bekaert : SSR-120 | -0.4 | 47.6 | 4.5 | 120 | 33 | 3.6
3755 | Unisolar / Bekaert | SSR-60 | Unisolar / Bekaert : SSR-60 | -0.4 | 23.8 | 4.5 | 60 | 16.5 | 3.6
3756 | Unisolar / Bekaert | Uni-Solar 11-L-B / 11-L-T | Unisolar / Bekaert : Uni-Solar 11-L-B / 11-L-T | -0.4 | 23.8 | 4.8 | 64 | 16.5 | 3.9
3757 | Unisolar / Bekaert | Uni-Solar 22-L-B / 22-L-T | Unisolar / Bekaert : Uni-Solar 22-L-B / 22-L-T | -0.4 | 47.6 | 4.8 | 128 | 33 | 3.9
3758 | Unisolar / Bekaert | Uni-Solar SHR-17 | Unisolar / Bekaert : Uni-Solar SHR-17 | -0.4 | 12 | 2.5 | 17 | 8.6 | 2
3759 | Unisolar / Bekaert | Uni-Solar SSR-128 | Unisolar / Bekaert : Uni-Solar SSR-128 | -0.4 | 47.6 | 4.8 | 128 | 33 | 3.9
3760 | Unisolar / Bekaert | Uni-Solar SSR-256 | Unisolar / Bekaert : Uni-Solar SSR-256 | -0.4 | 95.2 | 4.8 | 256 | 66 | 3.9
3761 | Unisolar / Bekaert | Uni-Solar SSR-64 | Unisolar / Bekaert : Uni-Solar SSR-64 | -0.4 | 23.8 | 4.8 | 64 | 16.5 | 3.9
3762 | Unisolar / Bekaert | Uni-Solar Unipac 10 | Unisolar / Bekaert : Uni-Solar Unipac 10 | -0.4 | 26 | 0.74 | 10.5 | 17.6 | 0.6
3763 | Unisolar / Bekaert | Uni-Solar Unipac 15 | Unisolar / Bekaert : Uni-Solar Unipac 15 | -0.4 | 26 | 1.11 | 15.8 | 17.6 | 0.9
3764 | Unisolar / Bekaert | Uni-Solar Unipac 30 | Unisolar / Bekaert : Uni-Solar Unipac 30 | -0.4 | 26 | 2.1 | 30 | 17.6 | 1.7
3765 | Unisolar / Bekaert | Uni-Solar US-11 | Unisolar / Bekaert : Uni-Solar US-11 | -0.4 | 23.8 | 0.78 | 10.3 | 16.5 | 0.62
3766 | Unisolar / Bekaert | Uni-Solar US-116 | Unisolar / Bekaert : Uni-Solar US-116 | -0.4 | 43.2 | 4.8 | 116 | 30 | 3.88
3767 | Unisolar / Bekaert | Uni-Solar US-21 | Unisolar / Bekaert : Uni-Solar US-21 | -0.4 | 23.8 | 1.59 | 21 | 16.5 | 1.27
3768 | Unisolar / Bekaert | Uni-Solar US-3 | Unisolar / Bekaert : Uni-Solar US-3 | -0.4 | 12 | 0.4 | 2.68 | 8.1 | 0.33
3769 | Unisolar / Bekaert | Uni-Solar US-32 | Unisolar / Bekaert : Uni-Solar US-32 | -0.4 | 23.8 | 2.4 | 32 | 16.5 | 1.94
3770 | Unisolar / Bekaert | Uni-Solar US-42 | Unisolar / Bekaert : Uni-Solar US-42 | -0.4 | 23.8 | 3.17 | 42 | 16.5 | 2.54
3771 | Unisolar / Bekaert | Uni-Solar US-5 | Unisolar / Bekaert : Uni-Solar US-5 | -0.4 | 23.8 | 0.37 | 5 | 16.5 | 0.3
3772 | Unisolar / Bekaert | Uni-Solar US-64 | Unisolar / Bekaert : Uni-Solar US-64 | -0.4 | 23.8 | 4.8 | 64 | 16.5 | 3.88
3773 | Unisolar / Bekaert | Uni-Solar USF-11 | Unisolar / Bekaert : Uni-Solar USF-11 | -0.4 | 23.8 | 0.78 | 10.3 | 16.5 | 0.62
3774 | Unisolar / Bekaert | Uni-Solar USF-32 | Unisolar / Bekaert : Uni-Solar USF-32 | -0.4 | 23.8 | 2.4 | 32 | 16.5 | 1.94
3775 | Unisolar / Bekaert | Uni-Solar USF-5 | Unisolar / Bekaert : Uni-Solar USF-5 | -0.4 | 23.8 | 0.37 | 5 | 16.5 | 0.3
3776 | Upsolar | UP-M165M | Upsolar : UP-M165M | -0.32 | 44 | 5.03 | 165 | 35.2 | 4.69
3777 | Upsolar | UP-M170M | Upsolar : UP-M170M | -0.32 | 44.2 | 5.19 | 170 | 35.4 | 4.81
3778 | Upsolar | UP-M175M | Upsolar : UP-M175M | -0.32 | 44.4 | 5.29 | 175 | 35.6 | 4.92
3779 | Upsolar | UP-M180M | Upsolar : UP-M180M | -0.32 | 44.6 | 5.38 | 180 | 35.8 | 5.03
3780 | Upsolar | UP-M185M | Upsolar : UP-M185M | -0.32 | 44.8 | 5.43 | 185 | 36 | 5.14
3781 | Upsolar | UP-M190M | Upsolar : UP-M190M | -0.32 | 45.1 | 5.55 | 190 | 36.3 | 5.23
3782 | Upsolar | UP-M210P | Upsolar : UP-M210P | -0.32 | 36.1 | 8.1 | 210 | 28.2 | 7.45
3783 | Upsolar | UP-M220P | Upsolar : UP-M220P | -0.32 | 36.7 | 8.25 | 220 | 28.7 | 7.67
3784 | Upsolar | UP-M230P | Upsolar : UP-M230P | -0.32 | 37.2 | 8.3 | 230 | 29.7 | 7.75
3785 | Upsolar | UP-M240P | Upsolar : UP-M240P | -0.32 | 37.6 | 8.4 | 240 | 30.2 | 7.95
3786 | Usha | 10 W Module | Usha : 10 W Module | -0.4 | 21 | 0.7 | 10 | 16.4 | 0.61
3787 | Usha | 37 W Module | Usha : 37 W Module | -0.4 | 21 | 2.4 | 37 | 16.4 | 2.25
3788 | Van de Loo | Disol DSM-10/10 L | Van de Loo : Disol DSM-10/10 L | -0.4 | 20.5 | 0.69 | 10 | 16.5 | 0.65
3789 | Van de Loo | Disol DSM-100 | Van de Loo : Disol DSM-100 | -0.4 | 43.5 | 2.98 | 100 | 34.5 | 2.85
3790 | Van de Loo | Disol DSM-20/20 L | Van de Loo : Disol DSM-20/20 L | -0.4 | 20.5 | 1.35 | 20 | 16.5 | 1.25
3791 | Van de Loo | Disol DSM-5/5 L | Van de Loo : Disol DSM-5/5 L | -0.4 | 20.5 | 0.35 | 5 | 17 | 0.32
3792 | Van de Loo | Disol DSM-50 | Van de Loo : Disol DSM-50 | -0.4 | 22 | 2.98 | 50 | 17.5 | 2.85
3793 | Viessmann | Vitovolt 300 | Viessmann : Vitovolt 300 | -0.4 | 90 | 5 | 320 | 70.5 | 4.53
3794 | Waaree | WS-230/WU-230 | Waaree : WS-230/WU-230 | -0.34 | 36 | 8.52 | 230 | 29 | 7.93
3795 | Waaree | WS-240/WU-240 | Waaree : WS-240/WU-240 | -0.34 | 36 | 8.89 | 240 | 29 | 8.28
3796 | WanXiang Solar | WXS 185S | WanXiang Solar : WXS 185S | -0.36 | 44.28 | 5.6 | 185 | 35.9 | 5.15
3797 | Webasto | Webasto allround 25 W | Webasto : Webasto allround 25 W | -0.4 | 21 | 1.58 | 25 | 16.8 | 1.49
3798 | Webasto | Webasto allround 50 W | Webasto : Webasto allround 50 W | -0.4 | 21 | 3.2 | 50 | 16.8 | 3
3799 | Webasto | Webasto flexible 12 W | Webasto : Webasto flexible 12 W | -0.4 | 21 | 0.75 | 12 | 16.8 | 0.71
3800 | Webasto | Webasto flexible 16 W | Webasto : Webasto flexible 16 W | -0.4 | 21 | 1.05 | 16 | 16.8 | 0.95
3801 | Webasto | Webasto flexible 25 W | Webasto : Webasto flexible 25 W | -0.4 | 21 | 1.58 | 25 | 16.8 | 1.49
3802 | Webasto | Webasto flexible 50 W-R | Webasto : Webasto flexible 50 W-R | -0.4 | 21 | 3.2 | 50 | 16.8 | 3
3803 | Webasto | Webasto flexible 50 W-S | Webasto : Webasto flexible 50 W-S | -0.4 | 21 | 3.2 | 50 | 16.8 | 3
3804 | Webel | W 1000-110Wp | Webel : W 1000-110Wp | -0.37 | 21 | 7.37 | 110 | 16.7 | 6.59
3805 | Webel | W 1000-115Wp | Webel : W 1000-115Wp | -0.37 | 21 | 7.85 | 115 | 16.7 | 6.89
3806 | Webel | W900 | Webel : W900 | -0.372 | 24.2 | 5.68 | 85 | 16.7 | 5.68
3807 | Webel | WS 155M 12V | Webel : WS 155M 12V | -0.25 | 21 | 10.68 | 155 | 16.7 | 9.3
3808 | Webel | WS 155M 24V | Webel : WS 155M 24V | -0.25 | 42 | 5.34 | 155 | 33.4 | 4.65
3809 | Webel | WS 160M 12V | Webel : WS 160M 12V | -0.25 | 21 | 10.89 | 160 | 16.7 | 9.59
3810 | Webel | WS 160M 24V | Webel : WS 160M 24V | -0.25 | 42 | 5.45 | 160 | 33.4 | 4.8
3811 | Webel | WS 165M 24V | Webel : WS 165M 24V | -0.25 | 42.2 | 5.56 | 165 | 33.6 | 4.92
3812 | WEILSOLAR | 43Wp | WEILSOLAR : 43Wp | -0.38 | 62.5 | 1.24 | 43 | 45.2 | 0.95
3813 | Welink | WL-110C | Welink : WL-110C | -0.38 | 21.6 | 6.6 | 110 | 17.6 | 6.25
3814 | Welink | WL-160A | Welink : WL-160A | -0.35 | 43.8 | 5.03 | 160 | 35 | 4.57
3815 | Welink | WL-170A | Welink : WL-170A | -0.35 | 44.4 | 5.27 | 170 | 35.5 | 4.79
3816 | Welink | WL-180A | Welink : WL-180A | -0.35 | 45 | 5.5 | 180 | 36 | 5
3817 | Welink | WL-200P | Welink : WL-200P | -0.35 | 36 | 7.75 | 200 | 28.7 | 6.97
3818 | Welink | WL-210P | Welink : WL-210P | -0.35 | 36.4 | 7.86 | 210 | 29.2 | 7.19
3819 | Welink | WL-220P | Welink : WL-220P | -0.35 | 36.8 | 8 | 220 | 29.8 | 7.39
3820 | Welink | WL-230P | Welink : WL-230P | -0.35 | 37 | 8.18 | 230 | 30 | 7.66
3821 | Welink | WL-70C | Welink : WL-70C | -0.38 | 21 | 4.7 | 70 | 16.8 | 4.16
3822 | Welink | WL-75C | Welink : WL-75C | -0.38 | 21.5 | 4.8 | 75 | 17.2 | 4.36
3823 | Welink | WL-80C | Welink : WL-80C | -0.38 | 21.6 | 4.9 | 80 | 17.6 | 4.55
3824 | Würth Solar | WS 11001 | Würth Solar : WS 11001 | -0.264 | 22 | 0.46 | 6.5 | 16.5 | 0.39
3825 | Würth Solar | WS 11002 | Würth Solar : WS 11002 | -0.264 | 22 | 0.63 | 9 | 16.5 | 0.55
3826 | Würth Solar | WS 11003 | Würth Solar : WS 11003 | -0.264 | 22 | 0.91 | 13 | 16.5 | 0.79
3827 | Würth Solar | WS 11004 | Würth Solar : WS 11004 | -0.264 | 44 | 0.63 | 18 | 33 | 0.55
3828 | Würth Solar | WS 11005 | Würth Solar : WS 11005 | -0.264 | 44 | 0.98 | 28 | 33 | 0.85
3829 | Würth Solar | WS 11006 | Würth Solar : WS 11006 | -0.264 | 44 | 1.5 | 43 | 33 | 1.3
3830 | Würth Solar | WS 11007 | Würth Solar : WS 11007 | -0.264 | 44 | 1.99 | 57 | 33 | 1.73
3831 | Würth Solar | WSG0025 E080 | Würth Solar : WSG0025 E080 | -0.29 | 160 | 0.72 | 80 | 120 | 0.67
3832 | Würth Solar | WSG0035 E075 | Würth Solar : WSG0035 E075 | -0.29 | 22 | 5.01 | 75 | 12 | 4.42
3833 | Würth Solar | WSG0036 E075 | Würth Solar : WSG0036 E075 | -0.29 | 44.5 | 2.36 | 75 | 24 | 2.15
3834 | Würth Solar | WSK0021 | Würth Solar : WSK0021 | -0.29 | 22 | 3.56 | 55 | 12 | 3.33
3835 | X-Group | X14-214 | X-Group : X14-214 | -0.33 | 36.7 | 7.95 | 214 | 29.12 | 7.36
3836 | X-Group | XG60P-205 | X-Group : XG60P-205 | -0.33 | 36.5 | 7.7 | 205 | 28.47 | 7.2
3837 | X-Group | XG60P-210 | X-Group : XG60P-210 | -0.33 | 36.6 | 7.85 | 210 | 28.77 | 7.3
3838 | X-Group | XG60P-215 | X-Group : XG60P-215 | -0.33 | 36.65 | 7.9 | 215 | 29.05 | 7.4
3839 | X-Group | XG60P-220 | X-Group : XG60P-220 | -0.33 | 36.7 | 8 | 220 | 29.33 | 7.5
3840 | X-Group | XG60P-225 | X-Group : XG60P-225 | -0.33 | 37 | 8.05 | 225 | 29.61 | 7.6
3841 | X-Group | XG60P-230 | X-Group : XG60P-230 | -0.33 | 37.1 | 8.1 | 230 | 29.87 | 7.7
3842 | X-Group | XG60P-235 | X-Group : XG60P-235 | -0.33 | 37.15 | 8.2 | 235 | 30.13 | 7.8
3843 | YingLi | YL150 (23) P1310x990 | YingLi : YL150 (23) P1310x990 | -0.37 | 29 | 7.2 | 150 | 22.5 | 6.7
3844 | YingLi | YL150 (35) P1580x808 | YingLi : YL150 (35) P1580x808 | -0.37 | 44 | 4.7 | 150 | 35 | 4.3
3845 | YingLi | YL155 (23) P1310x990 | YingLi : YL155 (23) P1310x990 | -0.37 | 29 | 7.4 | 155 | 22.5 | 6.9
3846 | YingLi | YL155 (35) P1580x808 | YingLi : YL155 (35) P1580x808 | -0.37 | 44 | 4.7 | 155 | 35 | 4.43
3847 | YingLi | YL160 (23) P1310x990 | YingLi : YL160 (23) P1310x990 | -0.37 | 29 | 7.7 | 160 | 23 | 6.96
3848 | YingLi | YL160 (35) P1580x808 | YingLi : YL160 (35) P1580x808 | -0.37 | 44 | 5 | 160 | 35 | 4.6
3849 | YingLi | YL165 (23) P1310x990 | YingLi : YL165 (23) P1310x990 | -0.37 | 29 | 7.9 | 165 | 23 | 7.17
3850 | YingLi | YL165 (35) P1580x808 | YingLi : YL165 (35) P1580x808 | -0.37 | 44 | 5.1 | 165 | 35 | 4.7
3851 | YingLi | YL170 (23) P1310x990 | YingLi : YL170 (23) P1310x990 | -0.37 | 29 | 8.1 | 170 | 23 | 7.39
3852 | YingLi | YL170 (35) P1580x808 | YingLi : YL170 (35) P1580x808 | -0.37 | 44 | 5.2 | 170 | 35 | 4.86
3853 | YingLi | YL175 (23) P1310x990 | YingLi : YL175 (23) P1310x990 | -0.37 | 29 | 8.2 | 175 | 23 | 7.61
3854 | YingLi | YL180 (23) P1310x990 | YingLi : YL180 (23) P1310x990 | -0.37 | 29.5 | 8.3 | 180 | 23 | 7.82
3855 | YingLi | YL185 (23) P1310x990 | YingLi : YL185 (23) P1310x990 | -0.37 | 29.5 | 8.45 | 185 | 23.5 | 7.83
3856 | Yingli | YL190 P-26b 1495x990 | Yingli : YL190 P-26b 1495x990 | -0.37 | 32.8 | 8.03 | 190 | 25.8 | 7.36
3857 | Yingli | YL195 P-26b 1495x990 | Yingli : YL195 P-26b 1495x990 | -0.37 | 33 | 8.15 | 195 | 26 | 7.5
3858 | YingLi | YL200 (156) P1650x1030 | YingLi : YL200 (156) P1650x1030 | -0.37 | 36 | 7.68 | 200 | 28.5 | 7.02
3859 | Yingli | YL200 P-26b 1495x990 | Yingli : YL200 P-26b 1495x990 | -0.37 | 33.3 | 8.22 | 200 | 26.3 | 7.6
3860 | YingLi | YL205 (156) P1650x1030 | YingLi : YL205 (156) P1650x1030 | -0.37 | 36 | 7.86 | 205 | 28.5 | 7.19
3861 | Yingli | YL205 P-26b 1495x990 | Yingli : YL205 P-26b 1495x990 | -0.37 | 33.5 | 8.33 | 205 | 26.5 | 7.74
3862 | YingLi | YL210 (156) P1650x1030 | YingLi : YL210 (156) P1650x1030 | -0.37 | 36 | 7.95 | 210 | 28.5 | 7.37
3863 | Yingli | YL210 P-26b 1495x990 | Yingli : YL210 P-26b 1495x990 | -0.37 | 33.6 | 8.45 | 210 | 26.6 | 7.9
3864 | Yingli | YL210 P-29b 1650x990 | Yingli : YL210 P-29b 1650x990 | -0.37 | 36 | 7.95 | 210 | 28.5 | 7.37
3865 | YingLi | YL215 (156) P1650x1030 | YingLi : YL215 (156) P1650x1030 | -0.37 | 36 | 8.1 | 215 | 29 | 7.41
3866 | Yingli | YL215 P-29b 1650x990 | Yingli : YL215 P-29b 1650x990 | -0.37 | 36 | 8.1 | 215 | 19 | 7.41
3867 | YingLi | YL220 (156) P1650x1030 | YingLi : YL220 (156) P1650x1030 | -0.37 | 36.5 | 8.15 | 220 | 29 | 7.59
3868 | Yingli | YL220 P-29b 1650x990 | Yingli : YL220 P-29b 1650x990 | -0.37 | 36.5 | 8.15 | 220 | 29 | 7.59
3869 | YingLi | YL225 (156) P1650x1030 | YingLi : YL225 (156) P1650x1030 | -0.37 | 36.5 | 8.28 | 225 | 29 | 7.63
3870 | Yingli | YL225 P-29b 1650x990 | Yingli : YL225 P-29b 1650x990 | -0.37 | 36.5 | 8.28 | 225 | 29.5 | 7.63
3871 | YingLi | YL230 (156) P1650x1030 | YingLi : YL230 (156) P1650x1030 | -0.37 | 37 | 8.4 | 230 | 29.5 | 7.8
3872 | Yingli | YL230 P-29b 1650x990 | Yingli : YL230 P-29b 1650x990 | -0.37 | 37 | 8.4 | 230 | 29.5 | 7.8
3873 | YingLi | YL235 (29) P1650x1030 | YingLi : YL235 (29) P1650x1030 | -0.37 | 37.2 | 8.45 | 235 | 30 | 7.83
3874 | Yingli | YL235 P-29b 1650x990 | Yingli : YL235 P-29b 1650x990 | -0.37 | 37 | 8.54 | 235 | 29.5 | 7.97
3875 | Yingli | YL235 P-32b 1810x990 | Yingli : YL235 P-32b 1810x990 | -0.37 | 40.5 | 8 | 235 | 32 | 7.34
3876 | YingLi | YL240 (29) P1650x1030 | YingLi : YL240 (29) P1650x1030 | -0.37 | 37.4 | 8.55 | 240 | 30 | 8
3877 | Yingli | YL240 P-32b 1810x990 | Yingli : YL240 P-32b 1810x990 | -0.37 | 40.5 | 8.15 | 240 | 32.2 | 7.45
3878 | Yingli | YL245 P-32b 1810x990 | Yingli : YL245 P-32b 1810x990 | -0.37 | 40.8 | 8.22 | 245 | 32.2 | 7.61
3879 | Yingli | YL250 P-32b 1810x990 | Yingli : YL250 P-32b 1810x990 | -0.37 | 40.9 | 8.33 | 250 | 32.3 | 7.74
3880 | Yingli | YL255 P-32b 1810x990 | Yingli : YL255 P-32b 1810x990 | -0.37 | 41 | 8.4 | 255 | 32.5 | 7.85
3881 | Yingli | YL260 P-35b 1970x990 | Yingli : YL260 P-35b 1970x990 | -0.37 | 44.6 | 8.04 | 260 | 35 | 7.43
3882 | Yingli | YL265 P-35b 1970x990 | Yingli : YL265 P-35b 1970x990 | -0.37 | 44.6 | 8.15 | 265 | 35.3 | 7.5
3883 | Yingli | YL270 P-35b 1970x990 | Yingli : YL270 P-35b 1970x990 | -0.37 | 44.8 | 8.2 | 270 | 35.3 | 7.65
3883 | Yingli | YL275 P-35b 1970x990 | Yingli : YL275 P-35b 1970x990 | -0.37 | 45 | 8.3 | 275 | 35.5 | 7.75
3883 | Yingli | YL280 P-35b 1970x990 | Yingli : YL280 P-35b 1970x990 | -0.37 | 45 | 8.35 | 280 | 35.5 | 7.89
3883 | YingLi | YL70 (17) P1172x541 | YingLi : YL70 (17) P1172x541 | -0.37 | 21.5 | 4.4 | 70 | 17 | 4.1
3883 | YingLi | YL75 (17) P1172x541 | YingLi : YL75 (17) P1172x541 | -0.37 | 22 | 4.7 | 75 | 17.5 | 1.3
3883 | YingLi | YL80 (17) P1172x541 | YingLi : YL80 (17) P1172x541 | -0.37 | 22 | 5 | 80 | 17.5 | 4.6
3883 | YingLi | YL85 (17) P1172x541 | YingLi : YL85 (17) P1172x541 | -0.37 | 22 | 5.2 | 85 | 17.5 | 4.9
3883 | YOCASOL | LDA160-A11 | YOCASOL : LDA160-A11 | -0.34 | 43.8 | 5.22 | 160 | 34.6 | 4.75
3883 | YOCASOL | LDA165-A11 | YOCASOL : LDA165-A11 | -0.34 | 44 | 5.33 | 165 | 34.8 | 4.75
3883 | YOCASOL | LDA170-A11 | YOCASOL : LDA170-A11 | -0.34 | 44.3 | 5.44 | 170 | 35.1 | 4.85
3883 | YOCASOL | LDA175-A11 | YOCASOL : LDA175-A11 | -0.34 | 44.5 | 5.55 | 175 | 35.3 | 4.96
3883 | YOCASOL | LDA180-A11 | YOCASOL : LDA180-A11 | -0.34 | 44.8 | 5.66 | 180 | 35.6 | 5.07
3883 | YOCASOL | PCA190-A01 | YOCASOL : PCA190-A01 | -0.37 | 32.7 | 8.62 | 190 | 25.6 | 7.42
3883 | YOCASOL | PCA195-A01 | YOCASOL : PCA195-A01 | -0.37 | 32.8 | 8.65 | 195 | 25.7 | 7.6
3883 | YOCASOL | PCA200-A01 | YOCASOL : PCA200-A01 | -0.37 | 32.8 | 8.68 | 200 | 25.7 | 4.78
3883 | YOCASOL | PCA205-A01 | YOCASOL : PCA205-A01 | -0.37 | 32.9 | 8.71 | 205 | 25.8 | 7.96
3883 | YOCASOL | PCA210-A01 | YOCASOL : PCA210-A01 | -0.37 | 32.9 | 8.74 | 210 | 25.8 | 8.14
3883 | YOCASOL | PCA215-A01 | YOCASOL : PCA215-A01 | -0.37 | 33 | 8.77 | 215 | 25.9 | 8.31
3883 | YOCASOL | PCB180-A21 | YOCASOL : PCB180-A21 | -0.32 | 32 | 8.04 | 180 | 25.6 | 7.03
3883 | YOCASOL | PCB185-A21 | YOCASOL : PCB185-A21 | -0.32 | 32.1 | 8.1 | 185 | 25.7 | 7.2
3883 | YOCASOL | PCB190-A21 | YOCASOL : PCB190-A21 | -0.32 | 32.3 | 8.18 | 190 | 25.8 | 7.36
3883 | YOCASOL | PCB195-A21 | YOCASOL : PCB195-A21 | -0.32 | 32.5 | 8.26 | 195 | 26 | 7.5
3883 | YOCASOL | PCB200-A21 | YOCASOL : PCB200-A21 | -0.32 | 32.7 | 8.36 | 200 | 26.2 | 7.63
3883 | Yohkon Energia | YE180M_165 | Yohkon Energia : YE180M_165 | -0.372 | 43.06 | 5.2 | 165 | 34.85 | 4.72
3883 | Yohkon Energia | YE180M_170 | Yohkon Energia : YE180M_170 | -0.37 | 43.27 | 5.25 | 170 | 35.35 | 4.8
3883 | Yohkon Energia | YE180M_175 | Yohkon Energia : YE180M_175 | -0.367 | 43.56 | 5.29 | 175 | 37.78 | 4.89
3883 | Yohkon Energia | YE180M_180 | Yohkon Energia : YE180M_180 | -0.374 | 43.99 | 5.33 | 180 | 36.5 | 4.94
3883 | Yohkon Energia | YE6220P_210 | Yohkon Energia : YE6220P_210 | -0.445 | 35.94 | 7.6 | 210 | 29.64 | 6.98
3883 | Yohkon Energia | YE6220P_215 | Yohkon Energia : YE6220P_215 | -0.444 | 36 | 7.78 | 215 | 29.85 | 7.1
3883 | Yohkon Energia | YE6220P_220 | Yohkon Energia : YE6220P_220 | -0.444 | 36.06 | 7.95 | 220 | 30.12 | 7.23
3883 | Yohkon Energia | YE6220P_225 | Yohkon Energia : YE6220P_225 | -0.442 | 36.24 | 8.04 | 225 | 30.24 | 7.31
3883 | Yohkon Energia | YE6220P_230 | Yohkon Energia : YE6220P_230 | -0.437 | 36.6 | 8.17 | 230 | 30.48 | 7.49
3883 | Yunnan Tianda Photovoltaic | TD170M5 | Yunnan Tianda Photovoltaic : TD170M5 | -0.37 | 43.8 | 5.35 | 170 | 34.6 | 4.91
3883 | Zenit Solar Modules | TD 160 | Zenit Solar Modules : TD 160 | -0.4 | 43.8 | 5.16 | 160 | 34.8 | 4.6
3883 | Zenit Solar Modules | TD 165 | Zenit Solar Modules : TD 165 | -0.4 | 44 | 5.2 | 165 | 34.8 | 4.74
3883 | Zenit Solar Modules | TD 170 | Zenit Solar Modules : TD 170 | -0.4 | 44.2 | 5.28 | 170 | 35 | 4.86
3883 | Zenit Solar Modules | TD 175 | Zenit Solar Modules : TD 175 | -0.4 | 44.4 | 5.36 | 175 | 35.2 | 4.97
3883 | Zenit Solar Modules | TD 180 | Zenit Solar Modules : TD 180 | -0.4 | 44.6 | 5.42 | 180 | 35.4 | 5.08
3883 | ZNSHINE SOLAR | ZX120M | ZNSHINE SOLAR : ZX120M | -0.33 | 22.2 | 7.52 | 120 | 17.3 | 6.94
3883 | ZNSHINE SOLAR | ZX130M | ZNSHINE SOLAR : ZX130M | -0.33 | 22.2 | 8 | 130 | 17.5 | 7.43
3883 | ZNSHINE SOLAR | ZX135M | ZNSHINE SOLAR : ZX135M | -0.33 | 22.4 | 8.14 | 135 | 17.5 | 7.71
3883 | ZNSHINE SOLAR | ZX185M | ZNSHINE SOLAR : ZX185M | -0.33 | 43.2 | 5.14 | 185 | 36 | 5.76
3883 | ZNSHINE SOLAR | ZX18M | ZNSHINE SOLAR : ZX18M | -0.33 | 22 | 1.11 | 18 | 17.4 | 1.03
3883 | ZNSHINE SOLAR | ZX20M | ZNSHINE SOLAR : ZX20M | -0.33 | 22.5 | 1.22 | 20 | 17.6 | 1.13
3883 | ZNSHINE SOLAR | ZX22M | ZNSHINE SOLAR : ZX22M | -0.33 | 22.7 | 1.32 | 22 | 17.8 | 1.23
3883 | ZNSHINE SOLAR | ZX45M | ZNSHINE SOLAR : ZX45M | -0.33 | 21.6 | 2.82 | 45 | 17.4 | 2.57
3883 | ZNSHINE SOLAR | ZX50M | ZNSHINE SOLAR : ZX50M | -0.33 | 21.6 | 3.12 | 50 | 17.5 | 2.87
3883 | ZNSHINE SOLAR | ZX55M | ZNSHINE SOLAR : ZX55M | -0.33 | 21.6 | 3.4 | 55 | 17.6 | 3.13
Note on E16: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E17: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E18: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E19: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E20: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E21: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E22: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E23: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E24: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E25: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E26: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E27: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E28: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E29: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E30: If provided in datasheet in [%/°C] please copy the value directly. If provided in [mV/°C] apply: 100 x [ (Temperature coefficient of Voc in mV ) / Voc]
Note on E162: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E163: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E254: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E255: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E256: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E257: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E258: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E271: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E272: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E273: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E274: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E307: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E308: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E309: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E310: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E311: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E312: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E313: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E331: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E340: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E341: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E342: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E343: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E344: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E348: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E349: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E350: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E351: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E352: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E353: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E354: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E355: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E356: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E357: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E358: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E359: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E360: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E362: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E447: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E521: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E527: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E528: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E529: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E530: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E531: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E532: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E533: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E534: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E535: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E536: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E537: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E538: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E539: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E540: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E541: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E542: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E543: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E544: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E545: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E546: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E547: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E548: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E549: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E550: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E551: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E552: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E553: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E554: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E555: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E562: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E563: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E564: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E565: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E566: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E567: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E569: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E570: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E571: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E572: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E573: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E574: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E575: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E576: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E577: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E578: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E579: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E580: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E581: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E582: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E583: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E584: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E585: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E586: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E587: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E588: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E589: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E590: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E591: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E628: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E629: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E630: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E631: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E632: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E633: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E634: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E635: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E636: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E637: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E638: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E639: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E640: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E641: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E642: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E643: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E644: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E645: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E646: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E647: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E648: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E649: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E650: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E651: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E652: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E653: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E654: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E655: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E656: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E657: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E658: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E659: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E660: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E661: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E662: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E663: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E664: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E665: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E666: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E667: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E668: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E669: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E670: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E671: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E672: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E673: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E674: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E675: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E676: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E677: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E678: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E679: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E680: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E681: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E682: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E683: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E684: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E685: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E686: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E687: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E688: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E689: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E690: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E691: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E692: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E693: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E694: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E695: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E696: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E697: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E698: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E699: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E700: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E701: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E702: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E703: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E704: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E705: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E706: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E707: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E708: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E709: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E710: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E711: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E712: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E713: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E714: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E715: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E716: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E717: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E718: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E719: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E720: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E721: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E722: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E723: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E724: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E726: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E727: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E728: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E729: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E730: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E731: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E732: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E733: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E734: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E735: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E736: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E737: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E738: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E739: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E740: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E741: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E742: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E743: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E744: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E745: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E746: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E747: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E748: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E749: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E750: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E751: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E752: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E753: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E754: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E755: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E756: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E757: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E758: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E776: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E777: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E778: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E782: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E783: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E784: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1025: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1026: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1027: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1028: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1029: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1030: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1031: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1032: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1033: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1034: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1035: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1036: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1037: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1038: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1039: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1040: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1041: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1042: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1043: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1044: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1045: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1046: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1047: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1048: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1049: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1050: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1051: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1052: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1053: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1054: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1055: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1056: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1057: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1058: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1059: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1060: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1061: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1062: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1063: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1064: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1065: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1066: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1067: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1068: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1069: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1070: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1071: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1072: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1073: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1074: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1075: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1076: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1077: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1078: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1084: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1095: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1096: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1097: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1098: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1099: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1100: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1101: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1102: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1103: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1104: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1105: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1106: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1107: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1108: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1109: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1110: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1111: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1112: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1113: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1114: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1115: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1116: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1117: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1118: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1119: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1120: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1121: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1136: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1137: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1138: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1139: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1140: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1141: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1142: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1143: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1144: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1145: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1146: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1147: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1148: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1149: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1150: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1151: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1152: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1153: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1154: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1155: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1156: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1157: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1158: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1159: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1160: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1161: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1251: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1252: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1253: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1254: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1255: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1256: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1257: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1258: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1259: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1260: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1261: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1302: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1303: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1304: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1305: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1322: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1323: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1324: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1325: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1326: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1327: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1328: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1329: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1330: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1331: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1332: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1333: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1334: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1335: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1336: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1337: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1338: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1339: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1340: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1359: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1360: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1361: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1362: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1363: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1364: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1365: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1366: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1367: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1368: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1369: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1370: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1371: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1372: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1373: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1374: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1375: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1376: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1406: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1407: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1408: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1409: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1410: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1411: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1412: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1413: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1414: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1415: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1416: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1417: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1459: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1460: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1461: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1462: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1465: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1466: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1467: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1468: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1469: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1470: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1471: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1472: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1473: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1474: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1475: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1476: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1477: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1478: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1479: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1480: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1481: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1510: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1511: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1512: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1513: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1514: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1515: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1516: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1517: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1518: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1519: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1520: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1521: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1522: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1523: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1524: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1525: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1526: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1527: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1528: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1529: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1530: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1531: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1532: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1533: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1534: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1535: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1536: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1537: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1605: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1606: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1607: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1608: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1609: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1701: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1702: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1703: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1704: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1705: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1706: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1707: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1708: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1709: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1710: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1714: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1715: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1716: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1717: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1718: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1767: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1768: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1769: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1770: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1771: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1772: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1773: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1797: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1798: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1799: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1800: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1801: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1802: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1811: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1812: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1813: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1814: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1815: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1816: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1862: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1902: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E1903: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2008: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2010: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2012: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2046: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2047: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2048: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2049: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2050: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2051: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2052: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2053: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2059: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2060: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2061: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2099: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2100: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2101: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2102: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2103: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2104: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2120: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2121: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2122: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2123: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2124: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2125: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2126: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2127: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2128: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2129: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2130: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2131: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2132: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2133: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2134: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2135: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2136: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2137: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2138: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2139: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2140: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2141: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2142: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2143: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2144: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2245: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2246: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2320: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2321: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2322: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2323: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2345: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2346: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2347: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2348: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2349: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2350: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2351: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2352: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2353: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2354: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2360: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2361: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2362: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2363: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2369: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2453: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2455: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2456: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2457: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2458: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2460: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2462: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2464: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2466: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2469: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2491: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2492: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2575: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2576: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2577: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2578: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2579: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2580: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2581: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2582: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2583: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2584: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2585: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2586: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2587: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2588: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2589: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2590: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2591: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2592: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2593: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2594: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2595: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2596: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2597: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2634: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2635: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2636: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2637: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2638: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2645: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2646: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2647: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2648: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2649: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2664: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2665: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2666: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2667: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2668: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2669: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2671: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2672: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2673: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2674: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2675: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2678: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2679: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2680: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2681: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2682: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2683: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2684: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2685: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2686: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2687: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2982: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2983: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2984: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2985: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2986: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2987: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2988: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2989: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2990: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2991: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2992: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2993: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2994: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2995: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2996: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2997: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2998: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E2999: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3000: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3001: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3002: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3003: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3004: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3005: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3006: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3007: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3008: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3009: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3106: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3111: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3112: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3113: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3114: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3115: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3116: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3117: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3118: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3120: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3122: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3124: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3125: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3127: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3161: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3162: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3163: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3164: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3165: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3166: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3167: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3168: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3169: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3170: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3171: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3173: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3174: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3175: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3176: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3177: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3178: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3192: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3193: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3194: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3195: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3196: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3197: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3198: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3199: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3200: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3201: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3202: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3203: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3204: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3205: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3206: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3207: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3208: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3209: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3279: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3280: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3289: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3290: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3291: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3293: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3295: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3398: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3399: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3400: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3401: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3402: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3403: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3404: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3405: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3406: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3407: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3408: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3409: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3410: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3411: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3412: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3413: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3414: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3415: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3416: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3417: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3418: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3419: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3420: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3421: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3422: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3425: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3426: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3427: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3428: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3429: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3430: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3457: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3458: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3459: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3460: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3461: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3462: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3463: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3464: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3465: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3466: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3467: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3468: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3497: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3498: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3499: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3500: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3545: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3546: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3547: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3548: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3656: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3695: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3696: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3697: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3698: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3699: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3700: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3709: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3710: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3750: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3751: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3752: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3753: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3754: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3755: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3756: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3757: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3836: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3837: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3838: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3839: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3840: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3841: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3842: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3843: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3844: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]
Note on E3845: BETA = 1000 x [ (Temperature coefficient of Voc) / Voc]

## HELP
Cos(φ) help
Cos(φ) should be set to 1 except for Germany
Cos(φ) is applicable for installations connected to the German medium voltage network and, starting April 2011, installations connected to the German low voltage network. Next to reactive power, the inverter has to provide reactive power. The relation of active power to apparent power is expressed as cos(φ) (or Power Factor (PF), which is the same number).
Contact the network provider for the settings or use the following table. Use the lowest value provided (furtherst away from 1).
Plant size | Cos(φ) (Germany only)
< 3.68 kVA | 1
3.68kVA – 13.8kVA | 0.95
> 13.8kVA | 0.9
#Value error
In case of #Value error Go To: Tools - Options - International Tab and reverse the Decimal and Thousands separator
NOT YET FUNCTIONAL
< = >

## Changelog (H) (hidden)
Date finished | Person | Action
23-2-2011 | tj | Update input window CS (Umin = 250, was 350), max 950V
23-2-2011 | tj | Added IS
24-2-2011 | tj | Module beta in %/C (was ‰/C)
24-2-2012 | tj | Reactive Power, has effect on max DC input of inverter and on cable losses
24-2-2013 | tj | U_MPP_max = 0.8*V_max (was 0.9*V_Max)
24-2-2014 | tj | Removed option of 4 DC inputs
24-2-2015 | tj | Insert Sac and Pac in results page
24-2-2016 | tj | Changed "Total converted energy" (cable losses page) in | Beschikbaar vermogen | Available power | verfügbare Leistung | potencia disponible | Puissance disponible | Potenza disponibile
24-2-2017 | tj | Added (English) changelog on introduction page
24-2-2018 | tj | Included 70 new modules
24-2-2019 | tj | cos(phi) explanation in HELP page
25-2-2011 | tj | Removed "Number of modules" feature
25-2-2012 | tj | Added "Vnom" to graphical design page
25-2-2013 | tj | Added "Total number of modules', which counts the number of modules in the designed system
2011-10-03 | tj | added 50 new modules
Todo
Date due | Person
April | tj | Actively track top 10 inverter manufacturers
? | tj | Search on first letter of solar module manufacturer

## Array (hidden)
ARRAY KARAKTERISTIEK
| input 1 | input 2
Umpp_Start | 418 | 418
Umpp_Tmax | 488.015 | 488.015
Umpp_Tmin | 582.8487 | 582.8487
Uoc_Tmin | 705.5538 | 705.5538
I1 | 0 | 0
I2 | 20.2863 | 20.2863
I4 | 16.9855 | 16.9855
I5 | 0 | 0

## Kabelgegevens (hidden)
| diameter (mm²) |  |  | lengte (m) |  | Materiaal | soortelijke weerstand
1 | 1.5 |  | 1 | 1 |  | copper | 1.75e-08
2 | 2.5 |  | 2 | 2 |  | aluminium | 2.78e-08
3 | 4 |  | 3 | 3
4 | 6 |  | 4 | 4
5 | 10 |  | 5 | 5 |  |  | geselecteerd DC1: | 1
6 | 16 |  | 6 | 6 |  |  | geselecteerd DC2: | 1
7 | 25 |  | 7 | 7 |  |  | geselecteerd DC3: | 1
8 | 35 |  | 8 | 8 |  |  | geselecteerd DC4: | 1
9 | 50 |  | 9 | 9
10 | 60 |  | 10 | 10 |  |  | geselecteerd AC: | 1
11 | 75 |  | 11 | 11
12 | 90 |  | 12 | 12
|  |  | 13 | 13
|  |  | 14 | 14
|  |  | 15 | 15
| geselecteerd DC1: | 4 | 16 | 16
| geselecteerd DC2: | 4 | 17 | 17
| geselecteerd DC3: | 3 | 18 | 18
| geselecteerd DC4: | 2 | 19 | 19
|  |  | 20 | 20
| geselecteerd AC: | 4 | 21 | 21
|  |  | 22 | 22
|  |  | 23 | 23
|  |  | 24 | 24
|  |  | 25 | 25
|  |  | 26 | 26
|  |  | 27 | 27
|  |  | 28 | 28
|  |  | 29 | 29
|  |  | 30 | 30
|  |  | 31 | 31
|  |  | 32 | 32
|  |  | 33 | 33
|  |  | 34 | 34
|  |  | 35 | 35
|  |  | 36 | 36
|  |  | 37 | 37
|  |  | 38 | 38
|  |  | 39 | 39
|  |  | 40 | 40
|  |  | 41 | 41
|  |  | 42 | 42
|  |  | 43 | 43
|  |  | 44 | 44
|  |  | 45 | 45
|  |  | 46 | 46
|  |  | 47 | 47
|  |  | 48 | 48
|  |  | 49 | 49
|  |  | 50 | 50
|  |  | 51 | 51
|  |  | 52 | 52
|  |  | 53 | 53
|  |  | 54 | 54
|  |  | 55 | 55
|  |  | 56 | 56
|  |  | 57 | 57
|  |  | 58 | 58
|  |  | 59 | 59
|  |  | 60 | 60
|  |  | 61 | 61
|  |  | 62 | 62
|  |  | 63 | 63
|  |  | 64 | 64
|  |  | 65 | 65
|  |  | 66 | 66
|  |  | 67 | 67
|  |  | 68 | 68
|  |  | 69 | 69
|  |  | 70 | 70
|  |  | 71 | 71
|  |  | 72 | 72
|  |  | 73 | 73
|  |  | 74 | 74
|  |  | 75 | 75
|  |  | 76 | 76
|  |  | 77 | 77
|  |  | 78 | 78
|  |  | 79 | 79
|  |  | 80 | 80
|  |  | 81 | 81
|  |  | 82 | 82
|  |  | 83 | 83
|  |  | 84 | 84
|  |  | 85 | 85
|  |  | 86 | 86
|  |  | 87 | 87
|  |  | 88 | 88
|  |  | 89 | 89
|  |  | 90 | 90
|  |  | 91 | 91
|  |  | 92 | 92
|  |  | 93 | 93
|  |  | 94 | 94
|  |  | 95 | 95
|  |  | 96 | 96
|  |  | 97 | 97
|  |  | 98 | 98
|  |  | 99 | 99
|  |  | 100 | 100
|  |  |  | geselecteerd DC1: | 25
|  |  |  | geselecteerd DC2: | 25
|  |  |  | geselecteerd DC3: | 95
|  |  |  | geselecteerd DC4: | 5
|  |  |  | geselecteerd AC: | 20

## Land-Regio (hidden)
sort | Land/regio | Instralingsgebied | Stad | country_ vmpttmin correction | country_ temperature range
1 | The Netherlands | 1 | Amsterdam | 1.55 | -35
2 | Germany - north | 1 | Amsterdam | 1.55 | -35
3 | Germany - central | 12 | Keulen | 1.55 | -35
4 | Germany - south | 16 | Parijs | 1.55 | -35
5 | Italy - north | 15 | Milaan | 1.55 | -25
6 | Italy - south | 19 | Sevilla | 1.55 | -25
7 | United Kingdom | 1 | Amsterdam | 1.55 | -35
8 | Switzerland | 16 | Parijs | 1.55 | -40
9 | Spain - north | 15 | Milaan | 1.55 | -35
10 | Spain - south | 19 | Sevilla | 1.55 | -25
11 | France - north | 16 | Parijs | 1.55 | -35
12 | France - south | 15 | Milaan | 1.55 | -35
13 | Denmark | 1 | Amsterdam | 1.55 | -35
14 | Belgium | 1 | Amsterdam | 1.55 | -35
15 | Austria | 16 | Parijs | 1.55 | -35
16 | Ireland | 1 | Amsterdam | 1.55 | -40
17 | Luxemburg | 1 | Amsterdam | 1.55 | -35
18 | Portugal | 19 | Sevilla | 1.55 | -25
19 | Europe - north | 20 | Stockholm | 1.55 | -35
20 | Europe - east | 1 | Amsterdam | 1.55 | -35
21 | Europe - south east | 11 | Istanbull | 1.55 | -25
22 | Afrika - central | 6 | Djakarta | 1.55 | -10
23 | Afrika - north | 2 | Bagdad | 1.55 | -10
24 | Afrika - south | 17 | Perth | 1.55 | -10
25 | Asia - east | 18 | Seoul | 1.55 | -25
26 | Asia - south | 2 | Bagdad | 1.55 | -10
27 | Asia - south east | 6 | Djakarta | 1.55 | -10
28 | Australia - central | 17 | Perth | 1.55 | -10
29 | Australia - east | 5 | Canberra | 1.55 | -25
30 | Australia - north | 13 | Lima | 1.55 | -10
31 | Australia - south | 10 | Invercargill Station | 1.55 | -40
32 | Australia - west | 17 | Perth | 1.55 | -10
33 | Canada | 20 | Stockholm | 1.55 | -40
34 | Central America | 9 | Honnolulu | 1.55 | -10
35 | Middle East | 2 | Bagdad | 1.55 | -25
36 | New Zealand | 10 | Invercargill Station | 1.55 | -40
37 | Southern America - central | 13 | Lima | 1.55 | -25
38 | Southern America - north | 7 | Fortaleza | 1.55 | -10
39 | Southern America - south | 4 | Buenos Aires | 1.55 | -40
40 | United States - central | 14 | Los Angeles | 1.55 | -25
41 | United States - north | 3 | Boston | 1.55 | -40
42 | United States - south | 9 | Honnolulu | 1.55 | -25
|  |  |  | geselecteerde land/regio: |  | 3
|  |  |  | Instralingsgebied horende bij land/regio: |  |  | 12

## Instralingsgebied (hidden)
| Geselecteerd: | 12
Instralings- gebied | Stad
1 | Amsterdam
2 | Bagdad
3 | Boston
4 | Buenos Aires
5 | Canberra
6 | Djakarta
7 | Fortaleza
8 | Guatamala
9 | Honnolulu
10 | Invercargill Station
11 | Istanbull
12 | Keulen
13 | Lima
14 | Los Angeles
15 | Milaan
16 | Parijs
17 | Perth
18 | Seoul
19 | Sevilla
20 | Stockholm

## Orientatie (hidden)
Sort | Orientatie
1 | N
2 | NNE
3 | NE
4 | ENE
5 | E
6 | ESE
7 | SE
8 | SSE
9 | S
10 | SSW
11 | SW
12 | WSW
13 | W
14 | WNW
15 | NW
16 | NNW
| Geselecteerd: | 9

## Hoek (hidden)
Sort | Hoek
1 | 0° (horizontal)
2 | 10°
3 | 20°
4 | 30°
5 | 40°
6 | 50°
7 | 60°
8 | 70°
9 | 80°
10 | 90° (vertical)
| Geselecteerd: | 4

## orientadjust (hidden)
Instralings- gebied | Stad | Orientatie | Hoek | orientation_ correctionvalue
1 | Amsterdam | N ( 0 degrees) | 0 degrees (horizontal) | 0.9 |  | Geselecteerd:
1 | Amsterdam | N ( 0 degrees) | 10 degrees | 0.83
1 | Amsterdam | N ( 0 degrees) | 20 degrees | 0.75 | Land/Regio: | 3 | = | Germany - central
1 | Amsterdam | N ( 0 degrees) | 30 degrees | 0.67 | Instralingsgebied: | 12 | = | Keulen
1 | Amsterdam | N ( 0 degrees) | 40 degrees | 0.59 | Orientatie:: | 9 | = | S
1 | Amsterdam | N ( 0 degrees) | 50 degrees | 0.51 | Hoek: | 4 | = | 30°
1 | Amsterdam | N ( 0 degrees) | 60 degrees | 0.45
1 | Amsterdam | N ( 0 degrees) | 70 degrees | 0.41
1 | Amsterdam | N ( 0 degrees) | 80 degrees | 0.38 | Levert correctiefactor: |  |  | 1
1 | Amsterdam | N ( 0 degrees) | 90 degrees (vertical) | 0.35
1 | Amsterdam | NNE (22.5) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | NNE (22.5) | 10 degrees | 0.83
1 | Amsterdam | NNE (22.5) | 20 degrees | 0.76
1 | Amsterdam | NNE (22.5) | 30 degrees | 0.68
1 | Amsterdam | NNE (22.5) | 40 degrees | 0.6
1 | Amsterdam | NNE (22.5) | 50 degrees | 0.53
1 | Amsterdam | NNE (22.5) | 60 degrees | 0.48
1 | Amsterdam | NNE (22.5) | 70 degrees | 0.43
1 | Amsterdam | NNE (22.5) | 80 degrees | 0.4
1 | Amsterdam | NNE (22.5) | 90 degrees (vertical) | 0.36
1 | Amsterdam | NE (45) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | NE (45) | 10 degrees | 0.85
1 | Amsterdam | NE (45) | 20 degrees | 0.78
1 | Amsterdam | NE (45) | 30 degrees | 0.72
1 | Amsterdam | NE (45) | 40 degrees | 0.65
1 | Amsterdam | NE (45) | 50 degrees | 0.59
1 | Amsterdam | NE (45) | 60 degrees | 0.54
1 | Amsterdam | NE (45) | 70 degrees | 0.49
1 | Amsterdam | NE (45) | 80 degrees | 0.45
1 | Amsterdam | NE (45) | 90 degrees (vertical) | 0.4
1 | Amsterdam | ENE (67.5) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | ENE (67.5) | 10 degrees | 0.87
1 | Amsterdam | ENE (67.5) | 20 degrees | 0.82
1 | Amsterdam | ENE (67.5) | 30 degrees | 0.78
1 | Amsterdam | ENE (67.5) | 40 degrees | 0.72
1 | Amsterdam | ENE (67.5) | 50 degrees | 0.67
1 | Amsterdam | ENE (67.5) | 60 degrees | 0.62
1 | Amsterdam | ENE (67.5) | 70 degrees | 0.57
1 | Amsterdam | ENE (67.5) | 80 degrees | 0.52
1 | Amsterdam | ENE (67.5) | 90 degrees (vertical) | 0.46
1 | Amsterdam | E (90) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | E (90) | 10 degrees | 0.89
1 | Amsterdam | E (90) | 20 degrees | 0.87
1 | Amsterdam | E (90) | 30 degrees | 0.84
1 | Amsterdam | E (90) | 40 degrees | 0.8
1 | Amsterdam | E (90) | 50 degrees | 0.76
1 | Amsterdam | E (90) | 60 degrees | 0.71
1 | Amsterdam | E (90) | 70 degrees | 0.65
1 | Amsterdam | E (90) | 80 degrees | 0.59
1 | Amsterdam | E (90) | 90 degrees (vertical) | 0.53
1 | Amsterdam | ESE (112.5) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | ESE (112.5) | 10 degrees | 0.91
1 | Amsterdam | ESE (112.5) | 20 degrees | 0.92
1 | Amsterdam | ESE (112.5) | 30 degrees | 0.9
1 | Amsterdam | ESE (112.5) | 40 degrees | 0.87
1 | Amsterdam | ESE (112.5) | 50 degrees | 0.84
1 | Amsterdam | ESE (112.5) | 60 degrees | 0.79
1 | Amsterdam | ESE (112.5) | 70 degrees | 0.73
1 | Amsterdam | ESE (112.5) | 80 degrees | 0.67
1 | Amsterdam | ESE (112.5) | 90 degrees (vertical) | 0.59
1 | Amsterdam | SE (135) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | SE (135) | 10 degrees | 0.93
1 | Amsterdam | SE (135) | 20 degrees | 0.95
1 | Amsterdam | SE (135) | 30 degrees | 0.95
1 | Amsterdam | SE (135) | 40 degrees | 0.94
1 | Amsterdam | SE (135) | 50 degrees | 0.91
1 | Amsterdam | SE (135) | 60 degrees | 0.86
1 | Amsterdam | SE (135) | 70 degrees | 0.8
1 | Amsterdam | SE (135) | 80 degrees | 0.73
1 | Amsterdam | SE (135) | 90 degrees (vertical) | 0.73
1 | Amsterdam | SSE (157.5) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | SSE (157.5) | 10 degrees | 0.95
1 | Amsterdam | SSE (157.5) | 20 degrees | 0.98
1 | Amsterdam | SSE (157.5) | 30 degrees | 0.99
1 | Amsterdam | SSE (157.5) | 40 degrees | 0.98
1 | Amsterdam | SSE (157.5) | 50 degrees | 0.96
1 | Amsterdam | SSE (157.5) | 60 degrees | 0.91
1 | Amsterdam | SSE (157.5) | 70 degrees | 0.85
1 | Amsterdam | SSE (157.5) | 80 degrees | 0.78
1 | Amsterdam | SSE (157.5) | 90 degrees (vertical) | 0.69
1 | Amsterdam | S (180) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | S (180) | 10 degrees | 0.95
1 | Amsterdam | S (180) | 20 degrees | 0.99
1 | Amsterdam | S (180) | 30 degrees | 1
1 | Amsterdam | S (180) | 40 degrees | 1
1 | Amsterdam | S (180) | 50 degrees | 0.97
1 | Amsterdam | S (180) | 60 degrees | 0.93
1 | Amsterdam | S (180) | 70 degrees | 0.87
1 | Amsterdam | S (180) | 80 degrees | 0.79
1 | Amsterdam | S (180) | 90 degrees (vertical) | 0.7
1 | Amsterdam | SSW (202.5) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | SSW (202.5) | 10 degrees | 0.95
1 | Amsterdam | SSW (202.5) | 20 degrees | 0.98
1 | Amsterdam | SSW (202.5) | 30 degrees | 0.99
1 | Amsterdam | SSW (202.5) | 40 degrees | 0.98
1 | Amsterdam | SSW (202.5) | 50 degrees | 0.96
1 | Amsterdam | SSW (202.5) | 60 degrees | 0.91
1 | Amsterdam | SSW (202.5) | 70 degrees | 0.85
1 | Amsterdam | SSW (202.5) | 80 degrees | 0.78
1 | Amsterdam | SSW (202.5) | 90 degrees (vertical) | 0.69
1 | Amsterdam | SW (225) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | SW (225) | 10 degrees | 0.93
1 | Amsterdam | SW (225) | 20 degrees | 0.95
1 | Amsterdam | SW (225) | 30 degrees | 0.95
1 | Amsterdam | SW (225) | 40 degrees | 0.94
1 | Amsterdam | SW (225) | 50 degrees | 0.91
1 | Amsterdam | SW (225) | 60 degrees | 0.86
1 | Amsterdam | SW (225) | 70 degrees | 0.8
1 | Amsterdam | SW (225) | 80 degrees | 0.73
1 | Amsterdam | SW (225) | 90 degrees (vertical) | 0.73
1 | Amsterdam | WSW (247.5) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | WSW (247.5) | 10 degrees | 0.91
1 | Amsterdam | WSW (247.5) | 20 degrees | 0.92
1 | Amsterdam | WSW (247.5) | 30 degrees | 0.9
1 | Amsterdam | WSW (247.5) | 40 degrees | 0.87
1 | Amsterdam | WSW (247.5) | 50 degrees | 0.84
1 | Amsterdam | WSW (247.5) | 60 degrees | 0.79
1 | Amsterdam | WSW (247.5) | 70 degrees | 0.73
1 | Amsterdam | WSW (247.5) | 80 degrees | 0.67
1 | Amsterdam | WSW (247.5) | 90 degrees (vertical) | 0.59
1 | Amsterdam | W (270) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | W (270) | 10 degrees | 0.89
1 | Amsterdam | W (270) | 20 degrees | 0.87
1 | Amsterdam | W (270) | 30 degrees | 0.84
1 | Amsterdam | W (270) | 40 degrees | 0.8
1 | Amsterdam | W (270) | 50 degrees | 0.76
1 | Amsterdam | W (270) | 60 degrees | 0.71
1 | Amsterdam | W (270) | 70 degrees | 0.65
1 | Amsterdam | W (270) | 80 degrees | 0.59
1 | Amsterdam | W (270) | 90 degrees (vertical) | 0.53
1 | Amsterdam | WNW (292.5) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | WNW (292.5) | 10 degrees | 0.87
1 | Amsterdam | WNW (292.5) | 20 degrees | 0.82
1 | Amsterdam | WNW (292.5) | 30 degrees | 0.78
1 | Amsterdam | WNW (292.5) | 40 degrees | 0.72
1 | Amsterdam | WNW (292.5) | 50 degrees | 0.67
1 | Amsterdam | WNW (292.5) | 60 degrees | 0.62
1 | Amsterdam | WNW (292.5) | 70 degrees | 0.57
1 | Amsterdam | WNW (292.5) | 80 degrees | 0.52
1 | Amsterdam | WNW (292.5) | 90 degrees (vertical) | 0.46
1 | Amsterdam | NW (315) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | NW (315) | 10 degrees | 0.85
1 | Amsterdam | NW (315) | 20 degrees | 0.78
1 | Amsterdam | NW (315) | 30 degrees | 0.72
1 | Amsterdam | NW (315) | 40 degrees | 0.65
1 | Amsterdam | NW (315) | 50 degrees | 0.59
1 | Amsterdam | NW (315) | 60 degrees | 0.54
1 | Amsterdam | NW (315) | 70 degrees | 0.49
1 | Amsterdam | NW (315) | 80 degrees | 0.45
1 | Amsterdam | NW (315) | 90 degrees (vertical) | 0.4
1 | Amsterdam | NNW (337.5) | 0 degrees (horizontal) | 0.9
1 | Amsterdam | NNW (337.5) | 10 degrees | 0.83
1 | Amsterdam | NNW (337.5) | 20 degrees | 0.76
1 | Amsterdam | NNW (337.5) | 30 degrees | 0.68
1 | Amsterdam | NNW (337.5) | 40 degrees | 0.6
1 | Amsterdam | NNW (337.5) | 50 degrees | 0.53
1 | Amsterdam | NNW (337.5) | 60 degrees | 0.48
1 | Amsterdam | NNW (337.5) | 70 degrees | 0.43
1 | Amsterdam | NNW (337.5) | 80 degrees | 0.4
1 | Amsterdam | NNW (337.5) | 90 degrees (vertical) | 0.36
2 | Bagdad | N ( 0 degrees) | 0 degrees (horizontal) | 0.93
2 | Bagdad | N ( 0 degrees) | 10 degrees | 0.87
2 | Bagdad | N ( 0 degrees) | 20 degrees | 0.78
2 | Bagdad | N ( 0 degrees) | 30 degrees | 0.68
2 | Bagdad | N ( 0 degrees) | 40 degrees | 0.58
2 | Bagdad | N ( 0 degrees) | 50 degrees | 0.49
2 | Bagdad | N ( 0 degrees) | 60 degrees | 0.4
2 | Bagdad | N ( 0 degrees) | 70 degrees | 0.33
2 | Bagdad | N ( 0 degrees) | 80 degrees | 0.27
2 | Bagdad | N ( 0 degrees) | 90 degrees (vertical) | 0.25
2 | Bagdad | NNE (22.5) | 0 degrees (horizontal) | 0.93
2 | Bagdad | NNE (22.5) | 10 degrees | 0.87
2 | Bagdad | NNE (22.5) | 20 degrees | 0.79
2 | Bagdad | NNE (22.5) | 30 degrees | 0.7
2 | Bagdad | NNE (22.5) | 40 degrees | 0.6
2 | Bagdad | NNE (22.5) | 50 degrees | 0.51
2 | Bagdad | NNE (22.5) | 60 degrees | 0.42
2 | Bagdad | NNE (22.5) | 70 degrees | 0.35
2 | Bagdad | NNE (22.5) | 80 degrees | 0.3
2 | Bagdad | NNE (22.5) | 90 degrees (vertical) | 0.27
2 | Bagdad | NE (45) | 0 degrees (horizontal) | 0.93
2 | Bagdad | NE (45) | 10 degrees | 0.88
2 | Bagdad | NE (45) | 20 degrees | 0.82
2 | Bagdad | NE (45) | 30 degrees | 0.74
2 | Bagdad | NE (45) | 40 degrees | 0.65
2 | Bagdad | NE (45) | 50 degrees | 0.57
2 | Bagdad | NE (45) | 60 degrees | 0.49
2 | Bagdad | NE (45) | 70 degrees | 0.43
2 | Bagdad | NE (45) | 80 degrees | 0.38
2 | Bagdad | NE (45) | 90 degrees (vertical) | 0.33
2 | Bagdad | ENE (67.5) | 0 degrees (horizontal) | 0.93
2 | Bagdad | ENE (67.5) | 10 degrees | 0.9
2 | Bagdad | ENE (67.5) | 20 degrees | 0.85
2 | Bagdad | ENE (67.5) | 30 degrees | 0.79
2 | Bagdad | ENE (67.5) | 40 degrees | 0.73
2 | Bagdad | ENE (67.5) | 50 degrees | 0.66
2 | Bagdad | ENE (67.5) | 60 degrees | 0.59
2 | Bagdad | ENE (67.5) | 70 degrees | 0.52
2 | Bagdad | ENE (67.5) | 80 degrees | 0.46
2 | Bagdad | ENE (67.5) | 90 degrees (vertical) | 0.41
2 | Bagdad | E (90) | 0 degrees (horizontal) | 0.93
2 | Bagdad | E (90) | 10 degrees | 0.92
2 | Bagdad | E (90) | 20 degrees | 0.89
2 | Bagdad | E (90) | 30 degrees | 0.85
2 | Bagdad | E (90) | 40 degrees | 0.8
2 | Bagdad | E (90) | 50 degrees | 0.74
2 | Bagdad | E (90) | 60 degrees | 0.68
2 | Bagdad | E (90) | 70 degrees | 0.61
2 | Bagdad | E (90) | 80 degrees | 0.54
2 | Bagdad | E (90) | 90 degrees (vertical) | 0.47
2 | Bagdad | ESE (112.5) | 0 degrees (horizontal) | 0.93
2 | Bagdad | ESE (112.5) | 10 degrees | 0.94
2 | Bagdad | ESE (112.5) | 20 degrees | 0.93
2 | Bagdad | ESE (112.5) | 30 degrees | 0.91
2 | Bagdad | ESE (112.5) | 40 degrees | 0.87
2 | Bagdad | ESE (112.5) | 50 degrees | 0.82
2 | Bagdad | ESE (112.5) | 60 degrees | 0.75
2 | Bagdad | ESE (112.5) | 70 degrees | 0.68
2 | Bagdad | ESE (112.5) | 80 degrees | 0.6
2 | Bagdad | ESE (112.5) | 90 degrees (vertical) | 0.53
2 | Bagdad | SE (135) | 0 degrees (horizontal) | 0.93
2 | Bagdad | SE (135) | 10 degrees | 0.96
2 | Bagdad | SE (135) | 20 degrees | 0.97
2 | Bagdad | SE (135) | 30 degrees | 0.96
2 | Bagdad | SE (135) | 40 degrees | 0.93
2 | Bagdad | SE (135) | 50 degrees | 0.88
2 | Bagdad | SE (135) | 60 degrees | 0.81
2 | Bagdad | SE (135) | 70 degrees | 0.74
2 | Bagdad | SE (135) | 80 degrees | 0.65
2 | Bagdad | SE (135) | 90 degrees (vertical) | 0.56
2 | Bagdad | SSE (157.5) | 0 degrees (horizontal) | 0.93
2 | Bagdad | SSE (157.5) | 10 degrees | 0.97
2 | Bagdad | SSE (157.5) | 20 degrees | 0.99
2 | Bagdad | SSE (157.5) | 30 degrees | 0.99
2 | Bagdad | SSE (157.5) | 40 degrees | 0.96
2 | Bagdad | SSE (157.5) | 50 degrees | 0.92
2 | Bagdad | SSE (157.5) | 60 degrees | 0.85
2 | Bagdad | SSE (157.5) | 70 degrees | 0.77
2 | Bagdad | SSE (157.5) | 80 degrees | 0.67
2 | Bagdad | SSE (157.5) | 90 degrees (vertical) | 0.57
2 | Bagdad | S (180) | 0 degrees (horizontal) | 0.93
2 | Bagdad | S (180) | 10 degrees | 0.98
2 | Bagdad | S (180) | 20 degrees | 1
2 | Bagdad | S (180) | 30 degrees | 1
2 | Bagdad | S (180) | 40 degrees | 0.98
2 | Bagdad | S (180) | 50 degrees | 0.93
2 | Bagdad | S (180) | 60 degrees | 0.86
2 | Bagdad | S (180) | 70 degrees | 0.78
2 | Bagdad | S (180) | 80 degrees | 0.68
2 | Bagdad | S (180) | 90 degrees (vertical) | 0.57
2 | Bagdad | SSW (202.5) | 0 degrees (horizontal) | 0.93
2 | Bagdad | SSW (202.5) | 10 degrees | 0.97
2 | Bagdad | SSW (202.5) | 20 degrees | 0.99
2 | Bagdad | SSW (202.5) | 30 degrees | 0.99
2 | Bagdad | SSW (202.5) | 40 degrees | 0.96
2 | Bagdad | SSW (202.5) | 50 degrees | 0.92
2 | Bagdad | SSW (202.5) | 60 degrees | 0.85
2 | Bagdad | SSW (202.5) | 70 degrees | 0.77
2 | Bagdad | SSW (202.5) | 80 degrees | 0.67
2 | Bagdad | SSW (202.5) | 90 degrees (vertical) | 0.57
2 | Bagdad | SW (225) | 0 degrees (horizontal) | 0.93
2 | Bagdad | SW (225) | 10 degrees | 0.96
2 | Bagdad | SW (225) | 20 degrees | 0.97
2 | Bagdad | SW (225) | 30 degrees | 0.96
2 | Bagdad | SW (225) | 40 degrees | 0.93
2 | Bagdad | SW (225) | 50 degrees | 0.88
2 | Bagdad | SW (225) | 60 degrees | 0.81
2 | Bagdad | SW (225) | 70 degrees | 0.74
2 | Bagdad | SW (225) | 80 degrees | 0.65
2 | Bagdad | SW (225) | 90 degrees (vertical) | 0.56
2 | Bagdad | WSW (247.5) | 0 degrees (horizontal) | 0.93
2 | Bagdad | WSW (247.5) | 10 degrees | 0.94
2 | Bagdad | WSW (247.5) | 20 degrees | 0.93
2 | Bagdad | WSW (247.5) | 30 degrees | 0.91
2 | Bagdad | WSW (247.5) | 40 degrees | 0.87
2 | Bagdad | WSW (247.5) | 50 degrees | 0.82
2 | Bagdad | WSW (247.5) | 60 degrees | 0.75
2 | Bagdad | WSW (247.5) | 70 degrees | 0.68
2 | Bagdad | WSW (247.5) | 80 degrees | 0.6
2 | Bagdad | WSW (247.5) | 90 degrees (vertical) | 0.53
2 | Bagdad | W (270) | 0 degrees (horizontal) | 0.93
2 | Bagdad | W (270) | 10 degrees | 0.92
2 | Bagdad | W (270) | 20 degrees | 0.89
2 | Bagdad | W (270) | 30 degrees | 0.85
2 | Bagdad | W (270) | 40 degrees | 0.8
2 | Bagdad | W (270) | 50 degrees | 0.74
2 | Bagdad | W (270) | 60 degrees | 0.68
2 | Bagdad | W (270) | 70 degrees | 0.61
2 | Bagdad | W (270) | 80 degrees | 0.54
2 | Bagdad | W (270) | 90 degrees (vertical) | 0.47
2 | Bagdad | WNW (292.5) | 0 degrees (horizontal) | 0.93
2 | Bagdad | WNW (292.5) | 10 degrees | 0.9
2 | Bagdad | WNW (292.5) | 20 degrees | 0.85
2 | Bagdad | WNW (292.5) | 30 degrees | 0.79
2 | Bagdad | WNW (292.5) | 40 degrees | 0.73
2 | Bagdad | WNW (292.5) | 50 degrees | 0.66
2 | Bagdad | WNW (292.5) | 60 degrees | 0.59
2 | Bagdad | WNW (292.5) | 70 degrees | 0.52
2 | Bagdad | WNW (292.5) | 80 degrees | 0.46
2 | Bagdad | WNW (292.5) | 90 degrees (vertical) | 0.41
2 | Bagdad | NW (315) | 0 degrees (horizontal) | 0.93
2 | Bagdad | NW (315) | 10 degrees | 0.88
2 | Bagdad | NW (315) | 20 degrees | 0.82
2 | Bagdad | NW (315) | 30 degrees | 0.74
2 | Bagdad | NW (315) | 40 degrees | 0.65
2 | Bagdad | NW (315) | 50 degrees | 0.57
2 | Bagdad | NW (315) | 60 degrees | 0.49
2 | Bagdad | NW (315) | 70 degrees | 0.43
2 | Bagdad | NW (315) | 80 degrees | 0.38
2 | Bagdad | NW (315) | 90 degrees (vertical) | 0.33
2 | Bagdad | NNW (337.5) | 0 degrees (horizontal) | 0.93
2 | Bagdad | NNW (337.5) | 10 degrees | 0.87
2 | Bagdad | NNW (337.5) | 20 degrees | 0.79
2 | Bagdad | NNW (337.5) | 30 degrees | 0.7
2 | Bagdad | NNW (337.5) | 40 degrees | 0.6
2 | Bagdad | NNW (337.5) | 50 degrees | 0.51
2 | Bagdad | NNW (337.5) | 60 degrees | 0.42
2 | Bagdad | NNW (337.5) | 70 degrees | 0.35
2 | Bagdad | NNW (337.5) | 80 degrees | 0.3
2 | Bagdad | NNW (337.5) | 90 degrees (vertical) | 0.27
3 | Boston | N ( 0 degrees) | 0 degrees (horizontal) | 0.89
3 | Boston | N ( 0 degrees) | 10 degrees | 0.81
3 | Boston | N ( 0 degrees) | 20 degrees | 0.72
3 | Boston | N ( 0 degrees) | 30 degrees | 0.63
3 | Boston | N ( 0 degrees) | 40 degrees | 0.54
3 | Boston | N ( 0 degrees) | 50 degrees | 0.47
3 | Boston | N ( 0 degrees) | 60 degrees | 0.4
3 | Boston | N ( 0 degrees) | 70 degrees | 0.35
3 | Boston | N ( 0 degrees) | 80 degrees | 0.32
3 | Boston | N ( 0 degrees) | 90 degrees (vertical) | 0.3
3 | Boston | NNE (22.5) | 0 degrees (horizontal) | 0.89
3 | Boston | NNE (22.5) | 10 degrees | 0.82
3 | Boston | NNE (22.5) | 20 degrees | 0.73
3 | Boston | NNE (22.5) | 30 degrees | 0.64
3 | Boston | NNE (22.5) | 40 degrees | 0.56
3 | Boston | NNE (22.5) | 50 degrees | 0.49
3 | Boston | NNE (22.5) | 60 degrees | 0.42
3 | Boston | NNE (22.5) | 70 degrees | 0.38
3 | Boston | NNE (22.5) | 80 degrees | 0.35
3 | Boston | NNE (22.5) | 90 degrees (vertical) | 0.32
3 | Boston | NE (45) | 0 degrees (horizontal) | 0.89
3 | Boston | NE (45) | 10 degrees | 0.83
3 | Boston | NE (45) | 20 degrees | 0.76
3 | Boston | NE (45) | 30 degrees | 0.69
3 | Boston | NE (45) | 40 degrees | 0.61
3 | Boston | NE (45) | 50 degrees | 0.55
3 | Boston | NE (45) | 60 degrees | 0.49
3 | Boston | NE (45) | 70 degrees | 0.44
3 | Boston | NE (45) | 80 degrees | 0.4
3 | Boston | NE (45) | 90 degrees (vertical) | 0.36
3 | Boston | ENE (67.5) | 0 degrees (horizontal) | 0.89
3 | Boston | ENE (67.5) | 10 degrees | 0.85
3 | Boston | ENE (67.5) | 20 degrees | 0.81
3 | Boston | ENE (67.5) | 30 degrees | 0.75
3 | Boston | ENE (67.5) | 40 degrees | 0.7
3 | Boston | ENE (67.5) | 50 degrees | 0.64
3 | Boston | ENE (67.5) | 60 degrees | 0.58
3 | Boston | ENE (67.5) | 70 degrees | 0.53
3 | Boston | ENE (67.5) | 80 degrees | 0.48
3 | Boston | ENE (67.5) | 90 degrees (vertical) | 0.43
3 | Boston | E (90) | 0 degrees (horizontal) | 0.89
3 | Boston | E (90) | 10 degrees | 0.88
3 | Boston | E (90) | 20 degrees | 0.86
3 | Boston | E (90) | 30 degrees | 0.82
3 | Boston | E (90) | 40 degrees | 0.78
3 | Boston | E (90) | 50 degrees | 0.73
3 | Boston | E (90) | 60 degrees | 0.68
3 | Boston | E (90) | 70 degrees | 0.62
3 | Boston | E (90) | 80 degrees | 0.56
3 | Boston | E (90) | 90 degrees (vertical) | 0.5
3 | Boston | ESE (112.5) | 0 degrees (horizontal) | 0.89
3 | Boston | ESE (112.5) | 10 degrees | 0.9
3 | Boston | ESE (112.5) | 20 degrees | 0.9
3 | Boston | ESE (112.5) | 30 degrees | 0.89
3 | Boston | ESE (112.5) | 40 degrees | 0.86
3 | Boston | ESE (112.5) | 50 degrees | 0.82
3 | Boston | ESE (112.5) | 60 degrees | 0.77
3 | Boston | ESE (112.5) | 70 degrees | 0.71
3 | Boston | ESE (112.5) | 80 degrees | 0.64
3 | Boston | ESE (112.5) | 90 degrees (vertical) | 0.57
3 | Boston | SE (135) | 0 degrees (horizontal) | 0.89
3 | Boston | SE (135) | 10 degrees | 0.92
3 | Boston | SE (135) | 20 degrees | 0.94
3 | Boston | SE (135) | 30 degrees | 0.95
3 | Boston | SE (135) | 40 degrees | 0.93
3 | Boston | SE (135) | 50 degrees | 0.9
3 | Boston | SE (135) | 60 degrees | 0.85
3 | Boston | SE (135) | 70 degrees | 0.79
3 | Boston | SE (135) | 80 degrees | 0.72
3 | Boston | SE (135) | 90 degrees (vertical) | 0.64
3 | Boston | SSE (157.5) | 0 degrees (horizontal) | 0.89
3 | Boston | SSE (157.5) | 10 degrees | 0.94
3 | Boston | SSE (157.5) | 20 degrees | 0.97
3 | Boston | SSE (157.5) | 30 degrees | 0.99
3 | Boston | SSE (157.5) | 40 degrees | 0.98
3 | Boston | SSE (157.5) | 50 degrees | 0.95
3 | Boston | SSE (157.5) | 60 degrees | 0.91
3 | Boston | SSE (157.5) | 70 degrees | 0.85
3 | Boston | SSE (157.5) | 80 degrees | 0.77
3 | Boston | SSE (157.5) | 90 degrees (vertical) | 0.68
3 | Boston | S (180) | 0 degrees (horizontal) | 0.89
3 | Boston | S (180) | 10 degrees | 0.94
3 | Boston | S (180) | 20 degrees | 0.98
3 | Boston | S (180) | 30 degrees | 1
3 | Boston | S (180) | 40 degrees | 1
3 | Boston | S (180) | 50 degrees | 0.97
3 | Boston | S (180) | 60 degrees | 0.93
3 | Boston | S (180) | 70 degrees | 0.86
3 | Boston | S (180) | 80 degrees | 0.78
3 | Boston | S (180) | 90 degrees (vertical) | 0.69
3 | Boston | SSW (202.5) | 0 degrees (horizontal) | 0.89
3 | Boston | SSW (202.5) | 10 degrees | 0.94
3 | Boston | SSW (202.5) | 20 degrees | 0.97
3 | Boston | SSW (202.5) | 30 degrees | 0.99
3 | Boston | SSW (202.5) | 40 degrees | 0.98
3 | Boston | SSW (202.5) | 50 degrees | 0.95
3 | Boston | SSW (202.5) | 60 degrees | 0.91
3 | Boston | SSW (202.5) | 70 degrees | 0.85
3 | Boston | SSW (202.5) | 80 degrees | 0.77
3 | Boston | SSW (202.5) | 90 degrees (vertical) | 0.68
3 | Boston | SW (225) | 0 degrees (horizontal) | 0.89
3 | Boston | SW (225) | 10 degrees | 0.92
3 | Boston | SW (225) | 20 degrees | 0.94
3 | Boston | SW (225) | 30 degrees | 0.95
3 | Boston | SW (225) | 40 degrees | 0.93
3 | Boston | SW (225) | 50 degrees | 0.9
3 | Boston | SW (225) | 60 degrees | 0.85
3 | Boston | SW (225) | 70 degrees | 0.79
3 | Boston | SW (225) | 80 degrees | 0.72
3 | Boston | SW (225) | 90 degrees (vertical) | 0.64
3 | Boston | WSW (247.5) | 0 degrees (horizontal) | 0.89
3 | Boston | WSW (247.5) | 10 degrees | 0.9
3 | Boston | WSW (247.5) | 20 degrees | 0.9
3 | Boston | WSW (247.5) | 30 degrees | 0.89
3 | Boston | WSW (247.5) | 40 degrees | 0.86
3 | Boston | WSW (247.5) | 50 degrees | 0.82
3 | Boston | WSW (247.5) | 60 degrees | 0.77
3 | Boston | WSW (247.5) | 70 degrees | 0.71
3 | Boston | WSW (247.5) | 80 degrees | 0.64
3 | Boston | WSW (247.5) | 90 degrees (vertical) | 0.57
3 | Boston | W (270) | 0 degrees (horizontal) | 0.89
3 | Boston | W (270) | 10 degrees | 0.88
3 | Boston | W (270) | 20 degrees | 0.86
3 | Boston | W (270) | 30 degrees | 0.82
3 | Boston | W (270) | 40 degrees | 0.78
3 | Boston | W (270) | 50 degrees | 0.73
3 | Boston | W (270) | 60 degrees | 0.68
3 | Boston | W (270) | 70 degrees | 0.62
3 | Boston | W (270) | 80 degrees | 0.56
3 | Boston | W (270) | 90 degrees (vertical) | 0.5
3 | Boston | WNW (292.5) | 0 degrees (horizontal) | 0.89
3 | Boston | WNW (292.5) | 10 degrees | 0.85
3 | Boston | WNW (292.5) | 20 degrees | 0.81
3 | Boston | WNW (292.5) | 30 degrees | 0.75
3 | Boston | WNW (292.5) | 40 degrees | 0.7
3 | Boston | WNW (292.5) | 50 degrees | 0.64
3 | Boston | WNW (292.5) | 60 degrees | 0.58
3 | Boston | WNW (292.5) | 70 degrees | 0.53
3 | Boston | WNW (292.5) | 80 degrees | 0.48
3 | Boston | WNW (292.5) | 90 degrees (vertical) | 0.43
3 | Boston | NW (315) | 0 degrees (horizontal) | 0.89
3 | Boston | NW (315) | 10 degrees | 0.83
3 | Boston | NW (315) | 20 degrees | 0.76
3 | Boston | NW (315) | 30 degrees | 0.69
3 | Boston | NW (315) | 40 degrees | 0.61
3 | Boston | NW (315) | 50 degrees | 0.55
3 | Boston | NW (315) | 60 degrees | 0.49
3 | Boston | NW (315) | 70 degrees | 0.44
3 | Boston | NW (315) | 80 degrees | 0.4
3 | Boston | NW (315) | 90 degrees (vertical) | 0.36
3 | Boston | NNW (337.5) | 0 degrees (horizontal) | 0.89
3 | Boston | NNW (337.5) | 10 degrees | 0.82
3 | Boston | NNW (337.5) | 20 degrees | 0.73
3 | Boston | NNW (337.5) | 30 degrees | 0.64
3 | Boston | NNW (337.5) | 40 degrees | 0.56
3 | Boston | NNW (337.5) | 50 degrees | 0.49
3 | Boston | NNW (337.5) | 60 degrees | 0.42
3 | Boston | NNW (337.5) | 70 degrees | 0.38
3 | Boston | NNW (337.5) | 80 degrees | 0.35
3 | Boston | NNW (337.5) | 90 degrees (vertical) | 0.32
4 | Buenos Aires | N ( 0 degrees) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | N ( 0 degrees) | 10 degrees | 0.97
4 | Buenos Aires | N ( 0 degrees) | 20 degrees | 1
4 | Buenos Aires | N ( 0 degrees) | 30 degrees | 1
4 | Buenos Aires | N ( 0 degrees) | 40 degrees | 0.98
4 | Buenos Aires | N ( 0 degrees) | 50 degrees | 0.94
4 | Buenos Aires | N ( 0 degrees) | 60 degrees | 0.88
4 | Buenos Aires | N ( 0 degrees) | 70 degrees | 0.81
4 | Buenos Aires | N ( 0 degrees) | 80 degrees | 0.71
4 | Buenos Aires | N ( 0 degrees) | 90 degrees (vertical) | 0.61
4 | Buenos Aires | NNE (22.5) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | NNE (22.5) | 10 degrees | 0.97
4 | Buenos Aires | NNE (22.5) | 20 degrees | 0.99
4 | Buenos Aires | NNE (22.5) | 30 degrees | 0.99
4 | Buenos Aires | NNE (22.5) | 40 degrees | 0.97
4 | Buenos Aires | NNE (22.5) | 50 degrees | 0.93
4 | Buenos Aires | NNE (22.5) | 60 degrees | 0.87
4 | Buenos Aires | NNE (22.5) | 70 degrees | 0.79
4 | Buenos Aires | NNE (22.5) | 80 degrees | 0.7
4 | Buenos Aires | NNE (22.5) | 90 degrees (vertical) | 0.61
4 | Buenos Aires | NE (45) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | NE (45) | 10 degrees | 0.96
4 | Buenos Aires | NE (45) | 20 degrees | 0.97
4 | Buenos Aires | NE (45) | 30 degrees | 0.96
4 | Buenos Aires | NE (45) | 40 degrees | 0.93
4 | Buenos Aires | NE (45) | 50 degrees | 0.89
4 | Buenos Aires | NE (45) | 60 degrees | 0.83
4 | Buenos Aires | NE (45) | 70 degrees | 0.75
4 | Buenos Aires | NE (45) | 80 degrees | 0.67
4 | Buenos Aires | NE (45) | 90 degrees (vertical) | 0.58
4 | Buenos Aires | ENE (67.5) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | ENE (67.5) | 10 degrees | 0.94
4 | Buenos Aires | ENE (67.5) | 20 degrees | 0.93
4 | Buenos Aires | ENE (67.5) | 30 degrees | 0.91
4 | Buenos Aires | ENE (67.5) | 40 degrees | 0.87
4 | Buenos Aires | ENE (67.5) | 50 degrees | 0.82
4 | Buenos Aires | ENE (67.5) | 60 degrees | 0.76
4 | Buenos Aires | ENE (67.5) | 70 degrees | 0.69
4 | Buenos Aires | ENE (67.5) | 80 degrees | 0.62
4 | Buenos Aires | ENE (67.5) | 90 degrees (vertical) | 0.54
4 | Buenos Aires | E (90) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | E (90) | 10 degrees | 0.92
4 | Buenos Aires | E (90) | 20 degrees | 0.89
4 | Buenos Aires | E (90) | 30 degrees | 0.85
4 | Buenos Aires | E (90) | 40 degrees | 0.8
4 | Buenos Aires | E (90) | 50 degrees | 0.75
4 | Buenos Aires | E (90) | 60 degrees | 0.68
4 | Buenos Aires | E (90) | 70 degrees | 0.62
4 | Buenos Aires | E (90) | 80 degrees | 0.55
4 | Buenos Aires | E (90) | 90 degrees (vertical) | 0.49
4 | Buenos Aires | ESE (112.5) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | ESE (112.5) | 10 degrees | 0.9
4 | Buenos Aires | ESE (112.5) | 20 degrees | 0.85
4 | Buenos Aires | ESE (112.5) | 30 degrees | 0.79
4 | Buenos Aires | ESE (112.5) | 40 degrees | 0.73
4 | Buenos Aires | ESE (112.5) | 50 degrees | 0.66
4 | Buenos Aires | ESE (112.5) | 60 degrees | 0.6
4 | Buenos Aires | ESE (112.5) | 70 degrees | 0.54
4 | Buenos Aires | ESE (112.5) | 80 degrees | 0.48
4 | Buenos Aires | ESE (112.5) | 90 degrees (vertical) | 0.42
4 | Buenos Aires | SE (135) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | SE (135) | 10 degrees | 0.88
4 | Buenos Aires | SE (135) | 20 degrees | 0.81
4 | Buenos Aires | SE (135) | 30 degrees | 0.74
4 | Buenos Aires | SE (135) | 40 degrees | 0.66
4 | Buenos Aires | SE (135) | 50 degrees | 0.58
4 | Buenos Aires | SE (135) | 60 degrees | 0.51
4 | Buenos Aires | SE (135) | 70 degrees | 0.45
4 | Buenos Aires | SE (135) | 80 degrees | 0.4
4 | Buenos Aires | SE (135) | 90 degrees (vertical) | 0.36
4 | Buenos Aires | SSE (157.5) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | SSE (157.5) | 10 degrees | 0.86
4 | Buenos Aires | SSE (157.5) | 20 degrees | 0.79
4 | Buenos Aires | SSE (157.5) | 30 degrees | 0.7
4 | Buenos Aires | SSE (157.5) | 40 degrees | 0.61
4 | Buenos Aires | SSE (157.5) | 50 degrees | 0.52
4 | Buenos Aires | SSE (157.5) | 60 degrees | 0.45
4 | Buenos Aires | SSE (157.5) | 70 degrees | 0.38
4 | Buenos Aires | SSE (157.5) | 80 degrees | 0.34
4 | Buenos Aires | SSE (157.5) | 90 degrees (vertical) | 0.31
4 | Buenos Aires | S (180) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | S (180) | 10 degrees | 0.86
4 | Buenos Aires | S (180) | 20 degrees | 0.78
4 | Buenos Aires | S (180) | 30 degrees | 0.68
4 | Buenos Aires | S (180) | 40 degrees | 0.59
4 | Buenos Aires | S (180) | 50 degrees | 0.51
4 | Buenos Aires | S (180) | 60 degrees | 0.43
4 | Buenos Aires | S (180) | 70 degrees | 0.36
4 | Buenos Aires | S (180) | 80 degrees | 0.31
4 | Buenos Aires | S (180) | 90 degrees (vertical) | 0.29
4 | Buenos Aires | SSW (202.5) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | SSW (202.5) | 10 degrees | 0.86
4 | Buenos Aires | SSW (202.5) | 20 degrees | 0.79
4 | Buenos Aires | SSW (202.5) | 30 degrees | 0.7
4 | Buenos Aires | SSW (202.5) | 40 degrees | 0.61
4 | Buenos Aires | SSW (202.5) | 50 degrees | 0.52
4 | Buenos Aires | SSW (202.5) | 60 degrees | 0.45
4 | Buenos Aires | SSW (202.5) | 70 degrees | 0.38
4 | Buenos Aires | SSW (202.5) | 80 degrees | 0.34
4 | Buenos Aires | SSW (202.5) | 90 degrees (vertical) | 0.31
4 | Buenos Aires | SW (225) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | SW (225) | 10 degrees | 0.88
4 | Buenos Aires | SW (225) | 20 degrees | 0.81
4 | Buenos Aires | SW (225) | 30 degrees | 0.74
4 | Buenos Aires | SW (225) | 40 degrees | 0.66
4 | Buenos Aires | SW (225) | 50 degrees | 0.58
4 | Buenos Aires | SW (225) | 60 degrees | 0.51
4 | Buenos Aires | SW (225) | 70 degrees | 0.45
4 | Buenos Aires | SW (225) | 80 degrees | 0.4
4 | Buenos Aires | SW (225) | 90 degrees (vertical) | 0.36
4 | Buenos Aires | WSW (247.5) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | WSW (247.5) | 10 degrees | 0.9
4 | Buenos Aires | WSW (247.5) | 20 degrees | 0.85
4 | Buenos Aires | WSW (247.5) | 30 degrees | 0.79
4 | Buenos Aires | WSW (247.5) | 40 degrees | 0.73
4 | Buenos Aires | WSW (247.5) | 50 degrees | 0.66
4 | Buenos Aires | WSW (247.5) | 60 degrees | 0.6
4 | Buenos Aires | WSW (247.5) | 70 degrees | 0.54
4 | Buenos Aires | WSW (247.5) | 80 degrees | 0.48
4 | Buenos Aires | WSW (247.5) | 90 degrees (vertical) | 0.42
4 | Buenos Aires | W (270) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | W (270) | 10 degrees | 0.92
4 | Buenos Aires | W (270) | 20 degrees | 0.89
4 | Buenos Aires | W (270) | 30 degrees | 0.85
4 | Buenos Aires | W (270) | 40 degrees | 0.8
4 | Buenos Aires | W (270) | 50 degrees | 0.75
4 | Buenos Aires | W (270) | 60 degrees | 0.68
4 | Buenos Aires | W (270) | 70 degrees | 0.62
4 | Buenos Aires | W (270) | 80 degrees | 0.55
4 | Buenos Aires | W (270) | 90 degrees (vertical) | 0.49
4 | Buenos Aires | WNW (292.5) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | WNW (292.5) | 10 degrees | 0.94
4 | Buenos Aires | WNW (292.5) | 20 degrees | 0.93
4 | Buenos Aires | WNW (292.5) | 30 degrees | 0.91
4 | Buenos Aires | WNW (292.5) | 40 degrees | 0.87
4 | Buenos Aires | WNW (292.5) | 50 degrees | 0.82
4 | Buenos Aires | WNW (292.5) | 60 degrees | 0.76
4 | Buenos Aires | WNW (292.5) | 70 degrees | 0.69
4 | Buenos Aires | WNW (292.5) | 80 degrees | 0.62
4 | Buenos Aires | WNW (292.5) | 90 degrees (vertical) | 0.54
4 | Buenos Aires | NW (315) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | NW (315) | 10 degrees | 0.96
4 | Buenos Aires | NW (315) | 20 degrees | 0.97
4 | Buenos Aires | NW (315) | 30 degrees | 0.96
4 | Buenos Aires | NW (315) | 40 degrees | 0.93
4 | Buenos Aires | NW (315) | 50 degrees | 0.89
4 | Buenos Aires | NW (315) | 60 degrees | 0.83
4 | Buenos Aires | NW (315) | 70 degrees | 0.75
4 | Buenos Aires | NW (315) | 80 degrees | 0.67
4 | Buenos Aires | NW (315) | 90 degrees (vertical) | 0.58
4 | Buenos Aires | NNW (337.5) | 0 degrees (horizontal) | 0.93
4 | Buenos Aires | NNW (337.5) | 10 degrees | 0.97
4 | Buenos Aires | NNW (337.5) | 20 degrees | 0.99
4 | Buenos Aires | NNW (337.5) | 30 degrees | 0.99
4 | Buenos Aires | NNW (337.5) | 40 degrees | 0.97
4 | Buenos Aires | NNW (337.5) | 50 degrees | 0.93
4 | Buenos Aires | NNW (337.5) | 60 degrees | 0.87
4 | Buenos Aires | NNW (337.5) | 70 degrees | 0.79
4 | Buenos Aires | NNW (337.5) | 80 degrees | 0.7
4 | Buenos Aires | NNW (337.5) | 90 degrees (vertical) | 0.61
5 | Canberra | N ( 0 degrees) | 0 degrees (horizontal) | 0.92
5 | Canberra | N ( 0 degrees) | 10 degrees | 0.97
5 | Canberra | N ( 0 degrees) | 20 degrees | 1
5 | Canberra | N ( 0 degrees) | 30 degrees | 1
5 | Canberra | N ( 0 degrees) | 40 degrees | 0.98
5 | Canberra | N ( 0 degrees) | 50 degrees | 0.95
5 | Canberra | N ( 0 degrees) | 60 degrees | 0.89
5 | Canberra | N ( 0 degrees) | 70 degrees | 0.81
5 | Canberra | N ( 0 degrees) | 80 degrees | 0.72
5 | Canberra | N ( 0 degrees) | 90 degrees (vertical) | 0.62
5 | Canberra | NNE (22.5) | 0 degrees (horizontal) | 0.92
5 | Canberra | NNE (22.5) | 10 degrees | 0.97
5 | Canberra | NNE (22.5) | 20 degrees | 0.99
5 | Canberra | NNE (22.5) | 30 degrees | 0.99
5 | Canberra | NNE (22.5) | 40 degrees | 0.97
5 | Canberra | NNE (22.5) | 50 degrees | 0.93
5 | Canberra | NNE (22.5) | 60 degrees | 0.87
5 | Canberra | NNE (22.5) | 70 degrees | 0.8
5 | Canberra | NNE (22.5) | 80 degrees | 0.71
5 | Canberra | NNE (22.5) | 90 degrees (vertical) | 0.62
5 | Canberra | NE (45) | 0 degrees (horizontal) | 0.92
5 | Canberra | NE (45) | 10 degrees | 0.95
5 | Canberra | NE (45) | 20 degrees | 0.96
5 | Canberra | NE (45) | 30 degrees | 0.96
5 | Canberra | NE (45) | 40 degrees | 0.93
5 | Canberra | NE (45) | 50 degrees | 0.89
5 | Canberra | NE (45) | 60 degrees | 0.83
5 | Canberra | NE (45) | 70 degrees | 0.76
5 | Canberra | NE (45) | 80 degrees | 0.68
5 | Canberra | NE (45) | 90 degrees (vertical) | 0.59
5 | Canberra | ENE (67.5) | 0 degrees (horizontal) | 0.92
5 | Canberra | ENE (67.5) | 10 degrees | 0.93
5 | Canberra | ENE (67.5) | 20 degrees | 0.93
5 | Canberra | ENE (67.5) | 30 degrees | 0.91
5 | Canberra | ENE (67.5) | 40 degrees | 0.87
5 | Canberra | ENE (67.5) | 50 degrees | 0.82
5 | Canberra | ENE (67.5) | 60 degrees | 0.76
5 | Canberra | ENE (67.5) | 70 degrees | 0.7
5 | Canberra | ENE (67.5) | 80 degrees | 0.62
5 | Canberra | ENE (67.5) | 90 degrees (vertical) | 0.55
5 | Canberra | E (90) | 0 degrees (horizontal) | 0.92
5 | Canberra | E (90) | 10 degrees | 0.91
5 | Canberra | E (90) | 20 degrees | 0.89
5 | Canberra | E (90) | 30 degrees | 0.85
5 | Canberra | E (90) | 40 degrees | 0.8
5 | Canberra | E (90) | 50 degrees | 0.75
5 | Canberra | E (90) | 60 degrees | 0.69
5 | Canberra | E (90) | 70 degrees | 0.62
5 | Canberra | E (90) | 80 degrees | 0.56
5 | Canberra | E (90) | 90 degrees (vertical) | 0.49
5 | Canberra | ESE (112.5) | 0 degrees (horizontal) | 0.92
5 | Canberra | ESE (112.5) | 10 degrees | 0.89
5 | Canberra | ESE (112.5) | 20 degrees | 0.85
5 | Canberra | ESE (112.5) | 30 degrees | 0.79
5 | Canberra | ESE (112.5) | 40 degrees | 0.73
5 | Canberra | ESE (112.5) | 50 degrees | 0.67
5 | Canberra | ESE (112.5) | 60 degrees | 0.6
5 | Canberra | ESE (112.5) | 70 degrees | 0.54
5 | Canberra | ESE (112.5) | 80 degrees | 0.48
5 | Canberra | ESE (112.5) | 90 degrees (vertical) | 0.43
5 | Canberra | SE (135) | 0 degrees (horizontal) | 0.92
5 | Canberra | SE (135) | 10 degrees | 0.87
5 | Canberra | SE (135) | 20 degrees | 0.81
5 | Canberra | SE (135) | 30 degrees | 0.74
5 | Canberra | SE (135) | 40 degrees | 0.66
5 | Canberra | SE (135) | 50 degrees | 0.59
5 | Canberra | SE (135) | 60 degrees | 0.52
5 | Canberra | SE (135) | 70 degrees | 0.46
5 | Canberra | SE (135) | 80 degrees | 0.41
5 | Canberra | SE (135) | 90 degrees (vertical) | 0.36
5 | Canberra | SSE (157.5) | 0 degrees (horizontal) | 0.92
5 | Canberra | SSE (157.5) | 10 degrees | 0.86
5 | Canberra | SSE (157.5) | 20 degrees | 0.78
5 | Canberra | SSE (157.5) | 30 degrees | 0.7
5 | Canberra | SSE (157.5) | 40 degrees | 0.61
5 | Canberra | SSE (157.5) | 50 degrees | 0.53
5 | Canberra | SSE (157.5) | 60 degrees | 0.46
5 | Canberra | SSE (157.5) | 70 degrees | 0.39
5 | Canberra | SSE (157.5) | 80 degrees | 0.35
5 | Canberra | SSE (157.5) | 90 degrees (vertical) | 0.32
5 | Canberra | S (180) | 0 degrees (horizontal) | 0.92
5 | Canberra | S (180) | 10 degrees | 0.86
5 | Canberra | S (180) | 20 degrees | 0.78
5 | Canberra | S (180) | 30 degrees | 0.68
5 | Canberra | S (180) | 40 degrees | 0.59
5 | Canberra | S (180) | 50 degrees | 0.51
5 | Canberra | S (180) | 60 degrees | 0.44
5 | Canberra | S (180) | 70 degrees | 0.37
5 | Canberra | S (180) | 80 degrees | 0.33
5 | Canberra | S (180) | 90 degrees (vertical) | 0.3
5 | Canberra | SSW (202.5) | 0 degrees (horizontal) | 0.92
5 | Canberra | SSW (202.5) | 10 degrees | 0.86
5 | Canberra | SSW (202.5) | 20 degrees | 0.78
5 | Canberra | SSW (202.5) | 30 degrees | 0.7
5 | Canberra | SSW (202.5) | 40 degrees | 0.61
5 | Canberra | SSW (202.5) | 50 degrees | 0.53
5 | Canberra | SSW (202.5) | 60 degrees | 0.46
5 | Canberra | SSW (202.5) | 70 degrees | 0.39
5 | Canberra | SSW (202.5) | 80 degrees | 0.35
5 | Canberra | SSW (202.5) | 90 degrees (vertical) | 0.32
5 | Canberra | SW (225) | 0 degrees (horizontal) | 0.92
5 | Canberra | SW (225) | 10 degrees | 0.87
5 | Canberra | SW (225) | 20 degrees | 0.81
5 | Canberra | SW (225) | 30 degrees | 0.74
5 | Canberra | SW (225) | 40 degrees | 0.66
5 | Canberra | SW (225) | 50 degrees | 0.59
5 | Canberra | SW (225) | 60 degrees | 0.52
5 | Canberra | SW (225) | 70 degrees | 0.46
5 | Canberra | SW (225) | 80 degrees | 0.41
5 | Canberra | SW (225) | 90 degrees (vertical) | 0.36
5 | Canberra | WSW (247.5) | 0 degrees (horizontal) | 0.92
5 | Canberra | WSW (247.5) | 10 degrees | 0.89
5 | Canberra | WSW (247.5) | 20 degrees | 0.85
5 | Canberra | WSW (247.5) | 30 degrees | 0.79
5 | Canberra | WSW (247.5) | 40 degrees | 0.73
5 | Canberra | WSW (247.5) | 50 degrees | 0.67
5 | Canberra | WSW (247.5) | 60 degrees | 0.6
5 | Canberra | WSW (247.5) | 70 degrees | 0.54
5 | Canberra | WSW (247.5) | 80 degrees | 0.48
5 | Canberra | WSW (247.5) | 90 degrees (vertical) | 0.43
5 | Canberra | W (270) | 0 degrees (horizontal) | 0.92
5 | Canberra | W (270) | 10 degrees | 0.91
5 | Canberra | W (270) | 20 degrees | 0.89
5 | Canberra | W (270) | 30 degrees | 0.85
5 | Canberra | W (270) | 40 degrees | 0.8
5 | Canberra | W (270) | 50 degrees | 0.75
5 | Canberra | W (270) | 60 degrees | 0.69
5 | Canberra | W (270) | 70 degrees | 0.62
5 | Canberra | W (270) | 80 degrees | 0.56
5 | Canberra | W (270) | 90 degrees (vertical) | 0.49
5 | Canberra | WNW (292.5) | 0 degrees (horizontal) | 0.92
5 | Canberra | WNW (292.5) | 10 degrees | 0.93
5 | Canberra | WNW (292.5) | 20 degrees | 0.93
5 | Canberra | WNW (292.5) | 30 degrees | 0.91
5 | Canberra | WNW (292.5) | 40 degrees | 0.87
5 | Canberra | WNW (292.5) | 50 degrees | 0.82
5 | Canberra | WNW (292.5) | 60 degrees | 0.76
5 | Canberra | WNW (292.5) | 70 degrees | 0.7
5 | Canberra | WNW (292.5) | 80 degrees | 0.62
5 | Canberra | WNW (292.5) | 90 degrees (vertical) | 0.55
5 | Canberra | NW (315) | 0 degrees (horizontal) | 0.92
5 | Canberra | NW (315) | 10 degrees | 0.95
5 | Canberra | NW (315) | 20 degrees | 0.96
5 | Canberra | NW (315) | 30 degrees | 0.96
5 | Canberra | NW (315) | 40 degrees | 0.93
5 | Canberra | NW (315) | 50 degrees | 0.89
5 | Canberra | NW (315) | 60 degrees | 0.83
5 | Canberra | NW (315) | 70 degrees | 0.76
5 | Canberra | NW (315) | 80 degrees | 0.68
5 | Canberra | NW (315) | 90 degrees (vertical) | 0.59
5 | Canberra | NNW (337.5) | 0 degrees (horizontal) | 0.92
5 | Canberra | NNW (337.5) | 10 degrees | 0.97
5 | Canberra | NNW (337.5) | 20 degrees | 0.99
5 | Canberra | NNW (337.5) | 30 degrees | 0.99
5 | Canberra | NNW (337.5) | 40 degrees | 0.97
5 | Canberra | NNW (337.5) | 50 degrees | 0.93
5 | Canberra | NNW (337.5) | 60 degrees | 0.87
5 | Canberra | NNW (337.5) | 70 degrees | 0.8
5 | Canberra | NNW (337.5) | 80 degrees | 0.71
5 | Canberra | NNW (337.5) | 90 degrees (vertical) | 0.62
6 | Djakarta | N ( 0 degrees) | 0 degrees (horizontal) | 1
6 | Djakarta | N ( 0 degrees) | 10 degrees | 1
6 | Djakarta | N ( 0 degrees) | 20 degrees | 0.98
6 | Djakarta | N ( 0 degrees) | 30 degrees | 0.95
6 | Djakarta | N ( 0 degrees) | 40 degrees | 0.89
6 | Djakarta | N ( 0 degrees) | 50 degrees | 0.82
6 | Djakarta | N ( 0 degrees) | 60 degrees | 0.74
6 | Djakarta | N ( 0 degrees) | 70 degrees | 0.64
6 | Djakarta | N ( 0 degrees) | 80 degrees | 0.55
6 | Djakarta | N ( 0 degrees) | 90 degrees (vertical) | 0.47
6 | Djakarta | NNE (22.5) | 0 degrees (horizontal) | 1
6 | Djakarta | NNE (22.5) | 10 degrees | 1
6 | Djakarta | NNE (22.5) | 20 degrees | 0.98
6 | Djakarta | NNE (22.5) | 30 degrees | 0.95
6 | Djakarta | NNE (22.5) | 40 degrees | 0.89
6 | Djakarta | NNE (22.5) | 50 degrees | 0.82
6 | Djakarta | NNE (22.5) | 60 degrees | 0.74
6 | Djakarta | NNE (22.5) | 70 degrees | 0.65
6 | Djakarta | NNE (22.5) | 80 degrees | 0.56
6 | Djakarta | NNE (22.5) | 90 degrees (vertical) | 0.47
6 | Djakarta | NE (45) | 0 degrees (horizontal) | 1
6 | Djakarta | NE (45) | 10 degrees | 1
6 | Djakarta | NE (45) | 20 degrees | 0.98
6 | Djakarta | NE (45) | 30 degrees | 0.94
6 | Djakarta | NE (45) | 40 degrees | 0.88
6 | Djakarta | NE (45) | 50 degrees | 0.82
6 | Djakarta | NE (45) | 60 degrees | 0.74
6 | Djakarta | NE (45) | 70 degrees | 0.66
6 | Djakarta | NE (45) | 80 degrees | 0.57
6 | Djakarta | NE (45) | 90 degrees (vertical) | 0.49
6 | Djakarta | ENE (67.5) | 0 degrees (horizontal) | 1
6 | Djakarta | ENE (67.5) | 10 degrees | 0.99
6 | Djakarta | ENE (67.5) | 20 degrees | 0.97
6 | Djakarta | ENE (67.5) | 30 degrees | 0.93
6 | Djakarta | ENE (67.5) | 40 degrees | 0.88
6 | Djakarta | ENE (67.5) | 50 degrees | 0.81
6 | Djakarta | ENE (67.5) | 60 degrees | 0.74
6 | Djakarta | ENE (67.5) | 70 degrees | 0.66
6 | Djakarta | ENE (67.5) | 80 degrees | 0.58
6 | Djakarta | ENE (67.5) | 90 degrees (vertical) | 0.51
6 | Djakarta | E (90) | 0 degrees (horizontal) | 1
6 | Djakarta | E (90) | 10 degrees | 0.99
6 | Djakarta | E (90) | 20 degrees | 0.96
6 | Djakarta | E (90) | 30 degrees | 0.92
6 | Djakarta | E (90) | 40 degrees | 0.86
6 | Djakarta | E (90) | 50 degrees | 0.79
6 | Djakarta | E (90) | 60 degrees | 0.72
6 | Djakarta | E (90) | 70 degrees | 0.65
6 | Djakarta | E (90) | 80 degrees | 0.57
6 | Djakarta | E (90) | 90 degrees (vertical) | 0.5
6 | Djakarta | ESE (112.5) | 0 degrees (horizontal) | 1
6 | Djakarta | ESE (112.5) | 10 degrees | 0.98
6 | Djakarta | ESE (112.5) | 20 degrees | 0.95
6 | Djakarta | ESE (112.5) | 30 degrees | 0.9
6 | Djakarta | ESE (112.5) | 40 degrees | 0.84
6 | Djakarta | ESE (112.5) | 50 degrees | 0.77
6 | Djakarta | ESE (112.5) | 60 degrees | 0.7
6 | Djakarta | ESE (112.5) | 70 degrees | 0.62
6 | Djakarta | ESE (112.5) | 80 degrees | 0.55
6 | Djakarta | ESE (112.5) | 90 degrees (vertical) | 0.48
6 | Djakarta | SE (135) | 0 degrees (horizontal) | 1
6 | Djakarta | SE (135) | 10 degrees | 0.98
6 | Djakarta | SE (135) | 20 degrees | 0.94
6 | Djakarta | SE (135) | 30 degrees | 0.88
6 | Djakarta | SE (135) | 40 degrees | 0.82
6 | Djakarta | SE (135) | 50 degrees | 0.74
6 | Djakarta | SE (135) | 60 degrees | 0.66
6 | Djakarta | SE (135) | 70 degrees | 0.58
6 | Djakarta | SE (135) | 80 degrees | 0.5
6 | Djakarta | SE (135) | 90 degrees (vertical) | 0.44
6 | Djakarta | SSE (157.5) | 0 degrees (horizontal) | 1
6 | Djakarta | SSE (157.5) | 10 degrees | 0.97
6 | Djakarta | SSE (157.5) | 20 degrees | 0.93
6 | Djakarta | SSE (157.5) | 30 degrees | 0.87
6 | Djakarta | SSE (157.5) | 40 degrees | 0.8
6 | Djakarta | SSE (157.5) | 50 degrees | 0.71
6 | Djakarta | SSE (157.5) | 60 degrees | 0.62
6 | Djakarta | SSE (157.5) | 70 degrees | 0.54
6 | Djakarta | SSE (157.5) | 80 degrees | 0.46
6 | Djakarta | SSE (157.5) | 90 degrees (vertical) | 0.4
6 | Djakarta | S (180) | 0 degrees (horizontal) | 1
6 | Djakarta | S (180) | 10 degrees | 0.97
6 | Djakarta | S (180) | 20 degrees | 0.93
6 | Djakarta | S (180) | 30 degrees | 0.87
6 | Djakarta | S (180) | 40 degrees | 0.79
6 | Djakarta | S (180) | 50 degrees | 0.7
6 | Djakarta | S (180) | 60 degrees | 0.61
6 | Djakarta | S (180) | 70 degrees | 0.52
6 | Djakarta | S (180) | 80 degrees | 0.45
6 | Djakarta | S (180) | 90 degrees (vertical) | 0.39
6 | Djakarta | SSW (202.5) | 0 degrees (horizontal) | 1
6 | Djakarta | SSW (202.5) | 10 degrees | 0.97
6 | Djakarta | SSW (202.5) | 20 degrees | 0.93
6 | Djakarta | SSW (202.5) | 30 degrees | 0.87
6 | Djakarta | SSW (202.5) | 40 degrees | 0.8
6 | Djakarta | SSW (202.5) | 50 degrees | 0.71
6 | Djakarta | SSW (202.5) | 60 degrees | 0.62
6 | Djakarta | SSW (202.5) | 70 degrees | 0.54
6 | Djakarta | SSW (202.5) | 80 degrees | 0.46
6 | Djakarta | SSW (202.5) | 90 degrees (vertical) | 0.4
6 | Djakarta | SW (225) | 0 degrees (horizontal) | 1
6 | Djakarta | SW (225) | 10 degrees | 0.98
6 | Djakarta | SW (225) | 20 degrees | 0.94
6 | Djakarta | SW (225) | 30 degrees | 0.88
6 | Djakarta | SW (225) | 40 degrees | 0.82
6 | Djakarta | SW (225) | 50 degrees | 0.74
6 | Djakarta | SW (225) | 60 degrees | 0.66
6 | Djakarta | SW (225) | 70 degrees | 0.58
6 | Djakarta | SW (225) | 80 degrees | 0.5
6 | Djakarta | SW (225) | 90 degrees (vertical) | 0.44
6 | Djakarta | WSW (247.5) | 0 degrees (horizontal) | 1
6 | Djakarta | WSW (247.5) | 10 degrees | 0.98
6 | Djakarta | WSW (247.5) | 20 degrees | 0.95
6 | Djakarta | WSW (247.5) | 30 degrees | 0.9
6 | Djakarta | WSW (247.5) | 40 degrees | 0.84
6 | Djakarta | WSW (247.5) | 50 degrees | 0.77
6 | Djakarta | WSW (247.5) | 60 degrees | 0.7
6 | Djakarta | WSW (247.5) | 70 degrees | 0.62
6 | Djakarta | WSW (247.5) | 80 degrees | 0.55
6 | Djakarta | WSW (247.5) | 90 degrees (vertical) | 0.48
6 | Djakarta | W (270) | 0 degrees (horizontal) | 1
6 | Djakarta | W (270) | 10 degrees | 0.99
6 | Djakarta | W (270) | 20 degrees | 0.96
6 | Djakarta | W (270) | 30 degrees | 0.92
6 | Djakarta | W (270) | 40 degrees | 0.86
6 | Djakarta | W (270) | 50 degrees | 0.79
6 | Djakarta | W (270) | 60 degrees | 0.72
6 | Djakarta | W (270) | 70 degrees | 0.65
6 | Djakarta | W (270) | 80 degrees | 0.57
6 | Djakarta | W (270) | 90 degrees (vertical) | 0.5
6 | Djakarta | WNW (292.5) | 0 degrees (horizontal) | 1
6 | Djakarta | WNW (292.5) | 10 degrees | 0.99
6 | Djakarta | WNW (292.5) | 20 degrees | 0.97
6 | Djakarta | WNW (292.5) | 30 degrees | 0.93
6 | Djakarta | WNW (292.5) | 40 degrees | 0.88
6 | Djakarta | WNW (292.5) | 50 degrees | 0.81
6 | Djakarta | WNW (292.5) | 60 degrees | 0.74
6 | Djakarta | WNW (292.5) | 70 degrees | 0.66
6 | Djakarta | WNW (292.5) | 80 degrees | 0.58
6 | Djakarta | WNW (292.5) | 90 degrees (vertical) | 0.51
6 | Djakarta | NW (315) | 0 degrees (horizontal) | 1
6 | Djakarta | NW (315) | 10 degrees | 1
6 | Djakarta | NW (315) | 20 degrees | 0.98
6 | Djakarta | NW (315) | 30 degrees | 0.94
6 | Djakarta | NW (315) | 40 degrees | 0.88
6 | Djakarta | NW (315) | 50 degrees | 0.82
6 | Djakarta | NW (315) | 60 degrees | 0.74
6 | Djakarta | NW (315) | 70 degrees | 0.66
6 | Djakarta | NW (315) | 80 degrees | 0.57
6 | Djakarta | NW (315) | 90 degrees (vertical) | 0.49
6 | Djakarta | NNW (337.5) | 0 degrees (horizontal) | 1
6 | Djakarta | NNW (337.5) | 10 degrees | 1
6 | Djakarta | NNW (337.5) | 20 degrees | 0.98
6 | Djakarta | NNW (337.5) | 30 degrees | 0.95
6 | Djakarta | NNW (337.5) | 40 degrees | 0.89
6 | Djakarta | NNW (337.5) | 50 degrees | 0.82
6 | Djakarta | NNW (337.5) | 60 degrees | 0.74
6 | Djakarta | NNW (337.5) | 70 degrees | 0.65
6 | Djakarta | NNW (337.5) | 80 degrees | 0.56
6 | Djakarta | NNW (337.5) | 90 degrees (vertical) | 0.47
7 | Fortaleza | N ( 0 degrees) | 0 degrees (horizontal) | 1
7 | Fortaleza | N ( 0 degrees) | 10 degrees | 1
7 | Fortaleza | N ( 0 degrees) | 20 degrees | 0.97
7 | Fortaleza | N ( 0 degrees) | 30 degrees | 0.93
7 | Fortaleza | N ( 0 degrees) | 40 degrees | 0.86
7 | Fortaleza | N ( 0 degrees) | 50 degrees | 0.79
7 | Fortaleza | N ( 0 degrees) | 60 degrees | 0.69
7 | Fortaleza | N ( 0 degrees) | 70 degrees | 0.59
7 | Fortaleza | N ( 0 degrees) | 80 degrees | 0.51
7 | Fortaleza | N ( 0 degrees) | 90 degrees (vertical) | 0.43
7 | Fortaleza | NNE (22.5) | 0 degrees (horizontal) | 1
7 | Fortaleza | NNE (22.5) | 10 degrees | 1
7 | Fortaleza | NNE (22.5) | 20 degrees | 0.97
7 | Fortaleza | NNE (22.5) | 30 degrees | 0.93
7 | Fortaleza | NNE (22.5) | 40 degrees | 0.87
7 | Fortaleza | NNE (22.5) | 50 degrees | 0.79
7 | Fortaleza | NNE (22.5) | 60 degrees | 0.7
7 | Fortaleza | NNE (22.5) | 70 degrees | 0.61
7 | Fortaleza | NNE (22.5) | 80 degrees | 0.51
7 | Fortaleza | NNE (22.5) | 90 degrees (vertical) | 0.43
7 | Fortaleza | NE (45) | 0 degrees (horizontal) | 1
7 | Fortaleza | NE (45) | 10 degrees | 0.99
7 | Fortaleza | NE (45) | 20 degrees | 0.97
7 | Fortaleza | NE (45) | 30 degrees | 0.93
7 | Fortaleza | NE (45) | 40 degrees | 0.87
7 | Fortaleza | NE (45) | 50 degrees | 0.79
7 | Fortaleza | NE (45) | 60 degrees | 0.71
7 | Fortaleza | NE (45) | 70 degrees | 0.63
7 | Fortaleza | NE (45) | 80 degrees | 0.54
7 | Fortaleza | NE (45) | 90 degrees (vertical) | 0.46
7 | Fortaleza | ENE (67.5) | 0 degrees (horizontal) | 1
7 | Fortaleza | ENE (67.5) | 10 degrees | 0.99
7 | Fortaleza | ENE (67.5) | 20 degrees | 0.97
7 | Fortaleza | ENE (67.5) | 30 degrees | 0.92
7 | Fortaleza | ENE (67.5) | 40 degrees | 0.86
7 | Fortaleza | ENE (67.5) | 50 degrees | 0.8
7 | Fortaleza | ENE (67.5) | 60 degrees | 0.72
7 | Fortaleza | ENE (67.5) | 70 degrees | 0.64
7 | Fortaleza | ENE (67.5) | 80 degrees | 0.56
7 | Fortaleza | ENE (67.5) | 90 degrees (vertical) | 0.49
7 | Fortaleza | E (90) | 0 degrees (horizontal) | 1
7 | Fortaleza | E (90) | 10 degrees | 0.99
7 | Fortaleza | E (90) | 20 degrees | 0.96
7 | Fortaleza | E (90) | 30 degrees | 0.92
7 | Fortaleza | E (90) | 40 degrees | 0.86
7 | Fortaleza | E (90) | 50 degrees | 0.79
7 | Fortaleza | E (90) | 60 degrees | 0.72
7 | Fortaleza | E (90) | 70 degrees | 0.64
7 | Fortaleza | E (90) | 80 degrees | 0.56
7 | Fortaleza | E (90) | 90 degrees (vertical) | 0.49
7 | Fortaleza | ESE (112.5) | 0 degrees (horizontal) | 1
7 | Fortaleza | ESE (112.5) | 10 degrees | 0.99
7 | Fortaleza | ESE (112.5) | 20 degrees | 0.96
7 | Fortaleza | ESE (112.5) | 30 degrees | 0.91
7 | Fortaleza | ESE (112.5) | 40 degrees | 0.85
7 | Fortaleza | ESE (112.5) | 50 degrees | 0.77
7 | Fortaleza | ESE (112.5) | 60 degrees | 0.7
7 | Fortaleza | ESE (112.5) | 70 degrees | 0.62
7 | Fortaleza | ESE (112.5) | 80 degrees | 0.55
7 | Fortaleza | ESE (112.5) | 90 degrees (vertical) | 0.47
7 | Fortaleza | SE (135) | 0 degrees (horizontal) | 1
7 | Fortaleza | SE (135) | 10 degrees | 0.98
7 | Fortaleza | SE (135) | 20 degrees | 0.95
7 | Fortaleza | SE (135) | 30 degrees | 0.9
7 | Fortaleza | SE (135) | 40 degrees | 0.83
7 | Fortaleza | SE (135) | 50 degrees | 0.75
7 | Fortaleza | SE (135) | 60 degrees | 0.67
7 | Fortaleza | SE (135) | 70 degrees | 0.59
7 | Fortaleza | SE (135) | 80 degrees | 0.51
7 | Fortaleza | SE (135) | 90 degrees (vertical) | 0.43
7 | Fortaleza | SSE (157.5) | 0 degrees (horizontal) | 1
7 | Fortaleza | SSE (157.5) | 10 degrees | 0.98
7 | Fortaleza | SSE (157.5) | 20 degrees | 0.95
7 | Fortaleza | SSE (157.5) | 30 degrees | 0.89
7 | Fortaleza | SSE (157.5) | 40 degrees | 0.82
7 | Fortaleza | SSE (157.5) | 50 degrees | 0.73
7 | Fortaleza | SSE (157.5) | 60 degrees | 0.64
7 | Fortaleza | SSE (157.5) | 70 degrees | 0.55
7 | Fortaleza | SSE (157.5) | 80 degrees | 0.47
7 | Fortaleza | SSE (157.5) | 90 degrees (vertical) | 0.39
7 | Fortaleza | S (180) | 0 degrees (horizontal) | 1
7 | Fortaleza | S (180) | 10 degrees | 0.98
7 | Fortaleza | S (180) | 20 degrees | 0.94
7 | Fortaleza | S (180) | 30 degrees | 0.89
7 | Fortaleza | S (180) | 40 degrees | 0.81
7 | Fortaleza | S (180) | 50 degrees | 0.72
7 | Fortaleza | S (180) | 60 degrees | 0.62
7 | Fortaleza | S (180) | 70 degrees | 0.53
7 | Fortaleza | S (180) | 80 degrees | 0.46
7 | Fortaleza | S (180) | 90 degrees (vertical) | 0.39
7 | Fortaleza | SSW (202.5) | 0 degrees (horizontal) | 1
7 | Fortaleza | SSW (202.5) | 10 degrees | 0.98
7 | Fortaleza | SSW (202.5) | 20 degrees | 0.95
7 | Fortaleza | SSW (202.5) | 30 degrees | 0.89
7 | Fortaleza | SSW (202.5) | 40 degrees | 0.82
7 | Fortaleza | SSW (202.5) | 50 degrees | 0.73
7 | Fortaleza | SSW (202.5) | 60 degrees | 0.64
7 | Fortaleza | SSW (202.5) | 70 degrees | 0.55
7 | Fortaleza | SSW (202.5) | 80 degrees | 0.47
7 | Fortaleza | SSW (202.5) | 90 degrees (vertical) | 0.39
7 | Fortaleza | SW (225) | 0 degrees (horizontal) | 1
7 | Fortaleza | SW (225) | 10 degrees | 0.98
7 | Fortaleza | SW (225) | 20 degrees | 0.95
7 | Fortaleza | SW (225) | 30 degrees | 0.9
7 | Fortaleza | SW (225) | 40 degrees | 0.83
7 | Fortaleza | SW (225) | 50 degrees | 0.75
7 | Fortaleza | SW (225) | 60 degrees | 0.67
7 | Fortaleza | SW (225) | 70 degrees | 0.59
7 | Fortaleza | SW (225) | 80 degrees | 0.51
7 | Fortaleza | SW (225) | 90 degrees (vertical) | 0.43
7 | Fortaleza | WSW (247.5) | 0 degrees (horizontal) | 1
7 | Fortaleza | WSW (247.5) | 10 degrees | 0.99
7 | Fortaleza | WSW (247.5) | 20 degrees | 0.96
7 | Fortaleza | WSW (247.5) | 30 degrees | 0.91
7 | Fortaleza | WSW (247.5) | 40 degrees | 0.85
7 | Fortaleza | WSW (247.5) | 50 degrees | 0.77
7 | Fortaleza | WSW (247.5) | 60 degrees | 0.7
7 | Fortaleza | WSW (247.5) | 70 degrees | 0.62
7 | Fortaleza | WSW (247.5) | 80 degrees | 0.55
7 | Fortaleza | WSW (247.5) | 90 degrees (vertical) | 0.47
7 | Fortaleza | W (270) | 0 degrees (horizontal) | 1
7 | Fortaleza | W (270) | 10 degrees | 0.99
7 | Fortaleza | W (270) | 20 degrees | 0.96
7 | Fortaleza | W (270) | 30 degrees | 0.92
7 | Fortaleza | W (270) | 40 degrees | 0.86
7 | Fortaleza | W (270) | 50 degrees | 0.79
7 | Fortaleza | W (270) | 60 degrees | 0.72
7 | Fortaleza | W (270) | 70 degrees | 0.64
7 | Fortaleza | W (270) | 80 degrees | 0.56
7 | Fortaleza | W (270) | 90 degrees (vertical) | 0.49
7 | Fortaleza | WNW (292.5) | 0 degrees (horizontal) | 1
7 | Fortaleza | WNW (292.5) | 10 degrees | 0.99
7 | Fortaleza | WNW (292.5) | 20 degrees | 0.97
7 | Fortaleza | WNW (292.5) | 30 degrees | 0.92
7 | Fortaleza | WNW (292.5) | 40 degrees | 0.86
7 | Fortaleza | WNW (292.5) | 50 degrees | 0.8
7 | Fortaleza | WNW (292.5) | 60 degrees | 0.72
7 | Fortaleza | WNW (292.5) | 70 degrees | 0.64
7 | Fortaleza | WNW (292.5) | 80 degrees | 0.56
7 | Fortaleza | WNW (292.5) | 90 degrees (vertical) | 0.49
7 | Fortaleza | NW (315) | 0 degrees (horizontal) | 1
7 | Fortaleza | NW (315) | 10 degrees | 0.99
7 | Fortaleza | NW (315) | 20 degrees | 0.97
7 | Fortaleza | NW (315) | 30 degrees | 0.93
7 | Fortaleza | NW (315) | 40 degrees | 0.87
7 | Fortaleza | NW (315) | 50 degrees | 0.79
7 | Fortaleza | NW (315) | 60 degrees | 0.71
7 | Fortaleza | NW (315) | 70 degrees | 0.63
7 | Fortaleza | NW (315) | 80 degrees | 0.54
7 | Fortaleza | NW (315) | 90 degrees (vertical) | 0.46
7 | Fortaleza | NNW (337.5) | 0 degrees (horizontal) | 1
7 | Fortaleza | NNW (337.5) | 10 degrees | 1
7 | Fortaleza | NNW (337.5) | 20 degrees | 0.97
7 | Fortaleza | NNW (337.5) | 30 degrees | 0.93
7 | Fortaleza | NNW (337.5) | 40 degrees | 0.87
7 | Fortaleza | NNW (337.5) | 50 degrees | 0.79
7 | Fortaleza | NNW (337.5) | 60 degrees | 0.7
7 | Fortaleza | NNW (337.5) | 70 degrees | 0.61
7 | Fortaleza | NNW (337.5) | 80 degrees | 0.51
7 | Fortaleza | NNW (337.5) | 90 degrees (vertical) | 0.43
8 | Guatamala | N ( 0 degrees) | 0 degrees (horizontal) | 0.98
8 | Guatamala | N ( 0 degrees) | 10 degrees | 0.94
8 | Guatamala | N ( 0 degrees) | 20 degrees | 0.89
8 | Guatamala | N ( 0 degrees) | 30 degrees | 0.81
8 | Guatamala | N ( 0 degrees) | 40 degrees | 0.72
8 | Guatamala | N ( 0 degrees) | 50 degrees | 0.63
8 | Guatamala | N ( 0 degrees) | 60 degrees | 0.54
8 | Guatamala | N ( 0 degrees) | 70 degrees | 0.47
8 | Guatamala | N ( 0 degrees) | 80 degrees | 0.4
8 | Guatamala | N ( 0 degrees) | 90 degrees (vertical) | 0.35
8 | Guatamala | NNE (22.5) | 0 degrees (horizontal) | 0.98
8 | Guatamala | NNE (22.5) | 10 degrees | 0.95
8 | Guatamala | NNE (22.5) | 20 degrees | 0.89
8 | Guatamala | NNE (22.5) | 30 degrees | 0.82
8 | Guatamala | NNE (22.5) | 40 degrees | 0.74
8 | Guatamala | NNE (22.5) | 50 degrees | 0.65
8 | Guatamala | NNE (22.5) | 60 degrees | 0.56
8 | Guatamala | NNE (22.5) | 70 degrees | 0.48
8 | Guatamala | NNE (22.5) | 80 degrees | 0.42
8 | Guatamala | NNE (22.5) | 90 degrees (vertical) | 0.36
8 | Guatamala | NE (45) | 0 degrees (horizontal) | 0.98
8 | Guatamala | NE (45) | 10 degrees | 0.95
8 | Guatamala | NE (45) | 20 degrees | 0.9
8 | Guatamala | NE (45) | 30 degrees | 0.84
8 | Guatamala | NE (45) | 40 degrees | 0.77
8 | Guatamala | NE (45) | 50 degrees | 0.69
8 | Guatamala | NE (45) | 60 degrees | 0.61
8 | Guatamala | NE (45) | 70 degrees | 0.53
8 | Guatamala | NE (45) | 80 degrees | 0.47
8 | Guatamala | NE (45) | 90 degrees (vertical) | 0.41
8 | Guatamala | ENE (67.5) | 0 degrees (horizontal) | 0.98
8 | Guatamala | ENE (67.5) | 10 degrees | 0.96
8 | Guatamala | ENE (67.5) | 20 degrees | 0.92
8 | Guatamala | ENE (67.5) | 30 degrees | 0.87
8 | Guatamala | ENE (67.5) | 40 degrees | 0.81
8 | Guatamala | ENE (67.5) | 50 degrees | 0.74
8 | Guatamala | ENE (67.5) | 60 degrees | 0.66
8 | Guatamala | ENE (67.5) | 70 degrees | 0.59
8 | Guatamala | ENE (67.5) | 80 degrees | 0.52
8 | Guatamala | ENE (67.5) | 90 degrees (vertical) | 0.46
8 | Guatamala | E (90) | 0 degrees (horizontal) | 0.98
8 | Guatamala | E (90) | 10 degrees | 0.97
8 | Guatamala | E (90) | 20 degrees | 0.94
8 | Guatamala | E (90) | 30 degrees | 0.9
8 | Guatamala | E (90) | 40 degrees | 0.85
8 | Guatamala | E (90) | 50 degrees | 0.78
8 | Guatamala | E (90) | 60 degrees | 0.71
8 | Guatamala | E (90) | 70 degrees | 0.64
8 | Guatamala | E (90) | 80 degrees | 0.57
8 | Guatamala | E (90) | 90 degrees (vertical) | 0.5
8 | Guatamala | ESE (112.5) | 0 degrees (horizontal) | 0.98
8 | Guatamala | ESE (112.5) | 10 degrees | 0.98
8 | Guatamala | ESE (112.5) | 20 degrees | 0.96
8 | Guatamala | ESE (112.5) | 30 degrees | 0.93
8 | Guatamala | ESE (112.5) | 40 degrees | 0.88
8 | Guatamala | ESE (112.5) | 50 degrees | 0.82
8 | Guatamala | ESE (112.5) | 60 degrees | 0.75
8 | Guatamala | ESE (112.5) | 70 degrees | 0.67
8 | Guatamala | ESE (112.5) | 80 degrees | 0.6
8 | Guatamala | ESE (112.5) | 90 degrees (vertical) | 0.52
8 | Guatamala | SE (135) | 0 degrees (horizontal) | 0.98
8 | Guatamala | SE (135) | 10 degrees | 0.99
8 | Guatamala | SE (135) | 20 degrees | 0.98
8 | Guatamala | SE (135) | 30 degrees | 0.95
8 | Guatamala | SE (135) | 40 degrees | 0.91
8 | Guatamala | SE (135) | 50 degrees | 0.85
8 | Guatamala | SE (135) | 60 degrees | 0.77
8 | Guatamala | SE (135) | 70 degrees | 0.69
8 | Guatamala | SE (135) | 80 degrees | 0.61
8 | Guatamala | SE (135) | 90 degrees (vertical) | 0.52
8 | Guatamala | SSE (157.5) | 0 degrees (horizontal) | 0.98
8 | Guatamala | SSE (157.5) | 10 degrees | 1
8 | Guatamala | SSE (157.5) | 20 degrees | 0.99
8 | Guatamala | SSE (157.5) | 30 degrees | 0.97
8 | Guatamala | SSE (157.5) | 40 degrees | 0.93
8 | Guatamala | SSE (157.5) | 50 degrees | 0.86
8 | Guatamala | SSE (157.5) | 60 degrees | 0.79
8 | Guatamala | SSE (157.5) | 70 degrees | 0.7
8 | Guatamala | SSE (157.5) | 80 degrees | 0.61
8 | Guatamala | SSE (157.5) | 90 degrees (vertical) | 0.51
8 | Guatamala | S (180) | 0 degrees (horizontal) | 0.98
8 | Guatamala | S (180) | 10 degrees | 1
8 | Guatamala | S (180) | 20 degrees | 1
8 | Guatamala | S (180) | 30 degrees | 0.97
8 | Guatamala | S (180) | 40 degrees | 0.93
8 | Guatamala | S (180) | 50 degrees | 0.87
8 | Guatamala | S (180) | 60 degrees | 0.79
8 | Guatamala | S (180) | 70 degrees | 0.7
8 | Guatamala | S (180) | 80 degrees | 0.6
8 | Guatamala | S (180) | 90 degrees (vertical) | 0.51
8 | Guatamala | SSW (202.5) | 0 degrees (horizontal) | 0.98
8 | Guatamala | SSW (202.5) | 10 degrees | 1
8 | Guatamala | SSW (202.5) | 20 degrees | 0.99
8 | Guatamala | SSW (202.5) | 30 degrees | 0.97
8 | Guatamala | SSW (202.5) | 40 degrees | 0.93
8 | Guatamala | SSW (202.5) | 50 degrees | 0.86
8 | Guatamala | SSW (202.5) | 60 degrees | 0.79
8 | Guatamala | SSW (202.5) | 70 degrees | 0.7
8 | Guatamala | SSW (202.5) | 80 degrees | 0.61
8 | Guatamala | SSW (202.5) | 90 degrees (vertical) | 0.98
8 | Guatamala | SW (225) | 0 degrees (horizontal) | 0.99
8 | Guatamala | SW (225) | 10 degrees | 0.98
8 | Guatamala | SW (225) | 20 degrees | 0.95
8 | Guatamala | SW (225) | 30 degrees | 0.91
8 | Guatamala | SW (225) | 40 degrees | 0.85
8 | Guatamala | SW (225) | 50 degrees | 0.77
8 | Guatamala | SW (225) | 60 degrees | 0.69
8 | Guatamala | SW (225) | 70 degrees | 0.61
8 | Guatamala | SW (225) | 80 degrees | 0.51
8 | Guatamala | SW (225) | 90 degrees (vertical) | 0.52
8 | Guatamala | WSW (247.5) | 0 degrees (horizontal) | 0.98
8 | Guatamala | WSW (247.5) | 10 degrees | 0.98
8 | Guatamala | WSW (247.5) | 20 degrees | 0.96
8 | Guatamala | WSW (247.5) | 30 degrees | 0.93
8 | Guatamala | WSW (247.5) | 40 degrees | 0.88
8 | Guatamala | WSW (247.5) | 50 degrees | 0.82
8 | Guatamala | WSW (247.5) | 60 degrees | 0.75
8 | Guatamala | WSW (247.5) | 70 degrees | 0.67
8 | Guatamala | WSW (247.5) | 80 degrees | 0.6
8 | Guatamala | WSW (247.5) | 90 degrees (vertical) | 0.52
8 | Guatamala | W (270) | 0 degrees (horizontal) | 0.98
8 | Guatamala | W (270) | 10 degrees | 0.97
8 | Guatamala | W (270) | 20 degrees | 0.94
8 | Guatamala | W (270) | 30 degrees | 0.9
8 | Guatamala | W (270) | 40 degrees | 0.85
8 | Guatamala | W (270) | 50 degrees | 0.78
8 | Guatamala | W (270) | 60 degrees | 0.71
8 | Guatamala | W (270) | 70 degrees | 0.64
8 | Guatamala | W (270) | 80 degrees | 0.57
8 | Guatamala | W (270) | 90 degrees (vertical) | 0.5
8 | Guatamala | WNW (292.5) | 0 degrees (horizontal) | 0.98
8 | Guatamala | WNW (292.5) | 10 degrees | 0.96
8 | Guatamala | WNW (292.5) | 20 degrees | 0.92
8 | Guatamala | WNW (292.5) | 30 degrees | 0.87
8 | Guatamala | WNW (292.5) | 40 degrees | 0.81
8 | Guatamala | WNW (292.5) | 50 degrees | 0.74
8 | Guatamala | WNW (292.5) | 60 degrees | 0.66
8 | Guatamala | WNW (292.5) | 70 degrees | 0.59
8 | Guatamala | WNW (292.5) | 80 degrees | 0.52
8 | Guatamala | WNW (292.5) | 90 degrees (vertical) | 0.46
8 | Guatamala | NW (315) | 0 degrees (horizontal) | 0.98
8 | Guatamala | NW (315) | 10 degrees | 0.95
8 | Guatamala | NW (315) | 20 degrees | 0.9
8 | Guatamala | NW (315) | 30 degrees | 0.84
8 | Guatamala | NW (315) | 40 degrees | 0.77
8 | Guatamala | NW (315) | 50 degrees | 0.69
8 | Guatamala | NW (315) | 60 degrees | 0.61
8 | Guatamala | NW (315) | 70 degrees | 0.53
8 | Guatamala | NW (315) | 80 degrees | 0.47
8 | Guatamala | NW (315) | 90 degrees (vertical) | 0.41
8 | Guatamala | NNW (337.5) | 0 degrees (horizontal) | 0.98
8 | Guatamala | NNW (337.5) | 10 degrees | 0.95
8 | Guatamala | NNW (337.5) | 20 degrees | 0.89
8 | Guatamala | NNW (337.5) | 30 degrees | 0.82
8 | Guatamala | NNW (337.5) | 40 degrees | 0.74
8 | Guatamala | NNW (337.5) | 50 degrees | 0.65
8 | Guatamala | NNW (337.5) | 60 degrees | 0.56
8 | Guatamala | NNW (337.5) | 70 degrees | 0.48
8 | Guatamala | NNW (337.5) | 80 degrees | 0.42
8 | Guatamala | NNW (337.5) | 90 degrees (vertical) | 0.36
9 | Honnolulu | N ( 0 degrees) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | N ( 0 degrees) | 10 degrees | 0.92
9 | Honnolulu | N ( 0 degrees) | 20 degrees | 0.85
9 | Honnolulu | N ( 0 degrees) | 30 degrees | 0.77
9 | Honnolulu | N ( 0 degrees) | 40 degrees | 0.67
9 | Honnolulu | N ( 0 degrees) | 50 degrees | 0.57
9 | Honnolulu | N ( 0 degrees) | 60 degrees | 0.48
9 | Honnolulu | N ( 0 degrees) | 70 degrees | 0.4
9 | Honnolulu | N ( 0 degrees) | 80 degrees | 0.33
9 | Honnolulu | N ( 0 degrees) | 90 degrees (vertical) | 0.28
9 | Honnolulu | NNE (22.5) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | NNE (22.5) | 10 degrees | 0.92
9 | Honnolulu | NNE (22.5) | 20 degrees | 0.86
9 | Honnolulu | NNE (22.5) | 30 degrees | 0.78
9 | Honnolulu | NNE (22.5) | 40 degrees | 0.68
9 | Honnolulu | NNE (22.5) | 50 degrees | 0.59
9 | Honnolulu | NNE (22.5) | 60 degrees | 0.5
9 | Honnolulu | NNE (22.5) | 70 degrees | 0.42
9 | Honnolulu | NNE (22.5) | 80 degrees | 0.35
9 | Honnolulu | NNE (22.5) | 90 degrees (vertical) | 0.31
9 | Honnolulu | NE (45) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | NE (45) | 10 degrees | 0.93
9 | Honnolulu | NE (45) | 20 degrees | 0.88
9 | Honnolulu | NE (45) | 30 degrees | 0.8
9 | Honnolulu | NE (45) | 40 degrees | 0.72
9 | Honnolulu | NE (45) | 50 degrees | 0.64
9 | Honnolulu | NE (45) | 60 degrees | 0.56
9 | Honnolulu | NE (45) | 70 degrees | 0.48
9 | Honnolulu | NE (45) | 80 degrees | 0.42
9 | Honnolulu | NE (45) | 90 degrees (vertical) | 0.36
9 | Honnolulu | ENE (67.5) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | ENE (67.5) | 10 degrees | 0.94
9 | Honnolulu | ENE (67.5) | 20 degrees | 0.9
9 | Honnolulu | ENE (67.5) | 30 degrees | 0.84
9 | Honnolulu | ENE (67.5) | 40 degrees | 0.78
9 | Honnolulu | ENE (67.5) | 50 degrees | 0.7
9 | Honnolulu | ENE (67.5) | 60 degrees | 0.63
9 | Honnolulu | ENE (67.5) | 70 degrees | 0.56
9 | Honnolulu | ENE (67.5) | 80 degrees | 0.49
9 | Honnolulu | ENE (67.5) | 90 degrees (vertical) | 0.43
9 | Honnolulu | E (90) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | E (90) | 10 degrees | 0.96
9 | Honnolulu | E (90) | 20 degrees | 0.93
9 | Honnolulu | E (90) | 30 degrees | 0.89
9 | Honnolulu | E (90) | 40 degrees | 0.83
9 | Honnolulu | E (90) | 50 degrees | 0.76
9 | Honnolulu | E (90) | 60 degrees | 0.69
9 | Honnolulu | E (90) | 70 degrees | 0.62
9 | Honnolulu | E (90) | 80 degrees | 0.55
9 | Honnolulu | E (90) | 90 degrees (vertical) | 0.48
9 | Honnolulu | ESE (112.5) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | ESE (112.5) | 10 degrees | 0.97
9 | Honnolulu | ESE (112.5) | 20 degrees | 0.96
9 | Honnolulu | ESE (112.5) | 30 degrees | 0.92
9 | Honnolulu | ESE (112.5) | 40 degrees | 0.87
9 | Honnolulu | ESE (112.5) | 50 degrees | 0.81
9 | Honnolulu | ESE (112.5) | 60 degrees | 0.74
9 | Honnolulu | ESE (112.5) | 70 degrees | 0.67
9 | Honnolulu | ESE (112.5) | 80 degrees | 0.59
9 | Honnolulu | ESE (112.5) | 90 degrees (vertical) | 0.51
9 | Honnolulu | SE (135) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | SE (135) | 10 degrees | 0.99
9 | Honnolulu | SE (135) | 20 degrees | 0.98
9 | Honnolulu | SE (135) | 30 degrees | 0.95
9 | Honnolulu | SE (135) | 40 degrees | 0.91
9 | Honnolulu | SE (135) | 50 degrees | 0.85
9 | Honnolulu | SE (135) | 60 degrees | 0.78
9 | Honnolulu | SE (135) | 70 degrees | 0.69
9 | Honnolulu | SE (135) | 80 degrees | 0.6
9 | Honnolulu | SE (135) | 90 degrees (vertical) | 0.52
9 | Honnolulu | SSE (157.5) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | SSE (157.5) | 10 degrees | 0.99
9 | Honnolulu | SSE (157.5) | 20 degrees | 1
9 | Honnolulu | SSE (157.5) | 30 degrees | 0.98
9 | Honnolulu | SSE (157.5) | 40 degrees | 0.93
9 | Honnolulu | SSE (157.5) | 50 degrees | 0.87
9 | Honnolulu | SSE (157.5) | 60 degrees | 0.8
9 | Honnolulu | SSE (157.5) | 70 degrees | 0.71
9 | Honnolulu | SSE (157.5) | 80 degrees | 0.61
9 | Honnolulu | SSE (157.5) | 90 degrees (vertical) | 0.51
9 | Honnolulu | S (180) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | S (180) | 10 degrees | 1
9 | Honnolulu | S (180) | 20 degrees | 1
9 | Honnolulu | S (180) | 30 degrees | 0.98
9 | Honnolulu | S (180) | 40 degrees | 0.94
9 | Honnolulu | S (180) | 50 degrees | 0.88
9 | Honnolulu | S (180) | 60 degrees | 0.8
9 | Honnolulu | S (180) | 70 degrees | 0.71
9 | Honnolulu | S (180) | 80 degrees | 0.6
9 | Honnolulu | S (180) | 90 degrees (vertical) | 0.5
9 | Honnolulu | SSW (202.5) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | SSW (202.5) | 10 degrees | 0.99
9 | Honnolulu | SSW (202.5) | 20 degrees | 1
9 | Honnolulu | SSW (202.5) | 30 degrees | 0.98
9 | Honnolulu | SSW (202.5) | 40 degrees | 0.93
9 | Honnolulu | SSW (202.5) | 50 degrees | 0.87
9 | Honnolulu | SSW (202.5) | 60 degrees | 0.8
9 | Honnolulu | SSW (202.5) | 70 degrees | 0.71
9 | Honnolulu | SSW (202.5) | 80 degrees | 0.61
9 | Honnolulu | SSW (202.5) | 90 degrees (vertical) | 0.51
9 | Honnolulu | SW (225) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | SW (225) | 10 degrees | 0.99
9 | Honnolulu | SW (225) | 20 degrees | 0.98
9 | Honnolulu | SW (225) | 30 degrees | 0.95
9 | Honnolulu | SW (225) | 40 degrees | 0.91
9 | Honnolulu | SW (225) | 50 degrees | 0.85
9 | Honnolulu | SW (225) | 60 degrees | 0.78
9 | Honnolulu | SW (225) | 70 degrees | 0.69
9 | Honnolulu | SW (225) | 80 degrees | 0.6
9 | Honnolulu | SW (225) | 90 degrees (vertical) | 0.52
9 | Honnolulu | WSW (247.5) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | WSW (247.5) | 10 degrees | 0.97
9 | Honnolulu | WSW (247.5) | 20 degrees | 0.96
9 | Honnolulu | WSW (247.5) | 30 degrees | 0.92
9 | Honnolulu | WSW (247.5) | 40 degrees | 0.87
9 | Honnolulu | WSW (247.5) | 50 degrees | 0.81
9 | Honnolulu | WSW (247.5) | 60 degrees | 0.74
9 | Honnolulu | WSW (247.5) | 70 degrees | 0.67
9 | Honnolulu | WSW (247.5) | 80 degrees | 0.59
9 | Honnolulu | WSW (247.5) | 90 degrees (vertical) | 0.51
9 | Honnolulu | W (270) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | W (270) | 10 degrees | 0.96
9 | Honnolulu | W (270) | 20 degrees | 0.93
9 | Honnolulu | W (270) | 30 degrees | 0.89
9 | Honnolulu | W (270) | 40 degrees | 0.83
9 | Honnolulu | W (270) | 50 degrees | 0.76
9 | Honnolulu | W (270) | 60 degrees | 0.69
9 | Honnolulu | W (270) | 70 degrees | 0.62
9 | Honnolulu | W (270) | 80 degrees | 0.55
9 | Honnolulu | W (270) | 90 degrees (vertical) | 0.48
9 | Honnolulu | WNW (292.5) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | WNW (292.5) | 10 degrees | 0.94
9 | Honnolulu | WNW (292.5) | 20 degrees | 0.9
9 | Honnolulu | WNW (292.5) | 30 degrees | 0.84
9 | Honnolulu | WNW (292.5) | 40 degrees | 0.78
9 | Honnolulu | WNW (292.5) | 50 degrees | 0.7
9 | Honnolulu | WNW (292.5) | 60 degrees | 0.63
9 | Honnolulu | WNW (292.5) | 70 degrees | 0.56
9 | Honnolulu | WNW (292.5) | 80 degrees | 0.49
9 | Honnolulu | WNW (292.5) | 90 degrees (vertical) | 0.43
9 | Honnolulu | NW (315) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | NW (315) | 10 degrees | 0.93
9 | Honnolulu | NW (315) | 20 degrees | 0.88
9 | Honnolulu | NW (315) | 30 degrees | 0.8
9 | Honnolulu | NW (315) | 40 degrees | 0.72
9 | Honnolulu | NW (315) | 50 degrees | 0.64
9 | Honnolulu | NW (315) | 60 degrees | 0.56
9 | Honnolulu | NW (315) | 70 degrees | 0.48
9 | Honnolulu | NW (315) | 80 degrees | 0.42
9 | Honnolulu | NW (315) | 90 degrees (vertical) | 0.36
9 | Honnolulu | NNW (337.5) | 0 degrees (horizontal) | 0.97
9 | Honnolulu | NNW (337.5) | 10 degrees | 0.92
9 | Honnolulu | NNW (337.5) | 20 degrees | 0.86
9 | Honnolulu | NNW (337.5) | 30 degrees | 0.78
9 | Honnolulu | NNW (337.5) | 40 degrees | 0.68
9 | Honnolulu | NNW (337.5) | 50 degrees | 0.59
9 | Honnolulu | NNW (337.5) | 60 degrees | 0.5
9 | Honnolulu | NNW (337.5) | 70 degrees | 0.42
9 | Honnolulu | NNW (337.5) | 80 degrees | 0.35
9 | Honnolulu | NNW (337.5) | 90 degrees (vertical) | 0.31
10 | Invercargill Station | N ( 0 degrees) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | N ( 0 degrees) | 10 degrees | 0.95488
10 | Invercargill Station | N ( 0 degrees) | 20 degrees | 0.98743
10 | Invercargill Station | N ( 0 degrees) | 30 degrees | 1
10 | Invercargill Station | N ( 0 degrees) | 40 degrees | 0.9926
10 | Invercargill Station | N ( 0 degrees) | 50 degrees | 0.96524
10 | Invercargill Station | N ( 0 degrees) | 60 degrees | 0.91938
10 | Invercargill Station | N ( 0 degrees) | 70 degrees | 0.85577
10 | Invercargill Station | N ( 0 degrees) | 80 degrees | 0.77663
10 | Invercargill Station | N ( 0 degrees) | 90 degrees (vertical) | 0.68565
10 | Invercargill Station | NNE (22.5) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | NNE (22.5) | 10 degrees | 0.95044
10 | Invercargill Station | NNE (22.5) | 20 degrees | 0.97929
10 | Invercargill Station | NNE (22.5) | 30 degrees | 0.98817
10 | Invercargill Station | NNE (22.5) | 40 degrees | 0.97855
10 | Invercargill Station | NNE (22.5) | 50 degrees | 0.9497
10 | Invercargill Station | NNE (22.5) | 60 degrees | 0.90311
10 | Invercargill Station | NNE (22.5) | 70 degrees | 0.8395
10 | Invercargill Station | NNE (22.5) | 80 degrees | 0.76257
10 | Invercargill Station | NNE (22.5) | 90 degrees (vertical) | 0.67382
10 | Invercargill Station | NE (45) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | NE (45) | 10 degrees | 0.93787
10 | Invercargill Station | NE (45) | 20 degrees | 0.95414
10 | Invercargill Station | NE (45) | 30 degrees | 0.9534
10 | Invercargill Station | NE (45) | 40 degrees | 0.93565
10 | Invercargill Station | NE (45) | 50 degrees | 0.90237
10 | Invercargill Station | NE (45) | 60 degrees | 0.85355
10 | Invercargill Station | NE (45) | 70 degrees | 0.79068
10 | Invercargill Station | NE (45) | 80 degrees | 0.71746
10 | Invercargill Station | NE (45) | 90 degrees (vertical) | 0.63683
10 | Invercargill Station | ENE (67.5) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | ENE (67.5) | 10 degrees | 0.9179
10 | Invercargill Station | ENE (67.5) | 20 degrees | 0.91642
10 | Invercargill Station | ENE (67.5) | 30 degrees | 0.90089
10 | Invercargill Station | ENE (67.5) | 40 degrees | 0.87204
10 | Invercargill Station | ENE (67.5) | 50 degrees | 0.83136
10 | Invercargill Station | ENE (67.5) | 60 degrees | 0.77959
10 | Invercargill Station | ENE (67.5) | 70 degrees | 0.71893
10 | Invercargill Station | ENE (67.5) | 80 degrees | 0.65163
10 | Invercargill Station | ENE (67.5) | 90 degrees (vertical) | 0.57914
10 | Invercargill Station | E (90) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | E (90) | 10 degrees | 0.89571
10 | Invercargill Station | E (90) | 20 degrees | 0.87426
10 | Invercargill Station | E (90) | 30 degrees | 0.84098
10 | Invercargill Station | E (90) | 40 degrees | 0.8003
10 | Invercargill Station | E (90) | 50 degrees | 0.75222
10 | Invercargill Station | E (90) | 60 degrees | 0.69822
10 | Invercargill Station | E (90) | 70 degrees | 0.63905
10 | Invercargill Station | E (90) | 80 degrees | 0.57766
10 | Invercargill Station | E (90) | 90 degrees (vertical) | 0.51479
10 | Invercargill Station | ESE (112.5) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | ESE (112.5) | 10 degrees | 0.87352
10 | Invercargill Station | ESE (112.5) | 20 degrees | 0.83062
10 | Invercargill Station | ESE (112.5) | 30 degrees | 0.77959
10 | Invercargill Station | ESE (112.5) | 40 degrees | 0.72485
10 | Invercargill Station | ESE (112.5) | 50 degrees | 0.66938
10 | Invercargill Station | ESE (112.5) | 60 degrees | 0.61391
10 | Invercargill Station | ESE (112.5) | 70 degrees | 0.55843
10 | Invercargill Station | ESE (112.5) | 80 degrees | 0.5037
10 | Invercargill Station | ESE (112.5) | 90 degrees (vertical) | 0.45044
10 | Invercargill Station | SE (135) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | SE (135) | 10 degrees | 0.85355
10 | Invercargill Station | SE (135) | 20 degrees | 0.79068
10 | Invercargill Station | SE (135) | 30 degrees | 0.73743
10 | Invercargill Station | SE (135) | 40 degrees | 0.65459
10 | Invercargill Station | SE (135) | 50 degrees | 0.59098
10 | Invercargill Station | SE (135) | 60 degrees | 0.53402
10 | Invercargill Station | SE (135) | 70 degrees | 0.48299
10 | Invercargill Station | SE (135) | 80 degrees | 0.43639
10 | Invercargill Station | SE (135) | 90 degrees (vertical) | 0.39349
10 | Invercargill Station | SSE (157.5) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | SSE (157.5) | 10 degrees | 0.84024
10 | Invercargill Station | SSE (157.5) | 20 degrees | 0.76331
10 | Invercargill Station | SSE (157.5) | 30 degrees | 0.68417
10 | Invercargill Station | SSE (157.5) | 40 degrees | 0.60799
10 | Invercargill Station | SSE (157.5) | 50 degrees | 0.5355
10 | Invercargill Station | SSE (157.5) | 60 degrees | 0.47337
10 | Invercargill Station | SSE (157.5) | 70 degrees | 0.42751
10 | Invercargill Station | SSE (157.5) | 80 degrees | 0.38979
10 | Invercargill Station | SSE (157.5) | 90 degrees (vertical) | 0.35503
10 | Invercargill Station | S (180) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | S (180) | 10 degrees | 0.8358
10 | Invercargill Station | S (180) | 20 degrees | 0.75444
10 | Invercargill Station | S (180) | 30 degrees | 0.67234
10 | Invercargill Station | S (180) | 40 degrees | 0.5932
10 | Invercargill Station | S (180) | 50 degrees | 0.51923
10 | Invercargill Station | S (180) | 60 degrees | 0.4534
10 | Invercargill Station | S (180) | 70 degrees | 0.40459
10 | Invercargill Station | S (180) | 80 degrees | 0.3713
10 | Invercargill Station | S (180) | 90 degrees (vertical) | 0.34172
10 | Invercargill Station | SSW (202.5) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | SSW (202.5) | 10 degrees | 0.84024
10 | Invercargill Station | SSW (202.5) | 20 degrees | 0.76331
10 | Invercargill Station | SSW (202.5) | 30 degrees | 0.68417
10 | Invercargill Station | SSW (202.5) | 40 degrees | 0.60799
10 | Invercargill Station | SSW (202.5) | 50 degrees | 0.5355
10 | Invercargill Station | SSW (202.5) | 60 degrees | 0.47337
10 | Invercargill Station | SSW (202.5) | 70 degrees | 0.42751
10 | Invercargill Station | SSW (202.5) | 80 degrees | 0.38979
10 | Invercargill Station | SSW (202.5) | 90 degrees (vertical) | 0.35503
10 | Invercargill Station | SW (225) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | SW (225) | 10 degrees | 0.85355
10 | Invercargill Station | SW (225) | 20 degrees | 0.79068
10 | Invercargill Station | SW (225) | 30 degrees | 0.73743
10 | Invercargill Station | SW (225) | 40 degrees | 0.65459
10 | Invercargill Station | SW (225) | 50 degrees | 0.59098
10 | Invercargill Station | SW (225) | 60 degrees | 0.53402
10 | Invercargill Station | SW (225) | 70 degrees | 0.48299
10 | Invercargill Station | SW (225) | 80 degrees | 0.43639
10 | Invercargill Station | SW (225) | 90 degrees (vertical) | 0.39349
10 | Invercargill Station | WSW (247.5) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | WSW (247.5) | 10 degrees | 0.87352
10 | Invercargill Station | WSW (247.5) | 20 degrees | 0.83062
10 | Invercargill Station | WSW (247.5) | 30 degrees | 0.77959
10 | Invercargill Station | WSW (247.5) | 40 degrees | 0.72485
10 | Invercargill Station | WSW (247.5) | 50 degrees | 0.66938
10 | Invercargill Station | WSW (247.5) | 60 degrees | 0.61391
10 | Invercargill Station | WSW (247.5) | 70 degrees | 0.55843
10 | Invercargill Station | WSW (247.5) | 80 degrees | 0.5037
10 | Invercargill Station | WSW (247.5) | 90 degrees (vertical) | 0.45044
10 | Invercargill Station | W (270) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | W (270) | 10 degrees | 0.89571
10 | Invercargill Station | W (270) | 20 degrees | 0.87426
10 | Invercargill Station | W (270) | 30 degrees | 0.84098
10 | Invercargill Station | W (270) | 40 degrees | 0.8003
10 | Invercargill Station | W (270) | 50 degrees | 0.75222
10 | Invercargill Station | W (270) | 60 degrees | 0.69822
10 | Invercargill Station | W (270) | 70 degrees | 0.63905
10 | Invercargill Station | W (270) | 80 degrees | 0.57766
10 | Invercargill Station | W (270) | 90 degrees (vertical) | 0.51479
10 | Invercargill Station | WNW (292.5) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | WNW (292.5) | 10 degrees | 0.9179
10 | Invercargill Station | WNW (292.5) | 20 degrees | 0.91642
10 | Invercargill Station | WNW (292.5) | 30 degrees | 0.90089
10 | Invercargill Station | WNW (292.5) | 40 degrees | 0.87204
10 | Invercargill Station | WNW (292.5) | 50 degrees | 0.83136
10 | Invercargill Station | WNW (292.5) | 60 degrees | 0.77959
10 | Invercargill Station | WNW (292.5) | 70 degrees | 0.71893
10 | Invercargill Station | WNW (292.5) | 80 degrees | 0.65163
10 | Invercargill Station | WNW (292.5) | 90 degrees (vertical) | 0.57914
10 | Invercargill Station | NW (315) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | NW (315) | 10 degrees | 0.93787
10 | Invercargill Station | NW (315) | 20 degrees | 0.95414
10 | Invercargill Station | NW (315) | 30 degrees | 0.9534
10 | Invercargill Station | NW (315) | 40 degrees | 0.93565
10 | Invercargill Station | NW (315) | 50 degrees | 0.90237
10 | Invercargill Station | NW (315) | 60 degrees | 0.85355
10 | Invercargill Station | NW (315) | 70 degrees | 0.79068
10 | Invercargill Station | NW (315) | 80 degrees | 0.71746
10 | Invercargill Station | NW (315) | 90 degrees (vertical) | 0.63683
10 | Invercargill Station | NNW (337.5) | 0 degrees (horizontal) | 0.9068
10 | Invercargill Station | NNW (337.5) | 10 degrees | 0.95044
10 | Invercargill Station | NNW (337.5) | 20 degrees | 0.97929
10 | Invercargill Station | NNW (337.5) | 30 degrees | 0.98817
10 | Invercargill Station | NNW (337.5) | 40 degrees | 0.97855
10 | Invercargill Station | NNW (337.5) | 50 degrees | 0.9497
10 | Invercargill Station | NNW (337.5) | 60 degrees | 0.90311
10 | Invercargill Station | NNW (337.5) | 70 degrees | 0.8395
10 | Invercargill Station | NNW (337.5) | 80 degrees | 0.76257
10 | Invercargill Station | NNW (337.5) | 90 degrees (vertical) | 0.67382
11 | Istanbul | N ( 0 degrees) | 0 degrees (horizontal) | 0.93
11 | Istanbul | N ( 0 degrees) | 10 degrees | 0.86
11 | Istanbul | N ( 0 degrees) | 20 degrees | 0.78
11 | Istanbul | N ( 0 degrees) | 30 degrees | 0.69
11 | Istanbul | N ( 0 degrees) | 40 degrees | 0.61
11 | Istanbul | N ( 0 degrees) | 50 degrees | 0.52
11 | Istanbul | N ( 0 degrees) | 60 degrees | 0.44
11 | Istanbul | N ( 0 degrees) | 70 degrees | 0.37
11 | Istanbul | N ( 0 degrees) | 80 degrees | 0.34
11 | Istanbul | N ( 0 degrees) | 90 degrees (vertical) | 0.31
11 | Istanbul | NNE (22.5) | 0 degrees (horizontal) | 0.93
11 | Istanbul | NNE (22.5) | 10 degrees | 0.87
11 | Istanbul | NNE (22.5) | 20 degrees | 0.79
11 | Istanbul | NNE (22.5) | 30 degrees | 0.71
11 | Istanbul | NNE (22.5) | 40 degrees | 0.62
11 | Istanbul | NNE (22.5) | 50 degrees | 0.54
11 | Istanbul | NNE (22.5) | 60 degrees | 0.46
11 | Istanbul | NNE (22.5) | 70 degrees | 0.4
11 | Istanbul | NNE (22.5) | 80 degrees | 0.36
11 | Istanbul | NNE (22.5) | 90 degrees (vertical) | 0.33
11 | Istanbul | NE (45) | 0 degrees (horizontal) | 0.93
11 | Istanbul | NE (45) | 10 degrees | 0.88
11 | Istanbul | NE (45) | 20 degrees | 0.82
11 | Istanbul | NE (45) | 30 degrees | 0.74
11 | Istanbul | NE (45) | 40 degrees | 0.67
11 | Istanbul | NE (45) | 50 degrees | 0.59
11 | Istanbul | NE (45) | 60 degrees | 0.53
11 | Istanbul | NE (45) | 70 degrees | 0.47
11 | Istanbul | NE (45) | 80 degrees | 0.42
11 | Istanbul | NE (45) | 90 degrees (vertical) | 0.38
11 | Istanbul | ENE (67.5) | 0 degrees (horizontal) | 0.93
11 | Istanbul | ENE (67.5) | 10 degrees | 0.9
11 | Istanbul | ENE (67.5) | 20 degrees | 0.85
11 | Istanbul | ENE (67.5) | 30 degrees | 0.8
11 | Istanbul | ENE (67.5) | 40 degrees | 0.74
11 | Istanbul | ENE (67.5) | 50 degrees | 0.68
11 | Istanbul | ENE (67.5) | 60 degrees | 0.61
11 | Istanbul | ENE (67.5) | 70 degrees | 0.55
11 | Istanbul | ENE (67.5) | 80 degrees | 0.5
11 | Istanbul | ENE (67.5) | 90 degrees (vertical) | 0.44
11 | Istanbul | E (90) | 0 degrees (horizontal) | 0.93
11 | Istanbul | E (90) | 10 degrees | 0.92
11 | Istanbul | E (90) | 20 degrees | 0.89
11 | Istanbul | E (90) | 30 degrees | 0.86
11 | Istanbul | E (90) | 40 degrees | 0.81
11 | Istanbul | E (90) | 50 degrees | 0.76
11 | Istanbul | E (90) | 60 degrees | 0.7
11 | Istanbul | E (90) | 70 degrees | 0.63
11 | Istanbul | E (90) | 80 degrees | 0.57
11 | Istanbul | E (90) | 90 degrees (vertical) | 0.5
11 | Istanbul | ESE (112.5) | 0 degrees (horizontal) | 0.93
11 | Istanbul | ESE (112.5) | 10 degrees | 0.94
11 | Istanbul | ESE (112.5) | 20 degrees | 0.93
11 | Istanbul | ESE (112.5) | 30 degrees | 0.91
11 | Istanbul | ESE (112.5) | 40 degrees | 0.88
11 | Istanbul | ESE (112.5) | 50 degrees | 0.83
11 | Istanbul | ESE (112.5) | 60 degrees | 0.77
11 | Istanbul | ESE (112.5) | 70 degrees | 0.7
11 | Istanbul | ESE (112.5) | 80 degrees | 0.63
11 | Istanbul | ESE (112.5) | 90 degrees (vertical) | 0.56
11 | Istanbul | SE (135) | 0 degrees (horizontal) | 0.93
11 | Istanbul | SE (135) | 10 degrees | 0.96
11 | Istanbul | SE (135) | 20 degrees | 0.97
11 | Istanbul | SE (135) | 30 degrees | 0.96
11 | Istanbul | SE (135) | 40 degrees | 0.93
11 | Istanbul | SE (135) | 50 degrees | 0.89
11 | Istanbul | SE (135) | 60 degrees | 0.83
11 | Istanbul | SE (135) | 70 degrees | 0.76
11 | Istanbul | SE (135) | 80 degrees | 0.68
11 | Istanbul | SE (135) | 90 degrees (vertical) | 0.6
11 | Istanbul | SSE (157.5) | 0 degrees (horizontal) | 0.93
11 | Istanbul | SSE (157.5) | 10 degrees | 0.97
11 | Istanbul | SSE (157.5) | 20 degrees | 0.99
11 | Istanbul | SSE (157.5) | 30 degrees | 0.99
11 | Istanbul | SSE (157.5) | 40 degrees | 0.97
11 | Istanbul | SSE (157.5) | 50 degrees | 0.93
11 | Istanbul | SSE (157.5) | 60 degrees | 0.87
11 | Istanbul | SSE (157.5) | 70 degrees | 0.8
11 | Istanbul | SSE (157.5) | 80 degrees | 0.71
11 | Istanbul | SSE (157.5) | 90 degrees (vertical) | 0.62
11 | Istanbul | S (180) | 0 degrees (horizontal) | 0.93
11 | Istanbul | S (180) | 10 degrees | 0.97
11 | Istanbul | S (180) | 20 degrees | 1
11 | Istanbul | S (180) | 30 degrees | 1
11 | Istanbul | S (180) | 40 degrees | 0.98
11 | Istanbul | S (180) | 50 degrees | 0.94
11 | Istanbul | S (180) | 60 degrees | 0.89
11 | Istanbul | S (180) | 70 degrees | 0.81
11 | Istanbul | S (180) | 80 degrees | 0.72
11 | Istanbul | S (180) | 90 degrees (vertical) | 0.62
11 | Istanbul | SSW (202.5) | 0 degrees (horizontal) | 0.93
11 | Istanbul | SSW (202.5) | 10 degrees | 0.97
11 | Istanbul | SSW (202.5) | 20 degrees | 0.99
11 | Istanbul | SSW (202.5) | 30 degrees | 0.99
11 | Istanbul | SSW (202.5) | 40 degrees | 0.97
11 | Istanbul | SSW (202.5) | 50 degrees | 0.93
11 | Istanbul | SSW (202.5) | 60 degrees | 0.87
11 | Istanbul | SSW (202.5) | 70 degrees | 0.8
11 | Istanbul | SSW (202.5) | 80 degrees | 0.71
11 | Istanbul | SSW (202.5) | 90 degrees (vertical) | 0.62
11 | Istanbul | SW (225) | 0 degrees (horizontal) | 0.93
11 | Istanbul | SW (225) | 10 degrees | 0.96
11 | Istanbul | SW (225) | 20 degrees | 0.97
11 | Istanbul | SW (225) | 30 degrees | 0.96
11 | Istanbul | SW (225) | 40 degrees | 0.93
11 | Istanbul | SW (225) | 50 degrees | 0.89
11 | Istanbul | SW (225) | 60 degrees | 0.83
11 | Istanbul | SW (225) | 70 degrees | 0.76
11 | Istanbul | SW (225) | 80 degrees | 0.68
11 | Istanbul | SW (225) | 90 degrees (vertical) | 0.6
11 | Istanbul | WSW (247.5) | 0 degrees (horizontal) | 0.93
11 | Istanbul | WSW (247.5) | 10 degrees | 0.94
11 | Istanbul | WSW (247.5) | 20 degrees | 0.93
11 | Istanbul | WSW (247.5) | 30 degrees | 0.91
11 | Istanbul | WSW (247.5) | 40 degrees | 0.88
11 | Istanbul | WSW (247.5) | 50 degrees | 0.83
11 | Istanbul | WSW (247.5) | 60 degrees | 0.77
11 | Istanbul | WSW (247.5) | 70 degrees | 0.7
11 | Istanbul | WSW (247.5) | 80 degrees | 0.63
11 | Istanbul | WSW (247.5) | 90 degrees (vertical) | 0.56
11 | Istanbul | W (270) | 0 degrees (horizontal) | 0.93
11 | Istanbul | W (270) | 10 degrees | 0.92
11 | Istanbul | W (270) | 20 degrees | 0.89
11 | Istanbul | W (270) | 30 degrees | 0.86
11 | Istanbul | W (270) | 40 degrees | 0.81
11 | Istanbul | W (270) | 50 degrees | 0.76
11 | Istanbul | W (270) | 60 degrees | 0.7
11 | Istanbul | W (270) | 70 degrees | 0.63
11 | Istanbul | W (270) | 80 degrees | 0.57
11 | Istanbul | W (270) | 90 degrees (vertical) | 0.5
11 | Istanbul | WNW (292.5) | 0 degrees (horizontal) | 0.93
11 | Istanbul | WNW (292.5) | 10 degrees | 0.9
11 | Istanbul | WNW (292.5) | 20 degrees | 0.85
11 | Istanbul | WNW (292.5) | 30 degrees | 0.8
11 | Istanbul | WNW (292.5) | 40 degrees | 0.74
11 | Istanbul | WNW (292.5) | 50 degrees | 0.68
11 | Istanbul | WNW (292.5) | 60 degrees | 0.61
11 | Istanbul | WNW (292.5) | 70 degrees | 0.55
11 | Istanbul | WNW (292.5) | 80 degrees | 0.5
11 | Istanbul | WNW (292.5) | 90 degrees (vertical) | 0.44
11 | Istanbul | NW (315) | 0 degrees (horizontal) | 0.93
11 | Istanbul | NW (315) | 10 degrees | 0.88
11 | Istanbul | NW (315) | 20 degrees | 0.82
11 | Istanbul | NW (315) | 30 degrees | 0.74
11 | Istanbul | NW (315) | 40 degrees | 0.67
11 | Istanbul | NW (315) | 50 degrees | 0.59
11 | Istanbul | NW (315) | 60 degrees | 0.53
11 | Istanbul | NW (315) | 70 degrees | 0.47
11 | Istanbul | NW (315) | 80 degrees | 0.42
11 | Istanbul | NW (315) | 90 degrees (vertical) | 0.38
11 | Istanbul | NNW (337.5) | 0 degrees (horizontal) | 0.93
11 | Istanbul | NNW (337.5) | 10 degrees | 0.87
11 | Istanbul | NNW (337.5) | 20 degrees | 0.79
11 | Istanbul | NNW (337.5) | 30 degrees | 0.71
11 | Istanbul | NNW (337.5) | 40 degrees | 0.62
11 | Istanbul | NNW (337.5) | 50 degrees | 0.54
11 | Istanbul | NNW (337.5) | 60 degrees | 0.46
11 | Istanbul | NNW (337.5) | 70 degrees | 0.4
11 | Istanbul | NNW (337.5) | 80 degrees | 0.36
11 | Istanbul | NNW (337.5) | 90 degrees (vertical) | 0.33
12 | Keulen | N ( 0 degrees) | 0 degrees (horizontal) | 0.91
12 | Keulen | N ( 0 degrees) | 10 degrees | 0.85
12 | Keulen | N ( 0 degrees) | 20 degrees | 0.78
12 | Keulen | N ( 0 degrees) | 30 degrees | 0.7
12 | Keulen | N ( 0 degrees) | 40 degrees | 0.63
12 | Keulen | N ( 0 degrees) | 50 degrees | 0.56
12 | Keulen | N ( 0 degrees) | 60 degrees | 0.49
12 | Keulen | N ( 0 degrees) | 70 degrees | 0.45
12 | Keulen | N ( 0 degrees) | 80 degrees | 0.41
12 | Keulen | N ( 0 degrees) | 90 degrees (vertical) | 0.38
12 | Keulen | NNE (22.5) | 0 degrees (horizontal) | 0.91
12 | Keulen | NNE (22.5) | 10 degrees | 0.86
12 | Keulen | NNE (22.5) | 20 degrees | 0.78
12 | Keulen | NNE (22.5) | 30 degrees | 0.71
12 | Keulen | NNE (22.5) | 40 degrees | 0.64
12 | Keulen | NNE (22.5) | 50 degrees | 0.57
12 | Keulen | NNE (22.5) | 60 degrees | 0.51
12 | Keulen | NNE (22.5) | 70 degrees | 0.47
12 | Keulen | NNE (22.5) | 80 degrees | 0.43
12 | Keulen | NNE (22.5) | 90 degrees (vertical) | 0.39
12 | Keulen | NE (45) | 0 degrees (horizontal) | 0.91
12 | Keulen | NE (45) | 10 degrees | 0.87
12 | Keulen | NE (45) | 20 degrees | 0.81
12 | Keulen | NE (45) | 30 degrees | 0.75
12 | Keulen | NE (45) | 40 degrees | 0.68
12 | Keulen | NE (45) | 50 degrees | 0.62
12 | Keulen | NE (45) | 60 degrees | 0.57
12 | Keulen | NE (45) | 70 degrees | 0.52
12 | Keulen | NE (45) | 80 degrees | 0.47
12 | Keulen | NE (45) | 90 degrees (vertical) | 0.43
12 | Keulen | ENE (67.5) | 0 degrees (horizontal) | 0.91
12 | Keulen | ENE (67.5) | 10 degrees | 0.89
12 | Keulen | ENE (67.5) | 20 degrees | 0.85
12 | Keulen | ENE (67.5) | 30 degrees | 0.8
12 | Keulen | ENE (67.5) | 40 degrees | 0.75
12 | Keulen | ENE (67.5) | 50 degrees | 0.69
12 | Keulen | ENE (67.5) | 60 degrees | 0.64
12 | Keulen | ENE (67.5) | 70 degrees | 0.59
12 | Keulen | ENE (67.5) | 80 degrees | 0.53
12 | Keulen | ENE (67.5) | 90 degrees (vertical) | 0.48
12 | Keulen | E (90) | 0 degrees (horizontal) | 0.91
12 | Keulen | E (90) | 10 degrees | 0.91
12 | Keulen | E (90) | 20 degrees | 0.89
12 | Keulen | E (90) | 30 degrees | 0.86
12 | Keulen | E (90) | 40 degrees | 0.82
12 | Keulen | E (90) | 50 degrees | 0.77
12 | Keulen | E (90) | 60 degrees | 0.72
12 | Keulen | E (90) | 70 degrees | 0.66
12 | Keulen | E (90) | 80 degrees | 0.6
12 | Keulen | E (90) | 90 degrees (vertical) | 0.54
12 | Keulen | ESE (112.5) | 0 degrees (horizontal) | 0.91
12 | Keulen | ESE (112.5) | 10 degrees | 0.93
12 | Keulen | ESE (112.5) | 20 degrees | 0.92
12 | Keulen | ESE (112.5) | 30 degrees | 0.91
12 | Keulen | ESE (112.5) | 40 degrees | 0.88
12 | Keulen | ESE (112.5) | 50 degrees | 0.84
12 | Keulen | ESE (112.5) | 60 degrees | 0.79
12 | Keulen | ESE (112.5) | 70 degrees | 0.73
12 | Keulen | ESE (112.5) | 80 degrees | 0.67
12 | Keulen | ESE (112.5) | 90 degrees (vertical) | 0.6
12 | Keulen | SE (135) | 0 degrees (horizontal) | 0.91
12 | Keulen | SE (135) | 10 degrees | 0.94
12 | Keulen | SE (135) | 20 degrees | 0.96
12 | Keulen | SE (135) | 30 degrees | 0.96
12 | Keulen | SE (135) | 40 degrees | 0.94
12 | Keulen | SE (135) | 50 degrees | 0.91
12 | Keulen | SE (135) | 60 degrees | 0.86
12 | Keulen | SE (135) | 70 degrees | 0.8
12 | Keulen | SE (135) | 80 degrees | 0.73
12 | Keulen | SE (135) | 90 degrees (vertical) | 0.65
12 | Keulen | SSE (157.5) | 0 degrees (horizontal) | 0.91
12 | Keulen | SSE (157.5) | 10 degrees | 0.96
12 | Keulen | SSE (157.5) | 20 degrees | 0.98
12 | Keulen | SSE (157.5) | 30 degrees | 0.99
12 | Keulen | SSE (157.5) | 40 degrees | 0.98
12 | Keulen | SSE (157.5) | 50 degrees | 0.95
12 | Keulen | SSE (157.5) | 60 degrees | 0.91
12 | Keulen | SSE (157.5) | 70 degrees | 0.84
12 | Keulen | SSE (157.5) | 80 degrees | 0.77
12 | Keulen | SSE (157.5) | 90 degrees (vertical) | 0.69
12 | Keulen | S (180) | 0 degrees (horizontal) | 0.91
12 | Keulen | S (180) | 10 degrees | 0.96
12 | Keulen | S (180) | 20 degrees | 0.99
12 | Keulen | S (180) | 30 degrees | 1
12 | Keulen | S (180) | 40 degrees | 0.99
12 | Keulen | S (180) | 50 degrees | 0.96
12 | Keulen | S (180) | 60 degrees | 0.92
12 | Keulen | S (180) | 70 degrees | 0.86
12 | Keulen | S (180) | 80 degrees | 0.78
12 | Keulen | S (180) | 90 degrees (vertical) | 0.7
12 | Keulen | SSW (202.5) | 0 degrees (horizontal) | 0.91
12 | Keulen | SSW (202.5) | 10 degrees | 0.96
12 | Keulen | SSW (202.5) | 20 degrees | 0.98
12 | Keulen | SSW (202.5) | 30 degrees | 0.99
12 | Keulen | SSW (202.5) | 40 degrees | 0.98
12 | Keulen | SSW (202.5) | 50 degrees | 0.95
12 | Keulen | SSW (202.5) | 60 degrees | 0.91
12 | Keulen | SSW (202.5) | 70 degrees | 0.84
12 | Keulen | SSW (202.5) | 80 degrees | 0.77
12 | Keulen | SSW (202.5) | 90 degrees (vertical) | 0.69
12 | Keulen | SW (225) | 0 degrees (horizontal) | 0.91
12 | Keulen | SW (225) | 10 degrees | 0.94
12 | Keulen | SW (225) | 20 degrees | 0.96
12 | Keulen | SW (225) | 30 degrees | 0.96
12 | Keulen | SW (225) | 40 degrees | 0.94
12 | Keulen | SW (225) | 50 degrees | 0.91
12 | Keulen | SW (225) | 60 degrees | 0.86
12 | Keulen | SW (225) | 70 degrees | 0.8
12 | Keulen | SW (225) | 80 degrees | 0.73
12 | Keulen | SW (225) | 90 degrees (vertical) | 0.65
12 | Keulen | WSW (247.5) | 0 degrees (horizontal) | 0.91
12 | Keulen | WSW (247.5) | 10 degrees | 0.93
12 | Keulen | WSW (247.5) | 20 degrees | 0.92
12 | Keulen | WSW (247.5) | 30 degrees | 0.91
12 | Keulen | WSW (247.5) | 40 degrees | 0.88
12 | Keulen | WSW (247.5) | 50 degrees | 0.84
12 | Keulen | WSW (247.5) | 60 degrees | 0.79
12 | Keulen | WSW (247.5) | 70 degrees | 0.73
12 | Keulen | WSW (247.5) | 80 degrees | 0.67
12 | Keulen | WSW (247.5) | 90 degrees (vertical) | 0.6
12 | Keulen | W (270) | 0 degrees (horizontal) | 0.91
12 | Keulen | W (270) | 10 degrees | 0.91
12 | Keulen | W (270) | 20 degrees | 0.89
12 | Keulen | W (270) | 30 degrees | 0.86
12 | Keulen | W (270) | 40 degrees | 0.82
12 | Keulen | W (270) | 50 degrees | 0.77
12 | Keulen | W (270) | 60 degrees | 0.72
12 | Keulen | W (270) | 70 degrees | 0.66
12 | Keulen | W (270) | 80 degrees | 0.6
12 | Keulen | W (270) | 90 degrees (vertical) | 0.54
12 | Keulen | WNW (292.5) | 0 degrees (horizontal) | 0.91
12 | Keulen | WNW (292.5) | 10 degrees | 0.89
12 | Keulen | WNW (292.5) | 20 degrees | 0.85
12 | Keulen | WNW (292.5) | 30 degrees | 0.8
12 | Keulen | WNW (292.5) | 40 degrees | 0.75
12 | Keulen | WNW (292.5) | 50 degrees | 0.69
12 | Keulen | WNW (292.5) | 60 degrees | 0.64
12 | Keulen | WNW (292.5) | 70 degrees | 0.59
12 | Keulen | WNW (292.5) | 80 degrees | 0.53
12 | Keulen | WNW (292.5) | 90 degrees (vertical) | 0.48
12 | Keulen | NW (315) | 0 degrees (horizontal) | 0.91
12 | Keulen | NW (315) | 10 degrees | 0.87
12 | Keulen | NW (315) | 20 degrees | 0.81
12 | Keulen | NW (315) | 30 degrees | 0.75
12 | Keulen | NW (315) | 40 degrees | 0.68
12 | Keulen | NW (315) | 50 degrees | 0.62
12 | Keulen | NW (315) | 60 degrees | 0.57
12 | Keulen | NW (315) | 70 degrees | 0.52
12 | Keulen | NW (315) | 80 degrees | 0.47
12 | Keulen | NW (315) | 90 degrees (vertical) | 0.43
12 | Keulen | NNW (337.5) | 0 degrees (horizontal) | 0.91
12 | Keulen | NNW (337.5) | 10 degrees | 0.86
12 | Keulen | NNW (337.5) | 20 degrees | 0.78
12 | Keulen | NNW (337.5) | 30 degrees | 0.71
12 | Keulen | NNW (337.5) | 40 degrees | 0.64
12 | Keulen | NNW (337.5) | 50 degrees | 0.57
12 | Keulen | NNW (337.5) | 60 degrees | 0.51
12 | Keulen | NNW (337.5) | 70 degrees | 0.47
12 | Keulen | NNW (337.5) | 80 degrees | 0.43
12 | Keulen | NNW (337.5) | 90 degrees (vertical) | 0.39
13 | Lima | N ( 0 degrees) | 0 degrees (horizontal) | 0.98
13 | Lima | N ( 0 degrees) | 10 degrees | 1
13 | Lima | N ( 0 degrees) | 20 degrees | 1
13 | Lima | N ( 0 degrees) | 30 degrees | 0.97
13 | Lima | N ( 0 degrees) | 40 degrees | 0.92
13 | Lima | N ( 0 degrees) | 50 degrees | 0.85
13 | Lima | N ( 0 degrees) | 60 degrees | 0.77
13 | Lima | N ( 0 degrees) | 70 degrees | 0.67
13 | Lima | N ( 0 degrees) | 80 degrees | 0.56
13 | Lima | N ( 0 degrees) | 90 degrees (vertical) | 0.46
13 | Lima | NNE (22.5) | 0 degrees (horizontal) | 0.98
13 | Lima | NNE (22.5) | 10 degrees | 1
13 | Lima | NNE (22.5) | 20 degrees | 0.99
13 | Lima | NNE (22.5) | 30 degrees | 0.96
13 | Lima | NNE (22.5) | 40 degrees | 0.91
13 | Lima | NNE (22.5) | 50 degrees | 0.85
13 | Lima | NNE (22.5) | 60 degrees | 0.76
13 | Lima | NNE (22.5) | 70 degrees | 0.67
13 | Lima | NNE (22.5) | 80 degrees | 0.57
13 | Lima | NNE (22.5) | 90 degrees (vertical) | 0.47
13 | Lima | NE (45) | 0 degrees (horizontal) | 0.98
13 | Lima | NE (45) | 10 degrees | 0.99
13 | Lima | NE (45) | 20 degrees | 0.98
13 | Lima | NE (45) | 30 degrees | 0.95
13 | Lima | NE (45) | 40 degrees | 0.9
13 | Lima | NE (45) | 50 degrees | 0.83
13 | Lima | NE (45) | 60 degrees | 0.75
13 | Lima | NE (45) | 70 degrees | 0.66
13 | Lima | NE (45) | 80 degrees | 0.57
13 | Lima | NE (45) | 90 degrees (vertical) | 0.49
13 | Lima | ENE (67.5) | 0 degrees (horizontal) | 0.98
13 | Lima | ENE (67.5) | 10 degrees | 0.98
13 | Lima | ENE (67.5) | 20 degrees | 0.96
13 | Lima | ENE (67.5) | 30 degrees | 0.92
13 | Lima | ENE (67.5) | 40 degrees | 0.87
13 | Lima | ENE (67.5) | 50 degrees | 0.8
13 | Lima | ENE (67.5) | 60 degrees | 0.73
13 | Lima | ENE (67.5) | 70 degrees | 0.65
13 | Lima | ENE (67.5) | 80 degrees | 0.57
13 | Lima | ENE (67.5) | 90 degrees (vertical) | 0.49
13 | Lima | E (90) | 0 degrees (horizontal) | 0.98
13 | Lima | E (90) | 10 degrees | 0.97
13 | Lima | E (90) | 20 degrees | 0.94
13 | Lima | E (90) | 30 degrees | 0.89
13 | Lima | E (90) | 40 degrees | 0.83
13 | Lima | E (90) | 50 degrees | 0.77
13 | Lima | E (90) | 60 degrees | 0.69
13 | Lima | E (90) | 70 degrees | 0.62
13 | Lima | E (90) | 80 degrees | 0.54
13 | Lima | E (90) | 90 degrees (vertical) | 0.47
13 | Lima | ESE (112.5) | 0 degrees (horizontal) | 0.98
13 | Lima | ESE (112.5) | 10 degrees | 0.96
13 | Lima | ESE (112.5) | 20 degrees | 0.92
13 | Lima | ESE (112.5) | 30 degrees | 0.86
13 | Lima | ESE (112.5) | 40 degrees | 0.79
13 | Lima | ESE (112.5) | 50 degrees | 0.72
13 | Lima | ESE (112.5) | 60 degrees | 0.64
13 | Lima | ESE (112.5) | 70 degrees | 0.56
13 | Lima | ESE (112.5) | 80 degrees | 0.49
13 | Lima | ESE (112.5) | 90 degrees (vertical) | 0.43
13 | Lima | SE (135) | 0 degrees (horizontal) | 0.98
13 | Lima | SE (135) | 10 degrees | 0.95
13 | Lima | SE (135) | 20 degrees | 0.9
13 | Lima | SE (135) | 30 degrees | 0.83
13 | Lima | SE (135) | 40 degrees | 0.75
13 | Lima | SE (135) | 50 degrees | 0.66
13 | Lima | SE (135) | 60 degrees | 0.58
13 | Lima | SE (135) | 70 degrees | 0.49
13 | Lima | SE (135) | 80 degrees | 0.42
13 | Lima | SE (135) | 90 degrees (vertical) | 0.37
13 | Lima | SSE (157.5) | 0 degrees (horizontal) | 0.98
13 | Lima | SSE (157.5) | 10 degrees | 0.94
13 | Lima | SSE (157.5) | 20 degrees | 0.88
13 | Lima | SSE (157.5) | 30 degrees | 0.81
13 | Lima | SSE (157.5) | 40 degrees | 0.71
13 | Lima | SSE (157.5) | 50 degrees | 0.61
13 | Lima | SSE (157.5) | 60 degrees | 0.52
13 | Lima | SSE (157.5) | 70 degrees | 0.43
13 | Lima | SSE (157.5) | 80 degrees | 0.36
13 | Lima | SSE (157.5) | 90 degrees (vertical) | 0.31
13 | Lima | S (180) | 0 degrees (horizontal) | 0.98
13 | Lima | S (180) | 10 degrees | 0.94
13 | Lima | S (180) | 20 degrees | 0.88
13 | Lima | S (180) | 30 degrees | 0.8
13 | Lima | S (180) | 40 degrees | 0.7
13 | Lima | S (180) | 50 degrees | 0.59
13 | Lima | S (180) | 60 degrees | 0.49
13 | Lima | S (180) | 70 degrees | 0.41
13 | Lima | S (180) | 80 degrees | 0.35
13 | Lima | S (180) | 90 degrees (vertical) | 0.29
13 | Lima | SSW (202.5) | 0 degrees (horizontal) | 0.98
13 | Lima | SSW (202.5) | 10 degrees | 0.94
13 | Lima | SSW (202.5) | 20 degrees | 0.88
13 | Lima | SSW (202.5) | 30 degrees | 0.81
13 | Lima | SSW (202.5) | 40 degrees | 0.71
13 | Lima | SSW (202.5) | 50 degrees | 0.61
13 | Lima | SSW (202.5) | 60 degrees | 0.52
13 | Lima | SSW (202.5) | 70 degrees | 0.43
13 | Lima | SSW (202.5) | 80 degrees | 0.36
13 | Lima | SSW (202.5) | 90 degrees (vertical) | 0.31
13 | Lima | SW (225) | 0 degrees (horizontal) | 0.98
13 | Lima | SW (225) | 10 degrees | 0.95
13 | Lima | SW (225) | 20 degrees | 0.9
13 | Lima | SW (225) | 30 degrees | 0.83
13 | Lima | SW (225) | 40 degrees | 0.75
13 | Lima | SW (225) | 50 degrees | 0.66
13 | Lima | SW (225) | 60 degrees | 0.58
13 | Lima | SW (225) | 70 degrees | 0.49
13 | Lima | SW (225) | 80 degrees | 0.42
13 | Lima | SW (225) | 90 degrees (vertical) | 0.37
13 | Lima | WSW (247.5) | 0 degrees (horizontal) | 0.98
13 | Lima | WSW (247.5) | 10 degrees | 0.96
13 | Lima | WSW (247.5) | 20 degrees | 0.92
13 | Lima | WSW (247.5) | 30 degrees | 0.86
13 | Lima | WSW (247.5) | 40 degrees | 0.79
13 | Lima | WSW (247.5) | 50 degrees | 0.72
13 | Lima | WSW (247.5) | 60 degrees | 0.64
13 | Lima | WSW (247.5) | 70 degrees | 0.56
13 | Lima | WSW (247.5) | 80 degrees | 0.49
13 | Lima | WSW (247.5) | 90 degrees (vertical) | 0.43
13 | Lima | W (270) | 0 degrees (horizontal) | 0.98
13 | Lima | W (270) | 10 degrees | 0.97
13 | Lima | W (270) | 20 degrees | 0.94
13 | Lima | W (270) | 30 degrees | 0.89
13 | Lima | W (270) | 40 degrees | 0.83
13 | Lima | W (270) | 50 degrees | 0.77
13 | Lima | W (270) | 60 degrees | 0.69
13 | Lima | W (270) | 70 degrees | 0.62
13 | Lima | W (270) | 80 degrees | 0.54
13 | Lima | W (270) | 90 degrees (vertical) | 0.47
13 | Lima | WNW (292.5) | 0 degrees (horizontal) | 0.98
13 | Lima | WNW (292.5) | 10 degrees | 0.98
13 | Lima | WNW (292.5) | 20 degrees | 0.96
13 | Lima | WNW (292.5) | 30 degrees | 0.92
13 | Lima | WNW (292.5) | 40 degrees | 0.87
13 | Lima | WNW (292.5) | 50 degrees | 0.8
13 | Lima | WNW (292.5) | 60 degrees | 0.73
13 | Lima | WNW (292.5) | 70 degrees | 0.65
13 | Lima | WNW (292.5) | 80 degrees | 0.57
13 | Lima | WNW (292.5) | 90 degrees (vertical) | 0.49
13 | Lima | NW (315) | 0 degrees (horizontal) | 0.98
13 | Lima | NW (315) | 10 degrees | 0.99
13 | Lima | NW (315) | 20 degrees | 0.98
13 | Lima | NW (315) | 30 degrees | 0.95
13 | Lima | NW (315) | 40 degrees | 0.9
13 | Lima | NW (315) | 50 degrees | 0.83
13 | Lima | NW (315) | 60 degrees | 0.75
13 | Lima | NW (315) | 70 degrees | 0.66
13 | Lima | NW (315) | 80 degrees | 0.57
13 | Lima | NW (315) | 90 degrees (vertical) | 0.49
13 | Lima | NNW (337.5) | 0 degrees (horizontal) | 0.98
13 | Lima | NNW (337.5) | 10 degrees | 1
13 | Lima | NNW (337.5) | 20 degrees | 0.99
13 | Lima | NNW (337.5) | 30 degrees | 0.96
13 | Lima | NNW (337.5) | 40 degrees | 0.91
13 | Lima | NNW (337.5) | 50 degrees | 0.85
13 | Lima | NNW (337.5) | 60 degrees | 0.76
13 | Lima | NNW (337.5) | 70 degrees | 0.67
13 | Lima | NNW (337.5) | 80 degrees | 0.57
13 | Lima | NNW (337.5) | 90 degrees (vertical) | 0.47
14 | Los Angeles | N ( 0 degrees) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | N ( 0 degrees) | 10 degrees | 0.84
14 | Los Angeles | N ( 0 degrees) | 20 degrees | 0.75
14 | Los Angeles | N ( 0 degrees) | 30 degrees | 0.65
14 | Los Angeles | N ( 0 degrees) | 40 degrees | 0.55
14 | Los Angeles | N ( 0 degrees) | 50 degrees | 0.47
14 | Los Angeles | N ( 0 degrees) | 60 degrees | 0.39
14 | Los Angeles | N ( 0 degrees) | 70 degrees | 0.32
14 | Los Angeles | N ( 0 degrees) | 80 degrees | 0.28
14 | Los Angeles | N ( 0 degrees) | 90 degrees (vertical) | 0.25
14 | Los Angeles | NNE (22.5) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | NNE (22.5) | 10 degrees | 0.85
14 | Los Angeles | NNE (22.5) | 20 degrees | 0.76
14 | Los Angeles | NNE (22.5) | 30 degrees | 0.67
14 | Los Angeles | NNE (22.5) | 40 degrees | 0.57
14 | Los Angeles | NNE (22.5) | 50 degrees | 0.48
14 | Los Angeles | NNE (22.5) | 60 degrees | 0.41
14 | Los Angeles | NNE (22.5) | 70 degrees | 0.35
14 | Los Angeles | NNE (22.5) | 80 degrees | 0.3
14 | Los Angeles | NNE (22.5) | 90 degrees (vertical) | 0.28
14 | Los Angeles | NE (45) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | NE (45) | 10 degrees | 0.86
14 | Los Angeles | NE (45) | 20 degrees | 0.79
14 | Los Angeles | NE (45) | 30 degrees | 0.71
14 | Los Angeles | NE (45) | 40 degrees | 0.63
14 | Los Angeles | NE (45) | 50 degrees | 0.55
14 | Los Angeles | NE (45) | 60 degrees | 0.48
14 | Los Angeles | NE (45) | 70 degrees | 0.42
14 | Los Angeles | NE (45) | 80 degrees | 0.37
14 | Los Angeles | NE (45) | 90 degrees (vertical) | 0.33
14 | Los Angeles | ENE (67.5) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | ENE (67.5) | 10 degrees | 0.88
14 | Los Angeles | ENE (67.5) | 20 degrees | 0.83
14 | Los Angeles | ENE (67.5) | 30 degrees | 0.77
14 | Los Angeles | ENE (67.5) | 40 degrees | 0.71
14 | Los Angeles | ENE (67.5) | 50 degrees | 0.64
14 | Los Angeles | ENE (67.5) | 60 degrees | 0.58
14 | Los Angeles | ENE (67.5) | 70 degrees | 0.51
14 | Los Angeles | ENE (67.5) | 80 degrees | 0.45
14 | Los Angeles | ENE (67.5) | 90 degrees (vertical) | 0.4
14 | Los Angeles | E (90) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | E (90) | 10 degrees | 0.9
14 | Los Angeles | E (90) | 20 degrees | 0.88
14 | Los Angeles | E (90) | 30 degrees | 0.84
14 | Los Angeles | E (90) | 40 degrees | 0.79
14 | Los Angeles | E (90) | 50 degrees | 0.73
14 | Los Angeles | E (90) | 60 degrees | 0.67
14 | Los Angeles | E (90) | 70 degrees | 0.6
14 | Los Angeles | E (90) | 80 degrees | 0.54
14 | Los Angeles | E (90) | 90 degrees (vertical) | 0.47
14 | Los Angeles | ESE (112.5) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | ESE (112.5) | 10 degrees | 0.93
14 | Los Angeles | ESE (112.5) | 20 degrees | 0.92
14 | Los Angeles | ESE (112.5) | 30 degrees | 0.9
14 | Los Angeles | ESE (112.5) | 40 degrees | 0.86
14 | Los Angeles | ESE (112.5) | 50 degrees | 0.81
14 | Los Angeles | ESE (112.5) | 60 degrees | 0.75
14 | Los Angeles | ESE (112.5) | 70 degrees | 0.68
14 | Los Angeles | ESE (112.5) | 80 degrees | 0.61
14 | Los Angeles | ESE (112.5) | 90 degrees (vertical) | 0.53
14 | Los Angeles | SE (135) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | SE (135) | 10 degrees | 0.95
14 | Los Angeles | SE (135) | 20 degrees | 0.96
14 | Los Angeles | SE (135) | 30 degrees | 0.95
14 | Los Angeles | SE (135) | 40 degrees | 0.93
14 | Los Angeles | SE (135) | 50 degrees | 0.88
14 | Los Angeles | SE (135) | 60 degrees | 0.82
14 | Los Angeles | SE (135) | 70 degrees | 0.75
14 | Los Angeles | SE (135) | 80 degrees | 0.67
14 | Los Angeles | SE (135) | 90 degrees (vertical) | 0.58
14 | Los Angeles | SSE (157.5) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | SSE (157.5) | 10 degrees | 0.96
14 | Los Angeles | SSE (157.5) | 20 degrees | 0.99
14 | Los Angeles | SSE (157.5) | 30 degrees | 0.99
14 | Los Angeles | SSE (157.5) | 40 degrees | 0.97
14 | Los Angeles | SSE (157.5) | 50 degrees | 0.93
14 | Los Angeles | SSE (157.5) | 60 degrees | 0.87
14 | Los Angeles | SSE (157.5) | 70 degrees | 0.79
14 | Los Angeles | SSE (157.5) | 80 degrees | 0.7
14 | Los Angeles | SSE (157.5) | 90 degrees (vertical) | 0.6
14 | Los Angeles | S (180) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | S (180) | 10 degrees | 0.96
14 | Los Angeles | S (180) | 20 degrees | 0.99
14 | Los Angeles | S (180) | 30 degrees | 1
14 | Los Angeles | S (180) | 40 degrees | 0.98
14 | Los Angeles | S (180) | 50 degrees | 0.95
14 | Los Angeles | S (180) | 60 degrees | 0.89
14 | Los Angeles | S (180) | 70 degrees | 0.81
14 | Los Angeles | S (180) | 80 degrees | 0.71
14 | Los Angeles | S (180) | 90 degrees (vertical) | 0.61
14 | Los Angeles | SSW (202.5) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | SSW (202.5) | 10 degrees | 0.96
14 | Los Angeles | SSW (202.5) | 20 degrees | 0.99
14 | Los Angeles | SSW (202.5) | 30 degrees | 0.99
14 | Los Angeles | SSW (202.5) | 40 degrees | 0.97
14 | Los Angeles | SSW (202.5) | 50 degrees | 0.93
14 | Los Angeles | SSW (202.5) | 60 degrees | 0.87
14 | Los Angeles | SSW (202.5) | 70 degrees | 0.79
14 | Los Angeles | SSW (202.5) | 80 degrees | 0.7
14 | Los Angeles | SSW (202.5) | 90 degrees (vertical) | 0.6
14 | Los Angeles | SW (225) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | SW (225) | 10 degrees | 0.95
14 | Los Angeles | SW (225) | 20 degrees | 0.96
14 | Los Angeles | SW (225) | 30 degrees | 0.95
14 | Los Angeles | SW (225) | 40 degrees | 0.93
14 | Los Angeles | SW (225) | 50 degrees | 0.88
14 | Los Angeles | SW (225) | 60 degrees | 0.82
14 | Los Angeles | SW (225) | 70 degrees | 0.75
14 | Los Angeles | SW (225) | 80 degrees | 0.67
14 | Los Angeles | SW (225) | 90 degrees (vertical) | 0.58
14 | Los Angeles | WSW (247.5) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | WSW (247.5) | 10 degrees | 0.93
14 | Los Angeles | WSW (247.5) | 20 degrees | 0.92
14 | Los Angeles | WSW (247.5) | 30 degrees | 0.9
14 | Los Angeles | WSW (247.5) | 40 degrees | 0.86
14 | Los Angeles | WSW (247.5) | 50 degrees | 0.81
14 | Los Angeles | WSW (247.5) | 60 degrees | 0.75
14 | Los Angeles | WSW (247.5) | 70 degrees | 0.68
14 | Los Angeles | WSW (247.5) | 80 degrees | 0.61
14 | Los Angeles | WSW (247.5) | 90 degrees (vertical) | 0.53
14 | Los Angeles | W (270) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | W (270) | 10 degrees | 0.9
14 | Los Angeles | W (270) | 20 degrees | 0.88
14 | Los Angeles | W (270) | 30 degrees | 0.84
14 | Los Angeles | W (270) | 40 degrees | 0.79
14 | Los Angeles | W (270) | 50 degrees | 0.73
14 | Los Angeles | W (270) | 60 degrees | 0.67
14 | Los Angeles | W (270) | 70 degrees | 0.6
14 | Los Angeles | W (270) | 80 degrees | 0.54
14 | Los Angeles | W (270) | 90 degrees (vertical) | 0.47
14 | Los Angeles | WNW (292.5) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | WNW (292.5) | 10 degrees | 0.88
14 | Los Angeles | WNW (292.5) | 20 degrees | 0.83
14 | Los Angeles | WNW (292.5) | 30 degrees | 0.77
14 | Los Angeles | WNW (292.5) | 40 degrees | 0.71
14 | Los Angeles | WNW (292.5) | 50 degrees | 0.64
14 | Los Angeles | WNW (292.5) | 60 degrees | 0.58
14 | Los Angeles | WNW (292.5) | 70 degrees | 0.51
14 | Los Angeles | WNW (292.5) | 80 degrees | 0.45
14 | Los Angeles | WNW (292.5) | 90 degrees (vertical) | 0.4
14 | Los Angeles | NW (315) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | NW (315) | 10 degrees | 0.86
14 | Los Angeles | NW (315) | 20 degrees | 0.79
14 | Los Angeles | NW (315) | 30 degrees | 0.71
14 | Los Angeles | NW (315) | 40 degrees | 0.63
14 | Los Angeles | NW (315) | 50 degrees | 0.55
14 | Los Angeles | NW (315) | 60 degrees | 0.48
14 | Los Angeles | NW (315) | 70 degrees | 0.42
14 | Los Angeles | NW (315) | 80 degrees | 0.37
14 | Los Angeles | NW (315) | 90 degrees (vertical) | 0.33
14 | Los Angeles | NNW (337.5) | 0 degrees (horizontal) | 0.91
14 | Los Angeles | NNW (337.5) | 10 degrees | 0.85
14 | Los Angeles | NNW (337.5) | 20 degrees | 0.76
14 | Los Angeles | NNW (337.5) | 30 degrees | 0.67
14 | Los Angeles | NNW (337.5) | 40 degrees | 0.57
14 | Los Angeles | NNW (337.5) | 50 degrees | 0.48
14 | Los Angeles | NNW (337.5) | 60 degrees | 0.41
14 | Los Angeles | NNW (337.5) | 70 degrees | 0.35
14 | Los Angeles | NNW (337.5) | 80 degrees | 0.3
14 | Los Angeles | NNW (337.5) | 90 degrees (vertical) | 0.28
15 | Milaan | N ( 0 degrees) | 0 degrees (horizontal) | 0.91
15 | Milaan | N ( 0 degrees) | 10 degrees | 0.84
15 | Milaan | N ( 0 degrees) | 20 degrees | 0.76
15 | Milaan | N ( 0 degrees) | 30 degrees | 0.67
15 | Milaan | N ( 0 degrees) | 40 degrees | 0.58
15 | Milaan | N ( 0 degrees) | 50 degrees | 0.5
15 | Milaan | N ( 0 degrees) | 60 degrees | 0.43
15 | Milaan | N ( 0 degrees) | 70 degrees | 0.37
15 | Milaan | N ( 0 degrees) | 80 degrees | 0.34
15 | Milaan | N ( 0 degrees) | 90 degrees (vertical) | 0.32
15 | Milaan | NNE (22.5) | 0 degrees (horizontal) | 0.91
15 | Milaan | NNE (22.5) | 10 degrees | 0.84
15 | Milaan | NNE (22.5) | 20 degrees | 0.77
15 | Milaan | NNE (22.5) | 30 degrees | 0.68
15 | Milaan | NNE (22.5) | 40 degrees | 0.6
15 | Milaan | NNE (22.5) | 50 degrees | 0.52
15 | Milaan | NNE (22.5) | 60 degrees | 0.45
15 | Milaan | NNE (22.5) | 70 degrees | 0.4
15 | Milaan | NNE (22.5) | 80 degrees | 0.37
15 | Milaan | NNE (22.5) | 90 degrees (vertical) | 0.33
15 | Milaan | NE (45) | 0 degrees (horizontal) | 0.91
15 | Milaan | NE (45) | 10 degrees | 0.86
15 | Milaan | NE (45) | 20 degrees | 0.79
15 | Milaan | NE (45) | 30 degrees | 0.72
15 | Milaan | NE (45) | 40 degrees | 0.65
15 | Milaan | NE (45) | 50 degrees | 0.58
15 | Milaan | NE (45) | 60 degrees | 0.52
15 | Milaan | NE (45) | 70 degrees | 0.47
15 | Milaan | NE (45) | 80 degrees | 0.42
15 | Milaan | NE (45) | 90 degrees (vertical) | 0.38
15 | Milaan | ENE (67.5) | 0 degrees (horizontal) | 0.91
15 | Milaan | ENE (67.5) | 10 degrees | 0.88
15 | Milaan | ENE (67.5) | 20 degrees | 0.83
15 | Milaan | ENE (67.5) | 30 degrees | 0.78
15 | Milaan | ENE (67.5) | 40 degrees | 0.72
15 | Milaan | ENE (67.5) | 50 degrees | 0.66
15 | Milaan | ENE (67.5) | 60 degrees | 0.61
15 | Milaan | ENE (67.5) | 70 degrees | 0.55
15 | Milaan | ENE (67.5) | 80 degrees | 0.49
15 | Milaan | ENE (67.5) | 90 degrees (vertical) | 0.44
15 | Milaan | E (90) | 0 degrees (horizontal) | 0.91
15 | Milaan | E (90) | 10 degrees | 0.9
15 | Milaan | E (90) | 20 degrees | 0.88
15 | Milaan | E (90) | 30 degrees | 0.84
15 | Milaan | E (90) | 40 degrees | 0.8
15 | Milaan | E (90) | 50 degrees | 0.75
15 | Milaan | E (90) | 60 degrees | 0.69
15 | Milaan | E (90) | 70 degrees | 0.63
15 | Milaan | E (90) | 80 degrees | 0.57
15 | Milaan | E (90) | 90 degrees (vertical) | 0.51
15 | Milaan | ESE (112.5) | 0 degrees (horizontal) | 0.91
15 | Milaan | ESE (112.5) | 10 degrees | 0.92
15 | Milaan | ESE (112.5) | 20 degrees | 0.92
15 | Milaan | ESE (112.5) | 30 degrees | 0.9
15 | Milaan | ESE (112.5) | 40 degrees | 0.87
15 | Milaan | ESE (112.5) | 50 degrees | 0.83
15 | Milaan | ESE (112.5) | 60 degrees | 0.78
15 | Milaan | ESE (112.5) | 70 degrees | 0.71
15 | Milaan | ESE (112.5) | 80 degrees | 0.64
15 | Milaan | ESE (112.5) | 90 degrees (vertical) | 0.57
15 | Milaan | SE (135) | 0 degrees (horizontal) | 0.91
15 | Milaan | SE (135) | 10 degrees | 0.94
15 | Milaan | SE (135) | 20 degrees | 0.96
15 | Milaan | SE (135) | 30 degrees | 0.95
15 | Milaan | SE (135) | 40 degrees | 0.93
15 | Milaan | SE (135) | 50 degrees | 0.9
15 | Milaan | SE (135) | 60 degrees | 0.85
15 | Milaan | SE (135) | 70 degrees | 0.78
15 | Milaan | SE (135) | 80 degrees | 0.7
15 | Milaan | SE (135) | 90 degrees (vertical) | 0.62
15 | Milaan | SSE (157.5) | 0 degrees (horizontal) | 0.91
15 | Milaan | SSE (157.5) | 10 degrees | 0.95
15 | Milaan | SSE (157.5) | 20 degrees | 0.98
15 | Milaan | SSE (157.5) | 30 degrees | 0.99
15 | Milaan | SSE (157.5) | 40 degrees | 0.98
15 | Milaan | SSE (157.5) | 50 degrees | 0.94
15 | Milaan | SSE (157.5) | 60 degrees | 0.89
15 | Milaan | SSE (157.5) | 70 degrees | 0.82
15 | Milaan | SSE (157.5) | 80 degrees | 0.74
15 | Milaan | SSE (157.5) | 90 degrees (vertical) | 0.65
15 | Milaan | S (180) | 0 degrees (horizontal) | 0.91
15 | Milaan | S (180) | 10 degrees | 0.96
15 | Milaan | S (180) | 20 degrees | 0.99
15 | Milaan | S (180) | 30 degrees | 1
15 | Milaan | S (180) | 40 degrees | 0.99
15 | Milaan | S (180) | 50 degrees | 0.96
15 | Milaan | S (180) | 60 degrees | 0.91
15 | Milaan | S (180) | 70 degrees | 0.84
15 | Milaan | S (180) | 80 degrees | 0.76
15 | Milaan | S (180) | 90 degrees (vertical) | 0.66
15 | Milaan | SSW (202.5) | 0 degrees (horizontal) | 0.91
15 | Milaan | SSW (202.5) | 10 degrees | 0.95
15 | Milaan | SSW (202.5) | 20 degrees | 0.98
15 | Milaan | SSW (202.5) | 30 degrees | 0.99
15 | Milaan | SSW (202.5) | 40 degrees | 0.98
15 | Milaan | SSW (202.5) | 50 degrees | 0.94
15 | Milaan | SSW (202.5) | 60 degrees | 0.89
15 | Milaan | SSW (202.5) | 70 degrees | 0.82
15 | Milaan | SSW (202.5) | 80 degrees | 0.74
15 | Milaan | SSW (202.5) | 90 degrees (vertical) | 0.65
15 | Milaan | SW (225) | 0 degrees (horizontal) | 0.91
15 | Milaan | SW (225) | 10 degrees | 0.94
15 | Milaan | SW (225) | 20 degrees | 0.96
15 | Milaan | SW (225) | 30 degrees | 0.95
15 | Milaan | SW (225) | 40 degrees | 0.93
15 | Milaan | SW (225) | 50 degrees | 0.9
15 | Milaan | SW (225) | 60 degrees | 0.85
15 | Milaan | SW (225) | 70 degrees | 0.78
15 | Milaan | SW (225) | 80 degrees | 0.7
15 | Milaan | SW (225) | 90 degrees (vertical) | 0.62
15 | Milaan | WSW (247.5) | 0 degrees (horizontal) | 0.91
15 | Milaan | WSW (247.5) | 10 degrees | 0.92
15 | Milaan | WSW (247.5) | 20 degrees | 0.92
15 | Milaan | WSW (247.5) | 30 degrees | 0.9
15 | Milaan | WSW (247.5) | 40 degrees | 0.87
15 | Milaan | WSW (247.5) | 50 degrees | 0.83
15 | Milaan | WSW (247.5) | 60 degrees | 0.78
15 | Milaan | WSW (247.5) | 70 degrees | 0.71
15 | Milaan | WSW (247.5) | 80 degrees | 0.64
15 | Milaan | WSW (247.5) | 90 degrees (vertical) | 0.57
15 | Milaan | W (270) | 0 degrees (horizontal) | 0.91
15 | Milaan | W (270) | 10 degrees | 0.9
15 | Milaan | W (270) | 20 degrees | 0.88
15 | Milaan | W (270) | 30 degrees | 0.84
15 | Milaan | W (270) | 40 degrees | 0.8
15 | Milaan | W (270) | 50 degrees | 0.75
15 | Milaan | W (270) | 60 degrees | 0.69
15 | Milaan | W (270) | 70 degrees | 0.63
15 | Milaan | W (270) | 80 degrees | 0.57
15 | Milaan | W (270) | 90 degrees (vertical) | 0.51
15 | Milaan | WNW (292.5) | 0 degrees (horizontal) | 0.91
15 | Milaan | WNW (292.5) | 10 degrees | 0.88
15 | Milaan | WNW (292.5) | 20 degrees | 0.83
15 | Milaan | WNW (292.5) | 30 degrees | 0.78
15 | Milaan | WNW (292.5) | 40 degrees | 0.72
15 | Milaan | WNW (292.5) | 50 degrees | 0.66
15 | Milaan | WNW (292.5) | 60 degrees | 0.61
15 | Milaan | WNW (292.5) | 70 degrees | 0.55
15 | Milaan | WNW (292.5) | 80 degrees | 0.49
15 | Milaan | WNW (292.5) | 90 degrees (vertical) | 0.44
15 | Milaan | NW (315) | 0 degrees (horizontal) | 0.91
15 | Milaan | NW (315) | 10 degrees | 0.86
15 | Milaan | NW (315) | 20 degrees | 0.79
15 | Milaan | NW (315) | 30 degrees | 0.72
15 | Milaan | NW (315) | 40 degrees | 0.65
15 | Milaan | NW (315) | 50 degrees | 0.58
15 | Milaan | NW (315) | 60 degrees | 0.52
15 | Milaan | NW (315) | 70 degrees | 0.47
15 | Milaan | NW (315) | 80 degrees | 0.42
15 | Milaan | NW (315) | 90 degrees (vertical) | 0.38
15 | Milaan | NNW (337.5) | 0 degrees (horizontal) | 0.91
15 | Milaan | NNW (337.5) | 10 degrees | 0.84
15 | Milaan | NNW (337.5) | 20 degrees | 0.77
15 | Milaan | NNW (337.5) | 30 degrees | 0.68
15 | Milaan | NNW (337.5) | 40 degrees | 0.6
15 | Milaan | NNW (337.5) | 50 degrees | 0.52
15 | Milaan | NNW (337.5) | 60 degrees | 0.45
15 | Milaan | NNW (337.5) | 70 degrees | 0.4
15 | Milaan | NNW (337.5) | 80 degrees | 0.37
15 | Milaan | NNW (337.5) | 90 degrees (vertical) | 0.33
16 | Parijs | N ( 0 degrees) | 0 degrees (horizontal) | 0.92
16 | Parijs | N ( 0 degrees) | 10 degrees | 0.85
16 | Parijs | N ( 0 degrees) | 20 degrees | 0.78
16 | Parijs | N ( 0 degrees) | 30 degrees | 0.7
16 | Parijs | N ( 0 degrees) | 40 degrees | 0.62
16 | Parijs | N ( 0 degrees) | 50 degrees | 0.55
16 | Parijs | N ( 0 degrees) | 60 degrees | 0.48
16 | Parijs | N ( 0 degrees) | 70 degrees | 0.43
16 | Parijs | N ( 0 degrees) | 80 degrees | 0.4
16 | Parijs | N ( 0 degrees) | 90 degrees (vertical) | 0.36
16 | Parijs | NNE (22.5) | 0 degrees (horizontal) | 0.92
16 | Parijs | NNE (22.5) | 10 degrees | 0.86
16 | Parijs | NNE (22.5) | 20 degrees | 0.79
16 | Parijs | NNE (22.5) | 30 degrees | 0.71
16 | Parijs | NNE (22.5) | 40 degrees | 0.63
16 | Parijs | NNE (22.5) | 50 degrees | 0.56
16 | Parijs | NNE (22.5) | 60 degrees | 0.5
16 | Parijs | NNE (22.5) | 70 degrees | 0.45
16 | Parijs | NNE (22.5) | 80 degrees | 0.42
16 | Parijs | NNE (22.5) | 90 degrees (vertical) | 0.38
16 | Parijs | NE (45) | 0 degrees (horizontal) | 0.92
16 | Parijs | NE (45) | 10 degrees | 0.87
16 | Parijs | NE (45) | 20 degrees | 0.81
16 | Parijs | NE (45) | 30 degrees | 0.74
16 | Parijs | NE (45) | 40 degrees | 0.68
16 | Parijs | NE (45) | 50 degrees | 0.62
16 | Parijs | NE (45) | 60 degrees | 0.56
16 | Parijs | NE (45) | 70 degrees | 0.51
16 | Parijs | NE (45) | 80 degrees | 0.46
16 | Parijs | NE (45) | 90 degrees (vertical) | 0.42
16 | Parijs | ENE (67.5) | 0 degrees (horizontal) | 0.92
16 | Parijs | ENE (67.5) | 10 degrees | 0.89
16 | Parijs | ENE (67.5) | 20 degrees | 0.85
16 | Parijs | ENE (67.5) | 30 degrees | 0.8
16 | Parijs | ENE (67.5) | 40 degrees | 0.74
16 | Parijs | ENE (67.5) | 50 degrees | 0.69
16 | Parijs | ENE (67.5) | 60 degrees | 0.63
16 | Parijs | ENE (67.5) | 70 degrees | 0.58
16 | Parijs | ENE (67.5) | 80 degrees | 0.52
16 | Parijs | ENE (67.5) | 90 degrees (vertical) | 0.47
16 | Parijs | E (90) | 0 degrees (horizontal) | 0.92
16 | Parijs | E (90) | 10 degrees | 0.91
16 | Parijs | E (90) | 20 degrees | 0.89
16 | Parijs | E (90) | 30 degrees | 0.85
16 | Parijs | E (90) | 40 degrees | 0.81
16 | Parijs | E (90) | 50 degrees | 0.77
16 | Parijs | E (90) | 60 degrees | 0.71
16 | Parijs | E (90) | 70 degrees | 0.65
16 | Parijs | E (90) | 80 degrees | 0.59
16 | Parijs | E (90) | 90 degrees (vertical) | 0.53
16 | Parijs | ESE (112.5) | 0 degrees (horizontal) | 0.92
16 | Parijs | ESE (112.5) | 10 degrees | 0.93
16 | Parijs | ESE (112.5) | 20 degrees | 0.93
16 | Parijs | ESE (112.5) | 30 degrees | 0.91
16 | Parijs | ESE (112.5) | 40 degrees | 0.88
16 | Parijs | ESE (112.5) | 50 degrees | 0.84
16 | Parijs | ESE (112.5) | 60 degrees | 0.79
16 | Parijs | ESE (112.5) | 70 degrees | 0.73
16 | Parijs | ESE (112.5) | 80 degrees | 0.66
16 | Parijs | ESE (112.5) | 90 degrees (vertical) | 0.59
16 | Parijs | SE (135) | 0 degrees (horizontal) | 0.92
16 | Parijs | SE (135) | 10 degrees | 0.95
16 | Parijs | SE (135) | 20 degrees | 0.96
16 | Parijs | SE (135) | 30 degrees | 0.96
16 | Parijs | SE (135) | 40 degrees | 0.94
16 | Parijs | SE (135) | 50 degrees | 0.9
16 | Parijs | SE (135) | 60 degrees | 0.85
16 | Parijs | SE (135) | 70 degrees | 0.79
16 | Parijs | SE (135) | 80 degrees | 0.72
16 | Parijs | SE (135) | 90 degrees (vertical) | 0.64
16 | Parijs | SSE (157.5) | 0 degrees (horizontal) | 0.92
16 | Parijs | SSE (157.5) | 10 degrees | 0.96
16 | Parijs | SSE (157.5) | 20 degrees | 0.98
16 | Parijs | SSE (157.5) | 30 degrees | 0.99
16 | Parijs | SSE (157.5) | 40 degrees | 0.98
16 | Parijs | SSE (157.5) | 50 degrees | 0.95
16 | Parijs | SSE (157.5) | 60 degrees | 0.9
16 | Parijs | SSE (157.5) | 70 degrees | 0.84
16 | Parijs | SSE (157.5) | 80 degrees | 0.76
16 | Parijs | SSE (157.5) | 90 degrees (vertical) | 0.67
16 | Parijs | S (180) | 0 degrees (horizontal) | 0.92
16 | Parijs | S (180) | 10 degrees | 0.96
16 | Parijs | S (180) | 20 degrees | 0.99
16 | Parijs | S (180) | 30 degrees | 1
16 | Parijs | S (180) | 40 degrees | 0.99
16 | Parijs | S (180) | 50 degrees | 0.96
16 | Parijs | S (180) | 60 degrees | 0.91
16 | Parijs | S (180) | 70 degrees | 0.85
16 | Parijs | S (180) | 80 degrees | 0.77
16 | Parijs | S (180) | 90 degrees (vertical) | 0.68
16 | Parijs | SSW (202.5) | 0 degrees (horizontal) | 0.92
16 | Parijs | SSW (202.5) | 10 degrees | 0.96
16 | Parijs | SSW (202.5) | 20 degrees | 0.98
16 | Parijs | SSW (202.5) | 30 degrees | 0.99
16 | Parijs | SSW (202.5) | 40 degrees | 0.98
16 | Parijs | SSW (202.5) | 50 degrees | 0.95
16 | Parijs | SSW (202.5) | 60 degrees | 0.9
16 | Parijs | SSW (202.5) | 70 degrees | 0.84
16 | Parijs | SSW (202.5) | 80 degrees | 0.76
16 | Parijs | SSW (202.5) | 90 degrees (vertical) | 0.67
16 | Parijs | SW (225) | 0 degrees (horizontal) | 0.92
16 | Parijs | SW (225) | 10 degrees | 0.95
16 | Parijs | SW (225) | 20 degrees | 0.96
16 | Parijs | SW (225) | 30 degrees | 0.96
16 | Parijs | SW (225) | 40 degrees | 0.94
16 | Parijs | SW (225) | 50 degrees | 0.9
16 | Parijs | SW (225) | 60 degrees | 0.85
16 | Parijs | SW (225) | 70 degrees | 0.79
16 | Parijs | SW (225) | 80 degrees | 0.72
16 | Parijs | SW (225) | 90 degrees (vertical) | 0.64
16 | Parijs | WSW (247.5) | 0 degrees (horizontal) | 0.92
16 | Parijs | WSW (247.5) | 10 degrees | 0.93
16 | Parijs | WSW (247.5) | 20 degrees | 0.93
16 | Parijs | WSW (247.5) | 30 degrees | 0.91
16 | Parijs | WSW (247.5) | 40 degrees | 0.88
16 | Parijs | WSW (247.5) | 50 degrees | 0.84
16 | Parijs | WSW (247.5) | 60 degrees | 0.79
16 | Parijs | WSW (247.5) | 70 degrees | 0.73
16 | Parijs | WSW (247.5) | 80 degrees | 0.66
16 | Parijs | WSW (247.5) | 90 degrees (vertical) | 0.59
16 | Parijs | W (270) | 0 degrees (horizontal) | 0.92
16 | Parijs | W (270) | 10 degrees | 0.91
16 | Parijs | W (270) | 20 degrees | 0.89
16 | Parijs | W (270) | 30 degrees | 0.85
16 | Parijs | W (270) | 40 degrees | 0.81
16 | Parijs | W (270) | 50 degrees | 0.77
16 | Parijs | W (270) | 60 degrees | 0.71
16 | Parijs | W (270) | 70 degrees | 0.65
16 | Parijs | W (270) | 80 degrees | 0.59
16 | Parijs | W (270) | 90 degrees (vertical) | 0.53
16 | Parijs | WNW (292.5) | 0 degrees (horizontal) | 0.92
16 | Parijs | WNW (292.5) | 10 degrees | 0.89
16 | Parijs | WNW (292.5) | 20 degrees | 0.85
16 | Parijs | WNW (292.5) | 30 degrees | 0.8
16 | Parijs | WNW (292.5) | 40 degrees | 0.74
16 | Parijs | WNW (292.5) | 50 degrees | 0.69
16 | Parijs | WNW (292.5) | 60 degrees | 0.63
16 | Parijs | WNW (292.5) | 70 degrees | 0.58
16 | Parijs | WNW (292.5) | 80 degrees | 0.52
16 | Parijs | WNW (292.5) | 90 degrees (vertical) | 0.47
16 | Parijs | NW (315) | 0 degrees (horizontal) | 0.92
16 | Parijs | NW (315) | 10 degrees | 0.87
16 | Parijs | NW (315) | 20 degrees | 0.81
16 | Parijs | NW (315) | 30 degrees | 0.74
16 | Parijs | NW (315) | 40 degrees | 0.68
16 | Parijs | NW (315) | 50 degrees | 0.62
16 | Parijs | NW (315) | 60 degrees | 0.56
16 | Parijs | NW (315) | 70 degrees | 0.51
16 | Parijs | NW (315) | 80 degrees | 0.46
16 | Parijs | NW (315) | 90 degrees (vertical) | 0.42
16 | Parijs | NNW (337.5) | 0 degrees (horizontal) | 0.92
16 | Parijs | NNW (337.5) | 10 degrees | 0.86
16 | Parijs | NNW (337.5) | 20 degrees | 0.79
16 | Parijs | NNW (337.5) | 30 degrees | 0.71
16 | Parijs | NNW (337.5) | 40 degrees | 0.63
16 | Parijs | NNW (337.5) | 50 degrees | 0.56
16 | Parijs | NNW (337.5) | 60 degrees | 0.5
16 | Parijs | NNW (337.5) | 70 degrees | 0.45
16 | Parijs | NNW (337.5) | 80 degrees | 0.42
16 | Parijs | NNW (337.5) | 90 degrees (vertical) | 0.38
17 | Perth | N ( 0 degrees) | 0 degrees (horizontal) | 0.93
17 | Perth | N ( 0 degrees) | 10 degrees | 0.98
17 | Perth | N ( 0 degrees) | 20 degrees | 1
17 | Perth | N ( 0 degrees) | 30 degrees | 1
17 | Perth | N ( 0 degrees) | 40 degrees | 0.98
17 | Perth | N ( 0 degrees) | 50 degrees | 0.93
17 | Perth | N ( 0 degrees) | 60 degrees | 0.87
17 | Perth | N ( 0 degrees) | 70 degrees | 0.79
17 | Perth | N ( 0 degrees) | 80 degrees | 0.69
17 | Perth | N ( 0 degrees) | 90 degrees (vertical) | 0.58
17 | Perth | NNE (22.5) | 0 degrees (horizontal) | 0.93
17 | Perth | NNE (22.5) | 10 degrees | 0.97
17 | Perth | NNE (22.5) | 20 degrees | 0.99
17 | Perth | NNE (22.5) | 30 degrees | 0.99
17 | Perth | NNE (22.5) | 40 degrees | 0.97
17 | Perth | NNE (22.5) | 50 degrees | 0.92
17 | Perth | NNE (22.5) | 60 degrees | 0.86
17 | Perth | NNE (22.5) | 70 degrees | 0.78
17 | Perth | NNE (22.5) | 80 degrees | 0.68
17 | Perth | NNE (22.5) | 90 degrees (vertical) | 0.58
17 | Perth | NE (45) | 0 degrees (horizontal) | 0.93
17 | Perth | NE (45) | 10 degrees | 0.96
17 | Perth | NE (45) | 20 degrees | 0.97
17 | Perth | NE (45) | 30 degrees | 0.96
17 | Perth | NE (45) | 40 degrees | 0.93
17 | Perth | NE (45) | 50 degrees | 0.88
17 | Perth | NE (45) | 60 degrees | 0.82
17 | Perth | NE (45) | 70 degrees | 0.74
17 | Perth | NE (45) | 80 degrees | 0.66
17 | Perth | NE (45) | 90 degrees (vertical) | 0.57
17 | Perth | ENE (67.5) | 0 degrees (horizontal) | 0.93
17 | Perth | ENE (67.5) | 10 degrees | 0.94
17 | Perth | ENE (67.5) | 20 degrees | 0.93
17 | Perth | ENE (67.5) | 30 degrees | 0.91
17 | Perth | ENE (67.5) | 40 degrees | 0.87
17 | Perth | ENE (67.5) | 50 degrees | 0.82
17 | Perth | ENE (67.5) | 60 degrees | 0.75
17 | Perth | ENE (67.5) | 70 degrees | 0.68
17 | Perth | ENE (67.5) | 80 degrees | 0.61
17 | Perth | ENE (67.5) | 90 degrees (vertical) | 0.53
17 | Perth | E (90) | 0 degrees (horizontal) | 0.93
17 | Perth | E (90) | 10 degrees | 0.92
17 | Perth | E (90) | 20 degrees | 0.89
17 | Perth | E (90) | 30 degrees | 0.85
17 | Perth | E (90) | 40 degrees | 0.8
17 | Perth | E (90) | 50 degrees | 0.74
17 | Perth | E (90) | 60 degrees | 0.68
17 | Perth | E (90) | 70 degrees | 0.61
17 | Perth | E (90) | 80 degrees | 0.54
17 | Perth | E (90) | 90 degrees (vertical) | 0.48
17 | Perth | ESE (112.5) | 0 degrees (horizontal) | 0.93
17 | Perth | ESE (112.5) | 10 degrees | 0.9
17 | Perth | ESE (112.5) | 20 degrees | 0.85
17 | Perth | ESE (112.5) | 30 degrees | 0.79
17 | Perth | ESE (112.5) | 40 degrees | 0.73
17 | Perth | ESE (112.5) | 50 degrees | 0.66
17 | Perth | ESE (112.5) | 60 degrees | 0.59
17 | Perth | ESE (112.5) | 70 degrees | 0.53
17 | Perth | ESE (112.5) | 80 degrees | 0.47
17 | Perth | ESE (112.5) | 90 degrees (vertical) | 0.41
17 | Perth | SE (135) | 0 degrees (horizontal) | 0.93
17 | Perth | SE (135) | 10 degrees | 0.88
17 | Perth | SE (135) | 20 degrees | 0.81
17 | Perth | SE (135) | 30 degrees | 0.74
17 | Perth | SE (135) | 40 degrees | 0.65
17 | Perth | SE (135) | 50 degrees | 0.57
17 | Perth | SE (135) | 60 degrees | 0.5
17 | Perth | SE (135) | 70 degrees | 0.44
17 | Perth | SE (135) | 80 degrees | 0.38
17 | Perth | SE (135) | 90 degrees (vertical) | 0.34
17 | Perth | SSE (157.5) | 0 degrees (horizontal) | 0.93
17 | Perth | SSE (157.5) | 10 degrees | 0.87
17 | Perth | SSE (157.5) | 20 degrees | 0.79
17 | Perth | SSE (157.5) | 30 degrees | 0.7
17 | Perth | SSE (157.5) | 40 degrees | 0.6
17 | Perth | SSE (157.5) | 50 degrees | 0.51
17 | Perth | SSE (157.5) | 60 degrees | 0.43
17 | Perth | SSE (157.5) | 70 degrees | 0.36
17 | Perth | SSE (157.5) | 80 degrees | 0.32
17 | Perth | SSE (157.5) | 90 degrees (vertical) | 0.29
17 | Perth | S (180) | 0 degrees (horizontal) | 0.93
17 | Perth | S (180) | 10 degrees | 0.86
17 | Perth | S (180) | 20 degrees | 0.78
17 | Perth | S (180) | 30 degrees | 0.68
17 | Perth | S (180) | 40 degrees | 0.58
17 | Perth | S (180) | 50 degrees | 0.49
17 | Perth | S (180) | 60 degrees | 0.41
17 | Perth | S (180) | 70 degrees | 0.34
17 | Perth | S (180) | 80 degrees | 0.29
17 | Perth | S (180) | 90 degrees (vertical) | 0.26
17 | Perth | SSW (202.5) | 0 degrees (horizontal) | 0.93
17 | Perth | SSW (202.5) | 10 degrees | 0.87
17 | Perth | SSW (202.5) | 20 degrees | 0.79
17 | Perth | SSW (202.5) | 30 degrees | 0.7
17 | Perth | SSW (202.5) | 40 degrees | 0.6
17 | Perth | SSW (202.5) | 50 degrees | 0.51
17 | Perth | SSW (202.5) | 60 degrees | 0.43
17 | Perth | SSW (202.5) | 70 degrees | 0.36
17 | Perth | SSW (202.5) | 80 degrees | 0.32
17 | Perth | SSW (202.5) | 90 degrees (vertical) | 0.29
17 | Perth | SW (225) | 0 degrees (horizontal) | 0.93
17 | Perth | SW (225) | 10 degrees | 0.88
17 | Perth | SW (225) | 20 degrees | 0.81
17 | Perth | SW (225) | 30 degrees | 0.74
17 | Perth | SW (225) | 40 degrees | 0.65
17 | Perth | SW (225) | 50 degrees | 0.57
17 | Perth | SW (225) | 60 degrees | 0.5
17 | Perth | SW (225) | 70 degrees | 0.44
17 | Perth | SW (225) | 80 degrees | 0.38
17 | Perth | SW (225) | 90 degrees (vertical) | 0.34
17 | Perth | WSW (247.5) | 0 degrees (horizontal) | 0.93
17 | Perth | WSW (247.5) | 10 degrees | 0.9
17 | Perth | WSW (247.5) | 20 degrees | 0.85
17 | Perth | WSW (247.5) | 30 degrees | 0.79
17 | Perth | WSW (247.5) | 40 degrees | 0.73
17 | Perth | WSW (247.5) | 50 degrees | 0.66
17 | Perth | WSW (247.5) | 60 degrees | 0.59
17 | Perth | WSW (247.5) | 70 degrees | 0.53
17 | Perth | WSW (247.5) | 80 degrees | 0.47
17 | Perth | WSW (247.5) | 90 degrees (vertical) | 0.41
17 | Perth | W (270) | 0 degrees (horizontal) | 0.93
17 | Perth | W (270) | 10 degrees | 0.92
17 | Perth | W (270) | 20 degrees | 0.89
17 | Perth | W (270) | 30 degrees | 0.85
17 | Perth | W (270) | 40 degrees | 0.8
17 | Perth | W (270) | 50 degrees | 0.74
17 | Perth | W (270) | 60 degrees | 0.68
17 | Perth | W (270) | 70 degrees | 0.61
17 | Perth | W (270) | 80 degrees | 0.54
17 | Perth | W (270) | 90 degrees (vertical) | 0.48
17 | Perth | WNW (292.5) | 0 degrees (horizontal) | 0.93
17 | Perth | WNW (292.5) | 10 degrees | 0.94
17 | Perth | WNW (292.5) | 20 degrees | 0.93
17 | Perth | WNW (292.5) | 30 degrees | 0.91
17 | Perth | WNW (292.5) | 40 degrees | 0.87
17 | Perth | WNW (292.5) | 50 degrees | 0.82
17 | Perth | WNW (292.5) | 60 degrees | 0.75
17 | Perth | WNW (292.5) | 70 degrees | 0.68
17 | Perth | WNW (292.5) | 80 degrees | 0.61
17 | Perth | WNW (292.5) | 90 degrees (vertical) | 0.53
17 | Perth | NW (315) | 0 degrees (horizontal) | 0.93
17 | Perth | NW (315) | 10 degrees | 0.96
17 | Perth | NW (315) | 20 degrees | 0.97
17 | Perth | NW (315) | 30 degrees | 0.96
17 | Perth | NW (315) | 40 degrees | 0.93
17 | Perth | NW (315) | 50 degrees | 0.88
17 | Perth | NW (315) | 60 degrees | 0.82
17 | Perth | NW (315) | 70 degrees | 0.74
17 | Perth | NW (315) | 80 degrees | 0.66
17 | Perth | NW (315) | 90 degrees (vertical) | 0.57
17 | Perth | NNW (337.5) | 0 degrees (horizontal) | 0.93
17 | Perth | NNW (337.5) | 10 degrees | 0.97
17 | Perth | NNW (337.5) | 20 degrees | 0.99
17 | Perth | NNW (337.5) | 30 degrees | 0.99
17 | Perth | NNW (337.5) | 40 degrees | 0.97
17 | Perth | NNW (337.5) | 50 degrees | 0.92
17 | Perth | NNW (337.5) | 60 degrees | 0.86
17 | Perth | NNW (337.5) | 70 degrees | 0.78
17 | Perth | NNW (337.5) | 80 degrees | 0.68
17 | Perth | NNW (337.5) | 90 degrees (vertical) | 0.58
18 | Seoul | N ( 0 degrees) | 0 degrees (horizontal) | 0.95
18 | Seoul | N ( 0 degrees) | 10 degrees | 0.9
18 | Seoul | N ( 0 degrees) | 20 degrees | 0.83
18 | Seoul | N ( 0 degrees) | 30 degrees | 0.76
18 | Seoul | N ( 0 degrees) | 40 degrees | 0.69
18 | Seoul | N ( 0 degrees) | 50 degrees | 0.62
18 | Seoul | N ( 0 degrees) | 60 degrees | 0.56
18 | Seoul | N ( 0 degrees) | 70 degrees | 0.51
18 | Seoul | N ( 0 degrees) | 80 degrees | 0.47
18 | Seoul | N ( 0 degrees) | 90 degrees (vertical) | 0.43
18 | Seoul | NNE (22.5) | 0 degrees (horizontal) | 0.95
18 | Seoul | NNE (22.5) | 10 degrees | 0.9
18 | Seoul | NNE (22.5) | 20 degrees | 0.84
18 | Seoul | NNE (22.5) | 30 degrees | 0.77
18 | Seoul | NNE (22.5) | 40 degrees | 0.7
18 | Seoul | NNE (22.5) | 50 degrees | 0.63
18 | Seoul | NNE (22.5) | 60 degrees | 0.58
18 | Seoul | NNE (22.5) | 70 degrees | 0.52
18 | Seoul | NNE (22.5) | 80 degrees | 0.48
18 | Seoul | NNE (22.5) | 90 degrees (vertical) | 0.44
18 | Seoul | NE (45) | 0 degrees (horizontal) | 0.95
18 | Seoul | NE (45) | 10 degrees | 0.91
18 | Seoul | NE (45) | 20 degrees | 0.86
18 | Seoul | NE (45) | 30 degrees | 0.8
18 | Seoul | NE (45) | 40 degrees | 0.74
18 | Seoul | NE (45) | 50 degrees | 0.68
18 | Seoul | NE (45) | 60 degrees | 0.62
18 | Seoul | NE (45) | 70 degrees | 0.56
18 | Seoul | NE (45) | 80 degrees | 0.51
18 | Seoul | NE (45) | 90 degrees (vertical) | 0.46
18 | Seoul | ENE (67.5) | 0 degrees (horizontal) | 0.95
18 | Seoul | ENE (67.5) | 10 degrees | 0.92
18 | Seoul | ENE (67.5) | 20 degrees | 0.89
18 | Seoul | ENE (67.5) | 30 degrees | 0.84
18 | Seoul | ENE (67.5) | 40 degrees | 0.79
18 | Seoul | ENE (67.5) | 50 degrees | 0.73
18 | Seoul | ENE (67.5) | 60 degrees | 0.68
18 | Seoul | ENE (67.5) | 70 degrees | 0.62
18 | Seoul | ENE (67.5) | 80 degrees | 0.56
18 | Seoul | ENE (67.5) | 90 degrees (vertical) | 0.51
18 | Seoul | E (90) | 0 degrees (horizontal) | 0.95
18 | Seoul | E (90) | 10 degrees | 0.94
18 | Seoul | E (90) | 20 degrees | 0.92
18 | Seoul | E (90) | 30 degrees | 0.81
18 | Seoul | E (90) | 40 degrees | 0.84
18 | Seoul | E (90) | 50 degrees | 0.79
18 | Seoul | E (90) | 60 degrees | 0.74
18 | Seoul | E (90) | 70 degrees | 0.68
18 | Seoul | E (90) | 80 degrees | 0.62
18 | Seoul | E (90) | 90 degrees (vertical) | 0.55
18 | Seoul | ESE (112.5) | 0 degrees (horizontal) | 0.95
18 | Seoul | ESE (112.5) | 10 degrees | 0.95
18 | Seoul | ESE (112.5) | 20 degrees | 0.95
18 | Seoul | ESE (112.5) | 30 degrees | 0.93
18 | Seoul | ESE (112.5) | 40 degrees | 0.9
18 | Seoul | ESE (112.5) | 50 degrees | 0.85
18 | Seoul | ESE (112.5) | 60 degrees | 0.8
18 | Seoul | ESE (112.5) | 70 degrees | 0.74
18 | Seoul | ESE (112.5) | 80 degrees | 0.67
18 | Seoul | ESE (112.5) | 90 degrees (vertical) | 0.6
18 | Seoul | SE (135) | 0 degrees (horizontal) | 0.95
18 | Seoul | SE (135) | 10 degrees | 0.97
18 | Seoul | SE (135) | 20 degrees | 0.98
18 | Seoul | SE (135) | 30 degrees | 0.97
18 | Seoul | SE (135) | 40 degrees | 0.94
18 | Seoul | SE (135) | 50 degrees | 0.9
18 | Seoul | SE (135) | 60 degrees | 0.85
18 | Seoul | SE (135) | 70 degrees | 0.79
18 | Seoul | SE (135) | 80 degrees | 0.72
18 | Seoul | SE (135) | 90 degrees (vertical) | 0.64
18 | Seoul | SSE (157.5) | 0 degrees (horizontal) | 0.95
18 | Seoul | SSE (157.5) | 10 degrees | 0.98
18 | Seoul | SSE (157.5) | 20 degrees | 0.99
18 | Seoul | SSE (157.5) | 30 degrees | 0.99
18 | Seoul | SSE (157.5) | 40 degrees | 0.97
18 | Seoul | SSE (157.5) | 50 degrees | 0.94
18 | Seoul | SSE (157.5) | 60 degrees | 0.89
18 | Seoul | SSE (157.5) | 70 degrees | 0.82
18 | Seoul | SSE (157.5) | 80 degrees | 0.75
18 | Seoul | SSE (157.5) | 90 degrees (vertical) | 0.67
18 | Seoul | S (180) | 0 degrees (horizontal) | 0.95
18 | Seoul | S (180) | 10 degrees | 0.98
18 | Seoul | S (180) | 20 degrees | 1
18 | Seoul | S (180) | 30 degrees | 1
18 | Seoul | S (180) | 40 degrees | 0.98
18 | Seoul | S (180) | 50 degrees | 0.95
18 | Seoul | S (180) | 60 degrees | 0.9
18 | Seoul | S (180) | 70 degrees | 0.84
18 | Seoul | S (180) | 80 degrees | 0.76
18 | Seoul | S (180) | 90 degrees (vertical) | 0.67
18 | Seoul | SSW (202.5) | 0 degrees (horizontal) | 0.95
18 | Seoul | SSW (202.5) | 10 degrees | 0.98
18 | Seoul | SSW (202.5) | 20 degrees | 0.99
18 | Seoul | SSW (202.5) | 30 degrees | 0.99
18 | Seoul | SSW (202.5) | 40 degrees | 0.97
18 | Seoul | SSW (202.5) | 50 degrees | 0.94
18 | Seoul | SSW (202.5) | 60 degrees | 0.89
18 | Seoul | SSW (202.5) | 70 degrees | 0.82
18 | Seoul | SSW (202.5) | 80 degrees | 0.75
18 | Seoul | SSW (202.5) | 90 degrees (vertical) | 0.67
18 | Seoul | SW (225) | 0 degrees (horizontal) | 0.95
18 | Seoul | SW (225) | 10 degrees | 0.97
18 | Seoul | SW (225) | 20 degrees | 0.98
18 | Seoul | SW (225) | 30 degrees | 0.97
18 | Seoul | SW (225) | 40 degrees | 0.94
18 | Seoul | SW (225) | 50 degrees | 0.9
18 | Seoul | SW (225) | 60 degrees | 0.85
18 | Seoul | SW (225) | 70 degrees | 0.79
18 | Seoul | SW (225) | 80 degrees | 0.72
18 | Seoul | SW (225) | 90 degrees (vertical) | 0.64
18 | Seoul | WSW (247.5) | 0 degrees (horizontal) | 0.95
18 | Seoul | WSW (247.5) | 10 degrees | 0.95
18 | Seoul | WSW (247.5) | 20 degrees | 0.95
18 | Seoul | WSW (247.5) | 30 degrees | 0.93
18 | Seoul | WSW (247.5) | 40 degrees | 0.9
18 | Seoul | WSW (247.5) | 50 degrees | 0.85
18 | Seoul | WSW (247.5) | 60 degrees | 0.8
18 | Seoul | WSW (247.5) | 70 degrees | 0.74
18 | Seoul | WSW (247.5) | 80 degrees | 0.67
18 | Seoul | WSW (247.5) | 90 degrees (vertical) | 0.6
18 | Seoul | W (270) | 0 degrees (horizontal) | 0.95
18 | Seoul | W (270) | 10 degrees | 0.94
18 | Seoul | W (270) | 20 degrees | 0.92
18 | Seoul | W (270) | 30 degrees | 0.81
18 | Seoul | W (270) | 40 degrees | 0.84
18 | Seoul | W (270) | 50 degrees | 0.79
18 | Seoul | W (270) | 60 degrees | 0.74
18 | Seoul | W (270) | 70 degrees | 0.68
18 | Seoul | W (270) | 80 degrees | 0.62
18 | Seoul | W (270) | 90 degrees (vertical) | 0.55
18 | Seoul | WNW (292.5) | 0 degrees (horizontal) | 0.95
18 | Seoul | WNW (292.5) | 10 degrees | 0.92
18 | Seoul | WNW (292.5) | 20 degrees | 0.89
18 | Seoul | WNW (292.5) | 30 degrees | 0.84
18 | Seoul | WNW (292.5) | 40 degrees | 0.79
18 | Seoul | WNW (292.5) | 50 degrees | 0.73
18 | Seoul | WNW (292.5) | 60 degrees | 0.68
18 | Seoul | WNW (292.5) | 70 degrees | 0.62
18 | Seoul | WNW (292.5) | 80 degrees | 0.56
18 | Seoul | WNW (292.5) | 90 degrees (vertical) | 0.51
18 | Seoul | NW (315) | 0 degrees (horizontal) | 0.95
18 | Seoul | NW (315) | 10 degrees | 0.91
18 | Seoul | NW (315) | 20 degrees | 0.86
18 | Seoul | NW (315) | 30 degrees | 0.8
18 | Seoul | NW (315) | 40 degrees | 0.74
18 | Seoul | NW (315) | 50 degrees | 0.68
18 | Seoul | NW (315) | 60 degrees | 0.62
18 | Seoul | NW (315) | 70 degrees | 0.56
18 | Seoul | NW (315) | 80 degrees | 0.51
18 | Seoul | NW (315) | 90 degrees (vertical) | 0.46
18 | Seoul | NNW (337.5) | 0 degrees (horizontal) | 0.95
18 | Seoul | NNW (337.5) | 10 degrees | 0.9
18 | Seoul | NNW (337.5) | 20 degrees | 0.84
18 | Seoul | NNW (337.5) | 30 degrees | 0.77
18 | Seoul | NNW (337.5) | 40 degrees | 0.7
18 | Seoul | NNW (337.5) | 50 degrees | 0.63
18 | Seoul | NNW (337.5) | 60 degrees | 0.58
18 | Seoul | NNW (337.5) | 70 degrees | 0.52
18 | Seoul | NNW (337.5) | 80 degrees | 0.48
18 | Seoul | NNW (337.5) | 90 degrees (vertical) | 0.44
19 | Sevilla | N ( 0 degrees) | 0 degrees (horizontal) | 0.9
19 | Sevilla | N ( 0 degrees) | 10 degrees | 0.83
19 | Sevilla | N ( 0 degrees) | 20 degrees | 0.74
19 | Sevilla | N ( 0 degrees) | 30 degrees | 0.64
19 | Sevilla | N ( 0 degrees) | 40 degrees | 0.54
19 | Sevilla | N ( 0 degrees) | 50 degrees | 0.45
19 | Sevilla | N ( 0 degrees) | 60 degrees | 0.37
19 | Sevilla | N ( 0 degrees) | 70 degrees | 0.31
19 | Sevilla | N ( 0 degrees) | 80 degrees | 0.27
19 | Sevilla | N ( 0 degrees) | 90 degrees (vertical) | 0.25
19 | Sevilla | NNE (22.5) | 0 degrees (horizontal) | 0.9
19 | Sevilla | NNE (22.5) | 10 degrees | 0.83
19 | Sevilla | NNE (22.5) | 20 degrees | 0.75
19 | Sevilla | NNE (22.5) | 30 degrees | 0.65
19 | Sevilla | NNE (22.5) | 40 degrees | 0.56
19 | Sevilla | NNE (22.5) | 50 degrees | 0.47
19 | Sevilla | NNE (22.5) | 60 degrees | 0.39
19 | Sevilla | NNE (22.5) | 70 degrees | 0.33
19 | Sevilla | NNE (22.5) | 80 degrees | 0.3
19 | Sevilla | NNE (22.5) | 90 degrees (vertical) | 0.27
19 | Sevilla | NE (45) | 0 degrees (horizontal) | 0.9
19 | Sevilla | NE (45) | 10 degrees | 0.85
19 | Sevilla | NE (45) | 20 degrees | 0.78
19 | Sevilla | NE (45) | 30 degrees | 0.7
19 | Sevilla | NE (45) | 40 degrees | 0.62
19 | Sevilla | NE (45) | 50 degrees | 0.54
19 | Sevilla | NE (45) | 60 degrees | 0.47
19 | Sevilla | NE (45) | 70 degrees | 0.41
19 | Sevilla | NE (45) | 80 degrees | 0.36
19 | Sevilla | NE (45) | 90 degrees (vertical) | 0.32
19 | Sevilla | ENE (67.5) | 0 degrees (horizontal) | 0.9
19 | Sevilla | ENE (67.5) | 10 degrees | 0.87
19 | Sevilla | ENE (67.5) | 20 degrees | 0.82
19 | Sevilla | ENE (67.5) | 30 degrees | 0.76
19 | Sevilla | ENE (67.5) | 40 degrees | 0.7
19 | Sevilla | ENE (67.5) | 50 degrees | 0.63
19 | Sevilla | ENE (67.5) | 60 degrees | 0.57
19 | Sevilla | ENE (67.5) | 70 degrees | 0.51
19 | Sevilla | ENE (67.5) | 80 degrees | 0.45
19 | Sevilla | ENE (67.5) | 90 degrees (vertical) | 0.4
19 | Sevilla | E (90) | 0 degrees (horizontal) | 0.9
19 | Sevilla | E (90) | 10 degrees | 0.89
19 | Sevilla | E (90) | 20 degrees | 0.87
19 | Sevilla | E (90) | 30 degrees | 0.83
19 | Sevilla | E (90) | 40 degrees | 0.78
19 | Sevilla | E (90) | 50 degrees | 0.73
19 | Sevilla | E (90) | 60 degrees | 0.66
19 | Sevilla | E (90) | 70 degrees | 0.6
19 | Sevilla | E (90) | 80 degrees | 0.54
19 | Sevilla | E (90) | 90 degrees (vertical) | 0.47
19 | Sevilla | ESE (112.5) | 0 degrees (horizontal) | 0.9
19 | Sevilla | ESE (112.5) | 10 degrees | 0.92
19 | Sevilla | ESE (112.5) | 20 degrees | 0.91
19 | Sevilla | ESE (112.5) | 30 degrees | 0.89
19 | Sevilla | ESE (112.5) | 40 degrees | 0.86
19 | Sevilla | ESE (112.5) | 50 degrees | 0.81
19 | Sevilla | ESE (112.5) | 60 degrees | 0.75
19 | Sevilla | ESE (112.5) | 70 degrees | 0.69
19 | Sevilla | ESE (112.5) | 80 degrees | 0.61
19 | Sevilla | ESE (112.5) | 90 degrees (vertical) | 0.54
19 | Sevilla | SE (135) | 0 degrees (horizontal) | 0.9
19 | Sevilla | SE (135) | 10 degrees | 0.94
19 | Sevilla | SE (135) | 20 degrees | 0.96
19 | Sevilla | SE (135) | 30 degrees | 0.95
19 | Sevilla | SE (135) | 40 degrees | 0.93
19 | Sevilla | SE (135) | 50 degrees | 0.89
19 | Sevilla | SE (135) | 60 degrees | 0.83
19 | Sevilla | SE (135) | 70 degrees | 0.76
19 | Sevilla | SE (135) | 80 degrees | 0.67
19 | Sevilla | SE (135) | 90 degrees (vertical) | 0.59
19 | Sevilla | SSE (157.5) | 0 degrees (horizontal) | 0.9
19 | Sevilla | SSE (157.5) | 10 degrees | 0.95
19 | Sevilla | SSE (157.5) | 20 degrees | 0.98
19 | Sevilla | SSE (157.5) | 30 degrees | 0.99
19 | Sevilla | SSE (157.5) | 40 degrees | 0.97
19 | Sevilla | SSE (157.5) | 50 degrees | 0.93
19 | Sevilla | SSE (157.5) | 60 degrees | 0.88
19 | Sevilla | SSE (157.5) | 70 degrees | 0.8
19 | Sevilla | SSE (157.5) | 80 degrees | 0.71
19 | Sevilla | SSE (157.5) | 90 degrees (vertical) | 0.61
19 | Sevilla | S (180) | 0 degrees (horizontal) | 0.9
19 | Sevilla | S (180) | 10 degrees | 0.96
19 | Sevilla | S (180) | 20 degrees | 0.99
19 | Sevilla | S (180) | 30 degrees | 1
19 | Sevilla | S (180) | 40 degrees | 0.99
19 | Sevilla | S (180) | 50 degrees | 0.95
19 | Sevilla | S (180) | 60 degrees | 0.89
19 | Sevilla | S (180) | 70 degrees | 0.82
19 | Sevilla | S (180) | 80 degrees | 0.72
19 | Sevilla | S (180) | 90 degrees (vertical) | 0.62
19 | Sevilla | SSW (202.5) | 0 degrees (horizontal) | 0.9
19 | Sevilla | SSW (202.5) | 10 degrees | 0.95
19 | Sevilla | SSW (202.5) | 20 degrees | 0.98
19 | Sevilla | SSW (202.5) | 30 degrees | 0.99
19 | Sevilla | SSW (202.5) | 40 degrees | 0.97
19 | Sevilla | SSW (202.5) | 50 degrees | 0.93
19 | Sevilla | SSW (202.5) | 60 degrees | 0.88
19 | Sevilla | SSW (202.5) | 70 degrees | 0.8
19 | Sevilla | SSW (202.5) | 80 degrees | 0.71
19 | Sevilla | SSW (202.5) | 90 degrees (vertical) | 0.61
19 | Sevilla | SW (225) | 0 degrees (horizontal) | 0.9
19 | Sevilla | SW (225) | 10 degrees | 0.94
19 | Sevilla | SW (225) | 20 degrees | 0.96
19 | Sevilla | SW (225) | 30 degrees | 0.95
19 | Sevilla | SW (225) | 40 degrees | 0.93
19 | Sevilla | SW (225) | 50 degrees | 0.89
19 | Sevilla | SW (225) | 60 degrees | 0.83
19 | Sevilla | SW (225) | 70 degrees | 0.76
19 | Sevilla | SW (225) | 80 degrees | 0.67
19 | Sevilla | SW (225) | 90 degrees (vertical) | 0.59
19 | Sevilla | WSW (247.5) | 0 degrees (horizontal) | 0.9
19 | Sevilla | WSW (247.5) | 10 degrees | 0.92
19 | Sevilla | WSW (247.5) | 20 degrees | 0.91
19 | Sevilla | WSW (247.5) | 30 degrees | 0.89
19 | Sevilla | WSW (247.5) | 40 degrees | 0.86
19 | Sevilla | WSW (247.5) | 50 degrees | 0.81
19 | Sevilla | WSW (247.5) | 60 degrees | 0.75
19 | Sevilla | WSW (247.5) | 70 degrees | 0.69
19 | Sevilla | WSW (247.5) | 80 degrees | 0.61
19 | Sevilla | WSW (247.5) | 90 degrees (vertical) | 0.54
19 | Sevilla | W (270) | 0 degrees (horizontal) | 0.9
19 | Sevilla | W (270) | 10 degrees | 0.89
19 | Sevilla | W (270) | 20 degrees | 0.87
19 | Sevilla | W (270) | 30 degrees | 0.83
19 | Sevilla | W (270) | 40 degrees | 0.78
19 | Sevilla | W (270) | 50 degrees | 0.73
19 | Sevilla | W (270) | 60 degrees | 0.66
19 | Sevilla | W (270) | 70 degrees | 0.6
19 | Sevilla | W (270) | 80 degrees | 0.54
19 | Sevilla | W (270) | 90 degrees (vertical) | 0.47
19 | Sevilla | WNW (292.5) | 0 degrees (horizontal) | 0.9
19 | Sevilla | WNW (292.5) | 10 degrees | 0.87
19 | Sevilla | WNW (292.5) | 20 degrees | 0.82
19 | Sevilla | WNW (292.5) | 30 degrees | 0.76
19 | Sevilla | WNW (292.5) | 40 degrees | 0.7
19 | Sevilla | WNW (292.5) | 50 degrees | 0.63
19 | Sevilla | WNW (292.5) | 60 degrees | 0.57
19 | Sevilla | WNW (292.5) | 70 degrees | 0.51
19 | Sevilla | WNW (292.5) | 80 degrees | 0.45
19 | Sevilla | WNW (292.5) | 90 degrees (vertical) | 0.4
19 | Sevilla | NW (315) | 0 degrees (horizontal) | 0.9
19 | Sevilla | NW (315) | 10 degrees | 0.85
19 | Sevilla | NW (315) | 20 degrees | 0.78
19 | Sevilla | NW (315) | 30 degrees | 0.7
19 | Sevilla | NW (315) | 40 degrees | 0.62
19 | Sevilla | NW (315) | 50 degrees | 0.54
19 | Sevilla | NW (315) | 60 degrees | 0.47
19 | Sevilla | NW (315) | 70 degrees | 0.41
19 | Sevilla | NW (315) | 80 degrees | 0.36
19 | Sevilla | NW (315) | 90 degrees (vertical) | 0.32
19 | Sevilla | NNW (337.5) | 0 degrees (horizontal) | 0.9
19 | Sevilla | NNW (337.5) | 10 degrees | 0.83
19 | Sevilla | NNW (337.5) | 20 degrees | 0.75
19 | Sevilla | NNW (337.5) | 30 degrees | 0.65
19 | Sevilla | NNW (337.5) | 40 degrees | 0.56
19 | Sevilla | NNW (337.5) | 50 degrees | 0.47
19 | Sevilla | NNW (337.5) | 60 degrees | 0.39
19 | Sevilla | NNW (337.5) | 70 degrees | 0.33
19 | Sevilla | NNW (337.5) | 80 degrees | 0.3
19 | Sevilla | NNW (337.5) | 90 degrees (vertical) | 0.27
20 | Stockholm | N ( 0 degrees) | 0 degrees (horizontal) | 0.86
20 | Stockholm | N ( 0 degrees) | 10 degrees | 0.78
20 | Stockholm | N ( 0 degrees) | 20 degrees | 0.69
20 | Stockholm | N ( 0 degrees) | 30 degrees | 0.61
20 | Stockholm | N ( 0 degrees) | 40 degrees | 0.53
20 | Stockholm | N ( 0 degrees) | 50 degrees | 0.46
20 | Stockholm | N ( 0 degrees) | 60 degrees | 0.42
20 | Stockholm | N ( 0 degrees) | 70 degrees | 0.39
20 | Stockholm | N ( 0 degrees) | 80 degrees | 0.37
20 | Stockholm | N ( 0 degrees) | 90 degrees (vertical) | 0.34
20 | Stockholm | NNE (22.5) | 0 degrees (horizontal) | 0.86
20 | Stockholm | NNE (22.5) | 10 degrees | 0.78
20 | Stockholm | NNE (22.5) | 20 degrees | 0.7
20 | Stockholm | NNE (22.5) | 30 degrees | 0.62
20 | Stockholm | NNE (22.5) | 40 degrees | 0.55
20 | Stockholm | NNE (22.5) | 50 degrees | 0.48
20 | Stockholm | NNE (22.5) | 60 degrees | 0.44
20 | Stockholm | NNE (22.5) | 70 degrees | 0.41
20 | Stockholm | NNE (22.5) | 80 degrees | 0.38
20 | Stockholm | NNE (22.5) | 90 degrees (vertical) | 0.35
20 | Stockholm | NE (45) | 0 degrees (horizontal) | 0.86
20 | Stockholm | NE (45) | 10 degrees | 0.8
20 | Stockholm | NE (45) | 20 degrees | 0.73
20 | Stockholm | NE (45) | 30 degrees | 0.67
20 | Stockholm | NE (45) | 40 degrees | 0.6
20 | Stockholm | NE (45) | 50 degrees | 0.55
20 | Stockholm | NE (45) | 60 degrees | 0.51
20 | Stockholm | NE (45) | 70 degrees | 0.47
20 | Stockholm | NE (45) | 80 degrees | 0.43
20 | Stockholm | NE (45) | 90 degrees (vertical) | 0.4
20 | Stockholm | ENE (67.5) | 0 degrees (horizontal) | 0.86
20 | Stockholm | ENE (67.5) | 10 degrees | 0.82
20 | Stockholm | ENE (67.5) | 20 degrees | 0.78
20 | Stockholm | ENE (67.5) | 30 degrees | 0.73
20 | Stockholm | ENE (67.5) | 40 degrees | 0.69
20 | Stockholm | ENE (67.5) | 50 degrees | 0.64
20 | Stockholm | ENE (67.5) | 60 degrees | 0.6
20 | Stockholm | ENE (67.5) | 70 degrees | 0.55
20 | Stockholm | ENE (67.5) | 80 degrees | 0.51
20 | Stockholm | ENE (67.5) | 90 degrees (vertical) | 0.46
20 | Stockholm | E (90) | 0 degrees (horizontal) | 0.86
20 | Stockholm | E (90) | 10 degrees | 0.85
20 | Stockholm | E (90) | 20 degrees | 0.83
20 | Stockholm | E (90) | 30 degrees | 0.81
20 | Stockholm | E (90) | 40 degrees | 0.77
20 | Stockholm | E (90) | 50 degrees | 0.74
20 | Stockholm | E (90) | 60 degrees | 0.7
20 | Stockholm | E (90) | 70 degrees | 0.65
20 | Stockholm | E (90) | 80 degrees | 0.6
20 | Stockholm | E (90) | 90 degrees (vertical) | 0.54
20 | Stockholm | ESE (112.5) | 0 degrees (horizontal) | 0.86
20 | Stockholm | ESE (112.5) | 10 degrees | 0.87
20 | Stockholm | ESE (112.5) | 20 degrees | 0.88
20 | Stockholm | ESE (112.5) | 30 degrees | 0.88
20 | Stockholm | ESE (112.5) | 40 degrees | 0.86
20 | Stockholm | ESE (112.5) | 50 degrees | 0.83
20 | Stockholm | ESE (112.5) | 60 degrees | 0.79
20 | Stockholm | ESE (112.5) | 70 degrees | 0.74
20 | Stockholm | ESE (112.5) | 80 degrees | 0.68
20 | Stockholm | ESE (112.5) | 90 degrees (vertical) | 0.62
20 | Stockholm | SE (135) | 0 degrees (horizontal) | 0.86
20 | Stockholm | SE (135) | 10 degrees | 0.9
20 | Stockholm | SE (135) | 20 degrees | 0.93
20 | Stockholm | SE (135) | 30 degrees | 0.94
20 | Stockholm | SE (135) | 40 degrees | 0.93
20 | Stockholm | SE (135) | 50 degrees | 0.91
20 | Stockholm | SE (135) | 60 degrees | 0.88
20 | Stockholm | SE (135) | 70 degrees | 0.83
20 | Stockholm | SE (135) | 80 degrees | 0.77
20 | Stockholm | SE (135) | 90 degrees (vertical) | 0.69
20 | Stockholm | SSE (157.5) | 0 degrees (horizontal) | 0.86
20 | Stockholm | SSE (157.5) | 10 degrees | 0.91
20 | Stockholm | SSE (157.5) | 20 degrees | 0.96
20 | Stockholm | SSE (157.5) | 30 degrees | 0.98
20 | Stockholm | SSE (157.5) | 40 degrees | 0.98
20 | Stockholm | SSE (157.5) | 50 degrees | 0.97
20 | Stockholm | SSE (157.5) | 60 degrees | 0.94
20 | Stockholm | SSE (157.5) | 70 degrees | 0.89
20 | Stockholm | SSE (157.5) | 80 degrees | 0.82
20 | Stockholm | SSE (157.5) | 90 degrees (vertical) | 0.74
20 | Stockholm | S (180) | 0 degrees (horizontal) | 0.86
20 | Stockholm | S (180) | 10 degrees | 0.92
20 | Stockholm | S (180) | 20 degrees | 0.97
20 | Stockholm | S (180) | 30 degrees | 0.99
20 | Stockholm | S (180) | 40 degrees | 1
20 | Stockholm | S (180) | 50 degrees | 0.99
20 | Stockholm | S (180) | 60 degrees | 0.96
20 | Stockholm | S (180) | 70 degrees | 0.9
20 | Stockholm | S (180) | 80 degrees | 0.84
20 | Stockholm | S (180) | 90 degrees (vertical) | 0.75
20 | Stockholm | SSW (202.5) | 0 degrees (horizontal) | 0.86
20 | Stockholm | SSW (202.5) | 10 degrees | 0.91
20 | Stockholm | SSW (202.5) | 20 degrees | 0.96
20 | Stockholm | SSW (202.5) | 30 degrees | 0.98
20 | Stockholm | SSW (202.5) | 40 degrees | 0.98
20 | Stockholm | SSW (202.5) | 50 degrees | 0.97
20 | Stockholm | SSW (202.5) | 60 degrees | 0.94
20 | Stockholm | SSW (202.5) | 70 degrees | 0.89
20 | Stockholm | SSW (202.5) | 80 degrees | 0.82
20 | Stockholm | SSW (202.5) | 90 degrees (vertical) | 0.74
20 | Stockholm | SW (225) | 0 degrees (horizontal) | 0.86
20 | Stockholm | SW (225) | 10 degrees | 0.9
20 | Stockholm | SW (225) | 20 degrees | 0.93
20 | Stockholm | SW (225) | 30 degrees | 0.94
20 | Stockholm | SW (225) | 40 degrees | 0.93
20 | Stockholm | SW (225) | 50 degrees | 0.91
20 | Stockholm | SW (225) | 60 degrees | 0.88
20 | Stockholm | SW (225) | 70 degrees | 0.83
20 | Stockholm | SW (225) | 80 degrees | 0.77
20 | Stockholm | SW (225) | 90 degrees (vertical) | 0.69
20 | Stockholm | WSW (247.5) | 0 degrees (horizontal) | 0.86
20 | Stockholm | WSW (247.5) | 10 degrees | 0.87
20 | Stockholm | WSW (247.5) | 20 degrees | 0.88
20 | Stockholm | WSW (247.5) | 30 degrees | 0.88
20 | Stockholm | WSW (247.5) | 40 degrees | 0.86
20 | Stockholm | WSW (247.5) | 50 degrees | 0.83
20 | Stockholm | WSW (247.5) | 60 degrees | 0.79
20 | Stockholm | WSW (247.5) | 70 degrees | 0.74
20 | Stockholm | WSW (247.5) | 80 degrees | 0.68
20 | Stockholm | WSW (247.5) | 90 degrees (vertical) | 0.62
20 | Stockholm | W (270) | 0 degrees (horizontal) | 0.86
20 | Stockholm | W (270) | 10 degrees | 0.85
20 | Stockholm | W (270) | 20 degrees | 0.83
20 | Stockholm | W (270) | 30 degrees | 0.81
20 | Stockholm | W (270) | 40 degrees | 0.77
20 | Stockholm | W (270) | 50 degrees | 0.74
20 | Stockholm | W (270) | 60 degrees | 0.7
20 | Stockholm | W (270) | 70 degrees | 0.65
20 | Stockholm | W (270) | 80 degrees | 0.6
20 | Stockholm | W (270) | 90 degrees (vertical) | 0.54
20 | Stockholm | WNW (292.5) | 0 degrees (horizontal) | 0.86
20 | Stockholm | WNW (292.5) | 10 degrees | 0.82
20 | Stockholm | WNW (292.5) | 20 degrees | 0.78
20 | Stockholm | WNW (292.5) | 30 degrees | 0.73
20 | Stockholm | WNW (292.5) | 40 degrees | 0.69
20 | Stockholm | WNW (292.5) | 50 degrees | 0.64
20 | Stockholm | WNW (292.5) | 60 degrees | 0.6
20 | Stockholm | WNW (292.5) | 70 degrees | 0.55
20 | Stockholm | WNW (292.5) | 80 degrees | 0.51
20 | Stockholm | WNW (292.5) | 90 degrees (vertical) | 0.46
20 | Stockholm | NW (315) | 0 degrees (horizontal) | 0.86
20 | Stockholm | NW (315) | 10 degrees | 0.8
20 | Stockholm | NW (315) | 20 degrees | 0.73
20 | Stockholm | NW (315) | 30 degrees | 0.67
20 | Stockholm | NW (315) | 40 degrees | 0.6
20 | Stockholm | NW (315) | 50 degrees | 0.55
20 | Stockholm | NW (315) | 60 degrees | 0.51
20 | Stockholm | NW (315) | 70 degrees | 0.47
20 | Stockholm | NW (315) | 80 degrees | 0.43
20 | Stockholm | NW (315) | 90 degrees (vertical) | 0.4
20 | Stockholm | NNW (337.5) | 0 degrees (horizontal) | 0.86
20 | Stockholm | NNW (337.5) | 10 degrees | 0.78
20 | Stockholm | NNW (337.5) | 20 degrees | 0.7
20 | Stockholm | NNW (337.5) | 30 degrees | 0.62
20 | Stockholm | NNW (337.5) | 40 degrees | 0.55
20 | Stockholm | NNW (337.5) | 50 degrees | 0.48
20 | Stockholm | NNW (337.5) | 60 degrees | 0.44
20 | Stockholm | NNW (337.5) | 70 degrees | 0.41
20 | Stockholm | NNW (337.5) | 80 degrees | 0.38
20 | Stockholm | NNW (337.5) | 90 degrees (vertical) | 0.35

## Module Data (hidden)
GEGEVENS GESELECTEERDE MODULE
Module: | Scheuten : MULTISOL 200A 200Wp
Pnom bij 25°C : | 200
BETA: | -0.33
Umpp_start : | 38
Uoc bij + 45 : | 53.705
Uoc bij 25°C : | 57.5
Uoc bij -10 : | 64.1412
Umpp bij + 45 : | 44.365
Umpp bij 25°C : | 47.5
Umpp bij -10 : | 52.9862
Orientatiefactor: | 1
Onderdimensioneringsfactor: | 0.9
Module kan door orientatie: | 200 | leveren (Ppv bij 25°C x CF)
Module hoeft: | 180 | te leveren (Ppv bij 25°C x CF x ODF)
Module kan bij + 45 : | 186.7766 | leveren
Module kan bij 25°C: | 200 | leveren
Module kan bij -10 : | 223.0721 | leveren
levert bij + 45 : | 180
levert bij 25°C | 180
levert bij -10 : | 180
Ipv bij + 45 : | 4.0573
Ipv bij 25°C | 3.7895
Ipv bij -10 : | 3.3971

## Mod. & Str. (hidden)
BEREKENING AANTAL MODULES EN STRINGS
Geselecteerde omvormer: |  | CS20TL
Totaal vermogen : | 20618
Vermogen per ingang : | 10309
Min aan te sluiten vermogen per ingang : |  |  | 5566.86
Min_Aantal_Modules_Vermogen : |  | 31
Max_Aantal_Modules_Vermogen : |  | 57
Spanning waarbij de stroom bij Tontwerp binnen de omvormerkarakteristiek valt, in het geval dat Impp_Module > Imax, maar Ipv_Module < Imax: | [5 empty] | 33.8104
| min | max
Modules_Spanning: | 7 | 15
Modules_Pmin: | 5
Modules_MPP-stroom: | 1
Modules_Max_Strings |  |  | 6
Modules_Vermogen: | 5 | 19
Modules_Combinatie: | 7 | 15
Strings_Stroom: | 3 | 7
|  | 7 | =Check of mogelijk => Als 0 dan niet
Max aantal aan te sluiten modules : |  | 79
Aantal ingangen op omvormer: |  | 2
Parallel Mode : |  | 0
| input 1 | input 2 | input 3 | input 4 | Totaal
Totaal ingegeven modules: | 55 | 55 | 5 | 1 | 110
max modules: | The number of connected modules on the inverter exceeds the indicated total modules range!
kleur
max modules: | 2